## Zone substations
Zone Substation |  | On-load Capacity - Nameplate Rating (MVA) | Hot or Cold Spare Capacity - Nameplate Rating (MVA) | Total Capacity - Nameplate Rating (MVA) | Cyclic N-1 Rating (MVA) | Hours Load is ≥ 95% of MD | Station Power Factor at MD | Load Transfers (MVA) | Generation Capacity <1MW (MW) (Note 3) | Generation Capacity >1MW (1MW) | Actual Demand (MVA) | 50% PoE Forecast Demand (MVA) |  |  |  |  | % Load Above N-1 Rating (2022) | Energy at Risk (MWh) (N-1 50% PoE) |  |  |  |  | Hours at Risk (N-1 50% PoE)
[11 empty] | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2022 | 2023 | 2024 | 2025 | 2026
BTS 22kV
BK | S | 23 | 10 | 33 | 27.2 |  | 0.98235 |  | 2.2 |  | 13.2614 | 14.1307 | 14.0499 | 13.6019 | 13.3919 | 13.6388 | -
BK | W | 23 | 10 | 33 | 28.6 |  | 0.99434 |  |  |  | 14.7445 | 14.3967 | 14.1494 | 13.9106 | 13.8668 | 14.4592 | -
C | S | 22.5 |  | 22.5 | 17 |  | 0.99263 |  | 1.4 |  | 9.4193 | 1.1565 | 0.75874 | 0.68021 | 0.59457 | 0.50767 | -
C | W | 22.5 |  | 22.5 | 17 |  | 0.9979 |  |  |  | 11.6046 | 0.33447 | 0.2772 | 0.22987 | 0.18917 | 0.14487 | -
F | S | 20 |  | 20 | 13 | 3 | 0.99229 | 6 | 2.7 |  | 11.7761 | 13.733 | 14.6806 | 14.3502 | 14.2153 | 14.6126 | 5.638% | 4 | 9 | 6 | 6 | 11 | 6 | 14 | 11 | 10 | 13
F | W | 20 |  | 20 | 15.3 | 3 | 0.99223 |  |  |  | 15.7797 | 16.4117 | 16.4542 | 16.1762 | 16.3223 | 17.0781 | 7.266%
BTS 66kV
BQ | S | 55 | 55 | 110 | 64.9 |  | 0.9889 | 15.2 | 2.5 | 12.4 | 53.937 | 61.1476 | 63.1153 | 61.2658 | 58.4872 | 58.5842 | -
BQ | W | 55 | 55 | 110 | 72.3 |  | 0.9984 | 15.2 | 2.122 |  | 42.8427 | 63.1358 | 63.5321 | 61.5389 | 60.867 | 63.4627 | -
VM | S | 57 | 27 | 84 | 62.8 |  | 0.98129 | 21.5 | 1.1 |  | 43.3333 | 53.5074 | 66.518 | 72.6749 | 71.6171 | 72.0518 | -
VM | W | 57 | 27 | 84 | 69.2 |  | 0.99276 | 21.5 | 0.98 |  | 37.3973 | 49.8436 | 60.9626 | 62.3096 | 61.5894 | 62.4273 | -
WA | S | 57 | 27 | 84 | 67.1 |  | 0.96356 | 12.2 | 0.179 |  | 31.274 | 46.2887 | 49.8342 | 48.5862 | 47.7155 | 48.4281 | -
WA | W | 57 | 27 | 84 | 73.7 |  | 0.97183 |  | 0.179 |  | 24.0523 | 44.4029 | 44.9121 | 43.8773 | 43.891 | 45.3019 | -
MP | S | 165 |  | 165 | 124 |  | 0.96589 |  | 0.7 | 1.15 | 69.3118 | 100.5037 | 101.7216 | 101.3775 | 100.1242 | 102.189 | -
MP | W | 165 |  | 165 | 123.4 |  | 0.97552 |  |  |  | 54.4927 | 85.3229 | 86.1738 | 85.5946 | 85.5282 | 88.2733 | -
DLF 22kV
TP | S | [5 empty] | - |  |  |  | 0 | Note 6 | Note 6 | Note 6 | Note 6 | Note 6 | -
| W | [5 empty] | - |  |  |  | 0 | Note 6 | Note 6 | Note 6 | Note 6 | Note 6 | -
FBTS 66kV
AP | S | 60 | 27 | 87 | 70 |  | 0.96845 | 17 | 2.6 |  | 41.9647 | 49.0512 | 50.5243 | 50.7966 | 49.9015 | 51.2555 | -
AP | W | 60 | 27 | 87 | 71.3 |  | 0.992 |  | 2.36 |  | 37.729 | 43.3581 | 44.762 | 44.1754 | 44.6703 | 46.9139 | -
E | S | 13.5 |  | 13.5 | 0 | 2 | 0.88814 | ?? | 0.057 |  | 2.3563 | 3.6013 | 3.6234 | 3.5443 | 3.5006 | 3.5834 | 100% | 13034 | 13060 | 12803 | 12732 | 13111 | 8760 | 8760 | 8760 | 8760 | 8760
E | W | 13.5 |  | 13.5 | 0 | 4 | 0.86529 |  | 0.057 |  | 3.2998 | 3.1699 | 3.1631 | 3.1069 | 3.1106 | 3.2244 | 100%
FB | S | 90 |  | 90 | 63.7 |  | 0.95339 | 3.4 | 0.27 |  | 25.7908 | 33.12 | 33.865 | 33.2568 | 32.9174 | 33.733 | -
FB | W | 90 |  | 90 | 62 |  | 0.96004 |  | 0.27 |  | 20.7087 | 24.374 | 24.5765 | 24.2142 | 24.174 | 24.9071 | -
MG | S | 60 | 27 | 87 | 64.3 |  | 0.96743 |  | 0.5 |  | 28.5219 | 28.4258 | 30.0358 | 29.9338 | 29.2148 | 29.7027 | -
MG | W | 60 | 27 | 87 | 75 |  | 0.97758 |  | 0.418 |  | 22.0021 | 28.4618 | 29.614 | 29.2565 | 28.9717 | 30.4616 | -
PM | S | 27 |  | 27 | 17.4 |  | 0.96905 | 2.1 | 1 |  | 12.2441 | 13.3542 | 14.8446 | 15.8587 | 15.5703 | 15.5784 | -
PM | W | 27 |  | 27 | 19.7 |  | 0.95693 | 2.1 | 0.836 |  | 12.2651 | 14.7557 | 16.2548 | 16.5362 | 16.2548 | 16.4885 | -
SB | S | 110 |  | 110 | 59.7 |  | 0.98009 |  | 0.4 | 6 | 36.4278 | 48.4776 | 51.7828 | 53.4003 | 53.8309 | 54.1482 | -
SB | W | 110 |  | 110 | 63.6 |  | 0.99348 |  | 0.296 |  | 23.2699 | 39.6162 | 41.6707 | 42.5549 | 42.7317 | 43.2084 | -
SO | S | 60 | 27 | 87 | 63.7 |  | 0.96294 | 8.4 | 0.5 |  | 28.8939 | 38.9373 | 39.8222 | 39.6277 | 39.4494 | 40.6913 | -
SO | W | 60 | 27 | 87 | 71.7 |  | 0.97427 |  | 0.295 |  | 19.3221 | 31.0388 | 31.4332 | 31.2697 | 31.6369 | 33.1164 | -
WG | S | 81 |  | 81 | 67.6 |  | 0.98849 |  | 0.5 |  | 34.4085 | 37.1603 | 38.2715 | 38.717 | 38.6112 | 39.6285 | -
WG | W | 81 |  | 81 | 71.9 |  | 0.99181 |  | 0.268 |  | 25.7202 | 39.0327 | 40.1676 | 40.1243 | 40.4157 | 41.8748 | -
RTS 66kV
AR | S | 60 |  | 60 | 32.9 |  | 0.9892 | 3.3 | 2 |  | 29.0143 | 32.8333 | 33.0077 | 31.7521 | 30.972 | 31.405 | -
AR | W | 60 |  | 60 | 35.8 |  | 0.98947 | 3.3 | 1.718 |  | 28.4616 | 28.8825 | 28.3932 | 27.6302 | 27.6353 | 28.675 | -
B | S | 54 |  | 54 | 29 |  | 0.95974 | 8.3 | 1.4 | 6.2 | 27.0618 | 26.5556 | 31.436 | 32.0175 | 31.2767 | 31.2971 | -
B | W | 54 |  | 54 | 32.2 |  | 0.97419 | 8.3 | 1.052 | 6.2 | 23.0347 | 27.5604 | 30.3657 | 30.0702 | 29.6609 | 30.0278 | -
BC | S | 57 | 30 | 87 | 71.6 |  | 0.97887 |  | 2 |  | 39.5251 | 45.9748 | 45.6224 | 44.51 | 43.1331 | 43.3703 | -
BC | W | 57 | 30 | 87 | 70.6 |  | 0.9781 |  | 1.771 |  | 43.673 | 44.6114 | 44.1317 | 42.9968 | 42.5131 | 43.6281 | -
CL | S | 60 | 27 | 87 | 71.7 |  | 0.97355 |  | 3.4 |  | 46.0143 | 52.8785 | 54.7395 | 53.3676 | 51.4662 | 51.4454 | -
CL | W | 60 | 27 | 87 | 70.7 |  | 0.98244 |  | 2.91 |  | 37.8086 | 39.3851 | 40.2599 | 39.3801 | 38.9887 | 40.0025 | -
CW | S | 54 |  | 54 | 34.4 |  | 0.97457 |  | 1.691 |  | 24.5163 | 28.7781 | 30.8611 | 31.2035 | 30.3633 | 30.5415 | -
CW | W | 54 |  | 54 | 38.2 |  | 0.97309 |  | 1.691 |  | 24.9016 | 28.089 | 29.6536 | 29.0654 | 28.5994 | 29.0354 | -
FR | S | 90 |  | 90 | 61.3 |  | 0.96916 | 24.8 | 0.21 |  | 33.9674 | 50.9458 | 52.178 | 51.9542 | 51.357 | 52.3523 | -
FR | W | 90 |  | 90 | 72.1 |  | 0.97526 | 24.8 | 0.21 |  | 26.5603 | 43.5582 | 44.3011 | 44.1116 | 43.932 | 45.0907 | -
MP | S | 165 |  | 165 | 124 |  | 0.96589 |  | 0.7 | 1.15 | 69.3118 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | -
MP | W | 165 |  | 165 | 123.4 |  | 0.97552 |  | 0.583 | 1.15 | 54.4927 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | -
NR | S | 83 |  | 83 | 65.2 |  | 0.97563 | 7.4 | 2.9 | 2.6 | 49.4876 | 52.6447 | 53.3193 | 52.3621 | 50.6481 | 50.969 | -
NR | W | 83 |  | 83 | 71.7 |  | 0.99063 |  | 2.514 | 2.6 | 42.6062 | 41.7858 | 42.5248 | 41.3357 | 40.8761 | 42.3308 | -
SK | S | 60 | 27 | 87 | 63.2 |  | 0.96829 |  | 0.9 | 6.2 | 41.7576 | 48.054 | 50.0906 | 48.2074 | 47.0813 | 47.8045 | -
SK | W | 60 | 27 | 87 | 72.9 |  | 0.97414 |  | 0.757 | 6.2 | 33.5192 | 39.7279 | 39.5512 | 38.2498 | 37.9596 | 39.0826 | -
TK | S | 60 | 27 | 87 | 52.5 |  | 0.96709 | 16.2 | 2.1 |  | 41.8107 | 48.4707 | 50.8257 | 49.4613 | 48.2759 | 48.8248 | -
TK | W | 60 | 27 | 87 | 54.7 |  | 0.97066 | 16.2 | 1.7 |  | 40.3203 | 42.3561 | 42.8741 | 41.8897 | 41.8628 | 43.3188 | -
WP | S | 110 |  | 110 | 71.6525 |  | 0.98211 |  |  |  | 17.7649 | 29.9441 | 30.4253 | 30.5319 | 29.8532 | 30.0886 | -
WP | W | 110 |  | 110 | 71.6525 |  | 0.98944 |  |  |  | 10.9422 | 21.4071 | 21.9183 | 22.0658 | 21.6136 | 21.8254 | -
RTS 22kV
R | S | 40 |  | 40 | 30.1 |  | 0.98277 |  | 0.8 |  | 21.3891 | 26.2917 | 34.2598 | 36.9311 | 36.2494 | 36.3152 | -
R | W | 40 |  | 40 | 36 |  | 0.99121 |  |  |  | 18.8955 | 27.5047 | 33.123 | 33.3676 | 32.9833 | 33.2647 | -
RP | S | 20 |  | 20 | 9.45 |  | - |  |  |  | 0 | Note 7 | Note 7 | Note 7 | Note 7 | Note 7 | -
RP | W | 20 |  | 20 | 10.2 |  | - |  |  |  | 0 | Note 7 | Note 7 | Note 7 | Note 7 | Note 7 | -
WMTS 66kV
JA | S | 165 |  | 165 | 127.8 |  | 0.97611 | 63 | 0.257 |  | 83.2099 | 112.3476 | 117.334 | 121.1601 | 119.5221 | 121.6357 | -
JA | W | 165 |  | 165 | 127.4 |  | 0.9923 | 63 | 0.257 |  | 59.7005 | 91.8765 | 96.5955 | 97.9386 | 97.6899 | 100.4359 | -
LQ | S | 120 | 60 | 180 | 131.8 |  | 0.9692 | 37 | 0.03 |  | 60.8812 | 86.1452 | 86.2786 | 83.4806 | 81.7148 | 82.9514 | -
LQ | W | 120 | 60 | 180 | 142.2 |  | 0.97696 |  | 0.03 |  | 42.4798 | 70.6811 | 69.903 | 67.8947 | 67.3212 | 69.139 | -
NC | S | 60 |  | 60 | 31.9 |  | 0.98662 | 4.8 | 7.9 |  | 27.8475 | 30.7974 | 30.544 | 30.7819 | 30.154 | 30.735 | -
NC | W | 60 |  | 60 | 40.2 |  | 0.99686 |  | 6.841 |  | 31.0016 | 30.2255 | 30.4689 | 30.185 | 30.1857 | 31.3598 | -
DA | S | 40.5 |  | 40.5 | 29.2 |  | 0.95431 | 15.5 | 0.6 | 2 | 24.7182 | Note 4 | Note 4 | 31.4966 | 30.5985 | 30.726 | -
DA | W | 40.5 |  | 40.5 | 32.6 |  | 0.96891 | 15.5 | 0.526 | 2 | 19.0957 | Note 4 | Note 4 | 25.6269 | 25.1875 | 25.6285 | -
WB | S | 60 |  | 60 | 17.1 | 2 | 0.97386 | 3.5 | 4.2 |  | 21.4646 | 35.5673 | 36.9236 | 36.2328 | 35.4657 | 35.9515 | 108% | 13706 | 14822 | 13300 | 12806 | 14724 | 3433 | 3743 | 3500 | 3331 | 3584
WB | W | 60 |  | 60 | 18.4 | 3 | 0.99179 | 2.7 | 3.642 |  | 22.7381 | 37.532 | 37.8637 | 37.0341 | 36.9232 | 38.1186 | 104%
WMTS 22kV
DA | S | 40.5 |  | 40.5 | 29.2 |  | 0.95431 | 15.5 | 0.6 | 2 | 24.7182 | 28.4583 | 31.7791 | Note 4 | Note 4 | Note 4 | -
DA | W | 40.5 |  | 40.5 | 32.6 |  | 0.96891 | 15.5 | 0.526 | 2 | 19.0957 | 24.7546 | 26.4155 | Note 4 | Note 4 | Note 4 | -
J | S | 30 | 10 | 40 | 15.4 |  | - |  |  |  | 0 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | -
J | W | 30 | 10 | 40 | 17.2 |  | - |  |  |  | 0 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | -
LS | S | 30 |  | 30 | 24.2 |  | 0.97725 |  | 0.7 |  | 16.0483 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | -
LS | W | 30 |  | 30 | 27 |  | 0.97048 |  | 0.594 |  | 18.5383 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | -
TSTS 66kV
L | S | 60 |  | 60 | 32.1 | 3 | 0.97539 | 14.4 | 6.7 |  | 37.9593 | 40.6598 | 40.0356 | 38.3718 | 37.3272 | 37.6937 | 26.67% | 76 | 63 | 34 | 21 | 25 | 24 | 21 | 15 | 11 | 12
L | W | 60 |  | 60 | 36.4 | 6 | 0.99464 | 13.4 | 5.478 |  | 30.7723 | 30.0441 | 29.377 | 28.557 | 28.489 | 29.4742 | -
Q | S | 60 |  | 60 | 27.2 | 2 | 0.97463 | 7.2 | 4.5 |  | 33.4886 | 35.5608 | 36.8431 | 35.1426 | 33.9572 | 34.2473 | 30.74% | 106 | 148 | 94 | 65 | 72 | 39 | 49 | 37 | 28 | 30
Q | W | 60 |  | 60 | 31.5 | 7 | 0.99315 | 5.8 | 3.998 |  | 28.6547 | 29.6208 | 29.649 | 28.6957 | 28.5255 | 29.4651 | -
SVTS 66kV
RD | S | 60 |  | 60 | 24.9 | 2 | 0.98203 | 8.7 | 4.6 |  | 30.8216 | 35.8446 | 35.268 | 33.675 | 32.6166 | 32.8625 | 43.95% | 159 | 139 | 92 | 68 | 73 | 47 | 43 | 32 | 25 | 27
RD | W | 60 |  | 60 | 28.7 | 6 | 0.99446 | 3.6 | 3.907 |  | 26.455 | 24.7692 | 24.1555 | 23.3864 | 23.3063 | 24.1916 | -
Note 1: J offloaded to JA and VM
Note 2: LS offload to BQ and VM planned
Note 3: Generation capacity <1MW is mostly solar PV
Note 4: DA transfer to WMTS66 planned
Note 5: Refer BTS66 for 2021 onwards
Note 6: TP offloaded to JA
Note 7: RP offload to WP planned
Note 8: WP commissioned mid 2020

## Sub transmission lines
Subtransmission line |  | Line Rating (MVA) | Hours Load is 95% of MD | Power Factor at MD | Load Transfers (MVA) | Generation Capacity (MW) (Note 1) | Historical Demand Worst case N-1 Scenario (MVA) | Forecast Demand Worst case N-1 Scenario (MVA) |  |  |  |  | % Load Above N-1 Rating (2022) | Energy at Risk (MWh) (N-1 50% PoE) |  |  |  |  | Hours at Risk (N-1 50% PoE)
[7 empty] | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2022 | 2023 | 2024 | 2025 | 2026
BTS 22kV
BTS-BK185 | S | 10.5 |  | 1 |  |  | 6.2 | 6.7 | 6.7 | 6.6 | 6.4 | 6.6 | -
| W | 10.5 |  | 1 |  |  | 7.1 | 6.8 | 6.8 | 6.8 | 6.7 | 6.7 | -
BTS-BK187 | S | 10.3 |  | 0.87342 |  |  | 7.9 | 8.2 | 8.5 | 8.6 | 8.2 | 8.1 | -
| W | 10.3 |  | 0.90588 |  |  | 8.5 | 8.4 | 8.6 | 8.5 | 8.4 | 8.4 | -
BTS-BK194 | S | 10.3 |  | 0.91892 |  |  | 7.4 | 7.8 | 7.6 | 7.2 | 7.2 | 7.2 | -
| W | 10.3 |  | 0.93827 |  |  | 8.1 | 7.9 | 7.9 | 7.6 | 7.5 | 7.5 | -
BTS-C186 | S | 9.9 |  | 0.97959 |  |  | 4.9 | 0.6 | 0.4 | 0.3 | 0.3 | 0.3 | -
| W | 11.2 |  | 1 |  |  | 6 | 6.1 | 0.2 | 0.1 | 0.1 | 0.1 | -
BTS-C191 | S | 9.9 |  | 0.97959 |  |  | 4.9 | 0.6 | 0.4 | 0.3 | 0.3 | 0.3 | -
| W | 11.2 |  | 1 |  |  | 6 | 6.1 | 0.2 | 0.1 | 0.1 | 0.1 | -
BTS-C196 | S | 9.9 |  | 0.97959 |  |  | 4.9 | 0.6 | 0.4 | 0.3 | 0.3 | 0.3 | -
| W | 11.2 |  | 1 |  |  | 6 | 6.1 | 0.2 | 0.1 | 0.1 | 0.1 | -
BTS-F179 | S | 12 | 3 | 0.98347 | 6 |  | 12.1 | 14.2 | 15.1 | 14.7 | 14.6 | 15 | 18.33% | 67.459 | 183.9121 | 160.6777 | 124.5458 | 156.1387 | 105.25 | 217 | 197 | 164.25 | 193.75
| W | 12.6 | 3 | 0.96933 | 6 |  | 16.3 | 16 | 17 | 16.9 | 16.6 | 16.8 | 26.98%
BTS-F182 | S | 12 |  | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | -
| W | 12.6 |  | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | -
BTS-F189 | S | 14.1 | 3 | 0.98333 | 6 |  | 12 | 14.1 | 15.1 | 14.8 | 14.6 | 15.1 | 0% | 2.651 | 8.4886 | 8.349 | 5.7412 | 8.4886 | 3 | 14.25 | 15 | 8.5 | 14.25
| W | 14.8 | 3 | 0.97546 | 6 |  | 16.3 | 16 | 17 | 17.1 | 16.8 | 17 | 8.108%
BTS 66kV
BTS-BQ1 | S | 159.9 |  | 0.9595 |  |  | 71.6 | 97.2 | 105.8 | 106.8 | 103.9 | 105.3 | -
| W | 170.6 |  | 0.98925 |  |  | 55.8 | 81.9 | 91.9 | 97 | 95.6 | 94.9 | -
BTS-BQ3 | S | 139.7 |  | 0.96148 |  |  | 67.5 | 91.1 | 99.5 | 100.5 | 97.7 | 99 | -
| W | 149.2 |  | 0.98861 |  |  | 52.7 | 76.6 | 86.5 | 91.4 | 90.1 | 89.4 | -
BTS-VM1 | S | 159.9 |  | 0.9629 |  |  | 62 | 83.8 | 92.5 | 93.9 | 91.4 | 92.6 | -
| W | 170.6 |  | 0.98768 |  |  | 48.7 | 69.9 | 79.5 | 84.7 | 83.7 | 83.1 | -
BQ-WP2 | S | 84 |  | 0.95665 |  |  | 34.6 | 51.7 | 53.3 | 53.3 | 52 | 53.1 | -
| W | 91.5 |  | 0.98069 |  |  | 25.9 | 45 | 46.4 | 47.3 | 46.5 | 46.2 | -
BQ-WP3 | S | 84 |  | 0.95665 |  |  | 34.6 | 51.7 | 53.3 | 53.3 | 52 | 53.1 | -
| W | 91.5 |  | 0.98069 |  |  | 25.9 | 45 | 46.4 | 47.3 | 46.5 | 46.2 | -
BTS-WP | S | 125.7 |  | 0.96137 |  |  | 67.3 | 92.1 | 99.8 | 100.7 | 97.9 | 99.3 | -
| W | 137.2 |  | 0.98851 |  |  | 52.2 | 77.9 | 86.7 | 91.2 | 89.9 | 89.2 | -
VM-BQ1 | S | 162.3 |  | 0.95187 |  |  | 37.4 | 50.9 | 60.2 | 63 | 62 | 62.7 | -
| W | 173.8 |  | 0.97377 |  |  | 30.5 | 40.3 | 48 | 54.2 | 54.5 | 54.1 | -
VM-BQ3 | S | 125.7 |  | 0.95187 |  |  | 37.4 | 50.9 | 60.2 | 63 | 62 | 62.7 | -
| W | 128 |  | 0.97377 |  |  | 30.5 | 40.3 | 48 | 54.2 | 54.5 | 54.1 | -
WP-MP1 | S | 78.3 |  | 0.92222 |  |  | 36 | 55.2 | 55.3 | 56.6 | 54.5 | 55.7 | -
| W | 84.6 |  | 0.96226 |  |  | 26.5 | 46.9 | 48.6 | 49.6 | 48.7 | 48.4 | -
WP-MP2 | S | 80 |  | 0.92244 |  |  | 36.1 | 55.3 | 55.8 | 56.7 | 54.7 | 55.9 | -
| W | 85.7 |  | 0.95865 |  |  | 26.6 | 47 | 48.7 | 49.7 | 48.8 | 48.5 | -
WP-MP3 | S | 83.9 |  | 0.92479 |  |  | 35.9 | 55.1 | 55.6 | 56.5 | 54.5 | 55.7 | -
| W | 91.5 |  | 0.96226 |  |  | 26.5 | 46.8 | 48.6 | 49.5 | 48.7 | 48.4 | -
VM-WA1 | S | 37.7 |  | 0.93082 |  |  | 15.9 | 26 | 28.1 | 27.3 | 27 | 27.2 | -
| W | 40 |  | 0.96639 |  |  | 11.9 | 21.9 | 24.1 | 25.3 | 24.5 | 24.5 | -
VM-WA2 | S | 37.7 |  | 0.9321 |  |  | 16.2 | 26.5 | 28.6 | 27.8 | 27.2 | 27.8 | -
| W | 40 |  | 0.96694 |  |  | 12.1 | 22.1 | 24.6 | 25.8 | 25 | 25 | -
VM-WA3 | S | 37.7 |  | 0.96667 |  |  | 15 | 21.4 | 23.2 | 22.5 | 22.2 | 22.5 | -
| W | 40 |  | 0.97458 |  |  | 11.8 | 19.8 | 20.8 | 20.8 | 20.1 | 20.2 | -
FBTS 66kV
FBTS-AP | S | 101.7 |  | 0.92896 |  |  | 73.2 | 81.1 | 84.9 | 84.8 | 82.9 | 85.6 | -
| W | 109.7 |  | 0.96236 |  |  | 61.1 | 70.2 | 74.5 | 77.6 | 76.6 | 76.8 | -
FBTS-MG | S | 100.6 |  | 0.92663 |  |  | 73.6 | 81.5 | 84.7 | 85.4 | 83.3 | 85.5 | -
| W | 115.5 |  | 0.96393 |  |  | 61 | 69.9 | 74.4 | 77.7 | 76.6 | 76.9 | -
MG-AP | S | 91.5 |  | 0.92308 |  |  | 44.2 | 51.8 | 53.3 | 53.8 | 52.7 | 54.1 | -
| W | 91.5 |  | 0.96899 |  |  | 38.7 | 41.8 | 44.9 | 46.8 | 46.2 | 46.7 | -
FBTS-E | S | 66.3 |  | 0.93333 |  |  | 15 | 17.5 | 19.3 | 20.4 | 20 | 20.1 | -
| W | 86.3 |  | 0.90625 |  |  | 16 | 17.8 | 18.7 | 20.4 | 20.7 | 20.4 | -
FBTS-PM | S | 66.3 |  | 0.94558 |  |  | 14.7 | 17.1 | 18.8 | 19.8 | 19.4 | 19.5 | -
| W | 86.3 |  | 0.92357 |  |  | 15.7 | 17.3 | 18.2 | 19.8 | 20 | 19.7 | -
E-PM | S | 74.3 |  | 0.93701 |  |  | 12.7 | 13.9 | 15.6 | 16.8 | 16.4 | 16.5 | -
| W | 91.5 |  | 0.92126 |  |  | 12.7 | 14.6 | 15.6 | 17.2 | 17.5 | 17.2 | -
FBTS-FB | S | 88 |  | 0.93505 |  |  | 66.2 | 86.8 | 89.2 | 89.1 | 88.6 | 90.8 | -
| W | 112 |  | 0.95229 |  |  | 52.4 | 65.7 | 69.1 | 70.6 | 70.2 | 70.4 | -
FBTS-WG | S | 88 |  | 0.93083 |  |  | 66.5 | 86.8 | 89.5 | 89.1 | 88.7 | 90.8 | -
| W | 112 |  | 0.95038 |  |  | 52.4 | 66 | 68.9 | 70.6 | 70 | 70.7 | -
FB-WG | S | 89.7 |  | 0.96154 |  |  | 39 | 50.2 | 51.7 | 52.2 | 52.1 | 53.3 | -
| W | 94.3 |  | 0.97411 |  |  | 30.9 | 41.9 | 43 | 44.2 | 44.2 | 44.5 | -
FBTS-SB | S | 117.7 |  | 0.95254 |  |  | 59 | 81.5 | 86.8 | 89.3 | 90 | 92.6 | -
| W | 130.3 |  | 0.96984 |  |  | 43.1 | 65.3 | 72.2 | 76 | 77.5 | 78.5 | -
FBTS-SO | S | 109.2 |  | 0.95085 |  |  | 59 | 81.5 | 86.8 | 89.3 | 90 | 92.7 | -
| W | 125.7 |  | 0.96984 |  |  | 43.1 | 65.3 | 72.6 | 76.2 | 77.5 | 78.5 | -
SB-SO | S | 109.7 |  | 0.93266 |  |  | 29.7 | 41 | 43.8 | 46.3 | 47.3 | 48.5 | -
| W | 121.7 |  | 0.98283 |  |  | 23.3 | 33.3 | 39.5 | 42.7 | 44.1 | 44.7 | -
DLF 22kV
DLF64-TP278 | S | 12.6 |  | 0.25 |  |  | 0.4 | 0.5 | 0.1 | 0.2 | 0.3 | 0.3 | -
| W | 13.1 |  | 0.25 |  |  | 0.8 | 0.5 | 1.1 | 0 | 0 | 0.1 | -
DLF5-TP53 | S | 12.6 |  | 0.25 |  |  | 0.4 | 0.5 | 0.1 | 0.2 | 0.3 | 0.3 | -
| W | 13.1 |  | 0.25 |  |  | 0.8 | 0.5 | 1.1 | 0 | 0 | 0.1 | -
RTS 22kV
RTS-R134 | S | 19.1 |  | 0.9875 |  |  | 8 | 10 | 12.6 | 13.4 | 13.1 | 13.2 | -
| W | 20.7 |  | 0.98649 |  |  | 7.4 | 8.1 | 10.2 | 12.1 | 12.1 | 11.9 | -
RTS-R135 | S | 21.5 |  | 0.9708 |  |  | 13.7 | 17 | 21.5 | 22.9 | 22.3 | 22.5 | -
| W | 24.7 |  | 0.98413 |  |  | 12.6 | 13.8 | 17.4 | 20.6 | 20.6 | 20.3 | -
RTS-R136 | S | 21.5 |  | 0.97059 |  |  | 13.6 | 16.9 | 21.3 | 22.7 | 22.1 | 22.3 | -
| W | 24.7 |  | 0.992 |  |  | 12.5 | 13.7 | 17.3 | 20.4 | 20.5 | 20.2 | -
RTS-RP123 | S | 11.4 |  | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | -
| W | 11.4 |  | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | -
RTS-RP124 | S | 7.6 |  | 0 |  |  | 0.6 | 0.6 | Note 5 | Note 5 | Note 5 | Note 5 | -
| W | 7.6 |  | 0 |  |  | 0.6 | 0.6 | Note 5 | Note 5 | Note 5 | Note 5 | -
RTS-RP125 | S | 9 |  | 0 |  |  | 0.4 | 0.4 | Note 5 | Note 5 | Note 5 | Note 5 | -
| W | 9.7 |  | 0 |  |  | 0.4 | 0.4 | Note 5 | Note 5 | Note 5 | Note 5 | -
RTS 66kV
RTS-AR | S | 94.3 |  | 0.92521 |  |  | 72.2 | 83.5 | 83.5 | 80.8 | 78.3 | 79.4 | -
| W | 123.5 |  | 0.91656 |  |  | 76.7 | 77.4 | 78.2 | 76.7 | 74.8 | 74.4 | -
RTS-TK | S | 116.6 |  | 0.96231 |  |  | 45.1 | 52.5 | 53.5 | 51.9 | 50.4 | 51 | -
| W | 122.3 |  | 0.96514 |  |  | 45.9 | 46.3 | 47.3 | 47.1 | 45.9 | 45.7 | -
RTS-TK/BC | S | 135.5 |  | 0.94977 |  |  | 85.6 | 100.2 | 102.5 | 99.5 | 96.5 | 97.8 | -
| W | 137.2 |  | 0.94966 |  |  | 87.4 | 88.3 | 90.2 | 89.9 | 87.7 | 87.4 | -
BC-AR | S | 84.6 |  | 0.90821 |  |  | 41.4 | 48.4 | 48.1 | 46.9 | 45.4 | 45.9 | -
| W | 91.4 |  | 0.89722 |  |  | 46.7 | 47 | 47.3 | 46.4 | 45.4 | 44.9 | -
TK-BC | S | 91.5 |  | 0.94564 |  |  | 69.9 | 81.1 | 81.1 | 78.5 | 76.1 | 76.9 | -
| W | 91.5 |  | 0.94293 |  |  | 73.6 | 74.6 | 75.2 | 74 | 71.8 | 71.3 | -
RTS-CL | S | 135.5 |  | 0.96759 |  |  | 83.3 | 95 | 98 | 96.7 | 94.6 | 94.8 | -
| W | 142.3 |  | 0.98514 |  |  | 67.3 | 69.3 | 71.6 | 73.1 | 71.9 | 71.8 | -
K-CL | S | 91.4 |  | 0.93154 |  |  | 48.2 | 55.8 | 57.9 | 56.4 | 54.2 | 54.8 | -
| W | 91.4 |  | 0.95408 |  |  | 39.2 | 39.5 | 40.8 | 41.8 | 41 | 40.6 | -
RTS-CW | S | 135.5 |  | 0.91738 |  |  | 105.3 | 112.5 | 121 | 122.7 | 117 | 118.2 | -
| W | 142.3 |  | 0.94662 |  |  | 91.8 | 93.3 | 100.3 | 106 | 103.8 | 102.4 | -
RTS-NR | S | 135.5 |  | 0.91032 |  |  | 103.7 | 111.6 | 120 | 121 | 117.2 | 118.3 | -
| W | 137.2 |  | 0.93791 |  |  | 91.8 | 93.5 | 100.8 | 106 | 103.6 | 102.3 | -
B-CW | S | 85.7 |  | 0.93081 |  |  | 76.6 | 78.6 | 84.1 | 84.8 | 81.1 | 81.9 | -
| W | 91.4 |  | 0.95963 |  |  | 64.4 | 64 | 68.3 | 71.9 | 70.4 | 69.6 | -
B-NR | S | 85.7 |  | 0.93103 |  |  | 52.2 | 57 | 64 | 65.2 | 63.4 | 64 | -
| W | 91.4 |  | 0.94045 |  |  | 48.7 | 51.4 | 57.3 | 61.7 | 60.6 | 59.7 | -
RTS-SK | S | 102.9 |  | 0.96411 |  |  | 61.3 | 71.3 | 74.5 | 72 | 70.5 | 71.6 | -
| W | 108 |  | 0.97973 |  |  | 59.2 | 65.2 | 67.6 | 67.5 | 66.4 | 65.5 | -
RTS-FR1 | S | 82.3 |  | 0.99558 |  |  | 22.6 | 29.6 | 30.4 | 30.5 | 29.9 | 30.6 | -
| W | 87.4 |  | 0.98639 |  |  | 14.7 | 24.2 | 25.2 | 25.6 | 25.5 | 25.4 | -
RTS-FR2 | S | 82.3 |  | 0.99559 |  |  | 22.7 | 29.7 | 30.7 | 30.8 | 30.2 | 31 | -
| W | 87.4 |  | 0.98649 |  |  | 14.8 | 24.3 | 25.4 | 25.8 | 25.8 | 25.6 | -
RTS-FR3 | S | 82.3 |  | 1 |  |  | 22.5 | 29.6 | 30.6 | 30.6 | 29.9 | 30.8 | -
| W | 87.4 |  | 0.98639 |  |  | 14.7 | 24.2 | 25.3 | 25.6 | 25.6 | 25.4 | -
FR-MP1 | S | Note 3 |  | Note 3 |  |  | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | -
| W | Note 3 |  | Note 3 |  |  | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | -
FR-WP1 | S | 78.3 |  | 0.98649 |  |  | 7.4 | 8.4 | 9 | 9.3 | 9.1 | 9.3 | -
| W | 84.6 |  | 1 |  |  | 3.6 | 6.6 | 7 | 7.4 | 7.6 | 7.5 | -
FR-MP2 | S | Note 3 |  | Note 3 |  |  | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | -
| W | Note 3 |  | Note 3 |  |  | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | -
FR-WP2 | S | 80 |  | 0.98485 |  |  | 6.6 | 6.8 | 7.1 | 7.1 | 6.9 | 7 | -
| W | 85.7 |  | 0.96429 |  |  | 2.8 | 5.4 | 5.6 | 5.8 | 5.8 | 5.7 | -
BQ-FR3 | S | Note 3 |  | Note 3 |  |  | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | -
| W | Note 3 |  | Note 3 |  |  | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | -
FR-WP3 | S | 81.7 |  | 0.98462 |  |  | 6.5 | 6.6 | 6.8 | 6.8 | 6.7 | 6.8 | -
| W | 88 |  | 0.96296 |  |  | 2.7 | 5.2 | 5.4 | 5.6 | 5.6 | 5.6 | -
BQ-MP3 | S | Note 3 |  | Note 3 |  |  | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | -
| W | Note 3 |  | Note 3 |  |  | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | -
SVTS 66kV
SVTS-RD | S | 116.6 |  | 0.95561 |  |  | 85.6 | 97.7 | 98.6 | 98 | 96.6 | 97.5 | -
| W | 122.3 |  | 0.97606 |  |  | 71 | 70.9 | 71.5 | 71.2 | 70.3 | 70.1 | -
TSTS 66kV
TSTS-L | S | 106.9 | 2 | 0.89944 | 10.9 |  | 107.4 | 113.6 | 114.3 | 110.1 | 107.1 | 108.1 | 6.268% | 6.1511 | 7.3754 | 1.6754 | 0.045034 | 0.44157 | 1.75 | 2 | 1 | 0.25 | 0.5
| W | 108.6 | 3 | 0.95642 | 10.9 |  | 82.6 | 82.8 | 83.8 | 83.3 | 81 | 81 | -
HB-Q | S | 95.5 |  | 0.91126 |  |  | 75.5 | 80.1 | 80.8 | 77.1 | 74.4 | 75.4 | -
| W | 108.6 |  | 0.96085 |  |  | 61.3 | 61.4 | 62.1 | 61.5 | 59.3 | 59.4 | -
L-Q | S | 95.4 |  | 0.94399 |  |  | 60.7 | 63.7 | 64.9 | 63 | 61.4 | 61.9 | -
| W | 108.6 |  | 0.97925 |  |  | 48.2 | 47.9 | 49.1 | 49.3 | 48.1 | 48.1 | -
WMTS 22kV
WMTS-BS216 | S | Note 4 |  | Note 4 |  |  | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | -
| W | Note 4 |  | Note 4 |  |  | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | -
WMTS-BS218 | S | Note 10 |  | Note 10 |  |  | Note 10 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | -
| W | Note 10 |  | Note 10 |  |  | Note 10 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | -
WMTS-DA213 | S | 23.8 |  | 0.89535 |  |  | 25.8 | 29.4 | 33 | 32.6 | 31.8 | 31.9 | 23.53% | Note 6 | Note 6 | Note 6 | Note 6 | Note 6 | Note 6 | Note 6 | Note 6 | Note 6 | Note 6
| W | 29.1 |  | 0.88938 |  |  | 22.6 | 23 | 25.4 | 27.1 | 26.3 | 25.8 | -
WMTS-DA222 | S | 23.8 |  | 0.92188 |  |  | 25.6 | 29.8 | 33.9 | 33.4 | 32.3 | 33 | 25.21% | Note 6 | Note 6 | Note 6 | Note 6 | Note 6 | Note 6 | Note 6 | Note 6 | Note 6 | Note 6
| W | 29.1 |  | 0.94359 |  |  | 19.5 | 23.4 | 25.9 | 27.7 | 26.9 | 26.2 | -
WMTS-J220 | S | 25.5 |  | 0.73543 |  |  | 22.3 | 22.3 | 22.2 | 22.3 | 22.6 | 22.2 | -
| W | 26.7 |  | 0.73214 |  |  | 22.4 | 22.2 | 22.2 | 22.3 | 22.3 | 22.3 | -
WMTS-LS214 | S | 19.1 |  | 0.87892 |  |  | 22.3 | 16.5 | 17.9 | 18 | 17.8 | 18 | -
| W | 19.1 |  | 0.87745 |  |  | 20.4 | 14.1 | 14.9 | 15.7 | 15.7 | 15.5 | -
WMTS-LS226 | S | 19.1 |  | 0.84211 |  |  | 19 | 11.3 | 11.6 | 11.4 | 11.1 | 11.2 | -
| W | 19.1 |  | 0.83902 |  |  | 20.5 | 11.3 | 11.3 | 11.3 | 11.3 | 11.2 | -
BS-J324 | S | Note 4 |  | Note 4 |  |  | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | -
| W | Note 4 |  | Note 4 |  |  | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | -
LS-J325 | S | 21.3 |  | 0.74545 |  |  | 22 | 22 | 21.9 | 22 | 21.9 | 22 | 3.286%
| W | 25.9 |  | 0.74429 |  |  | 21.9 | 21.9 | 21.9 | 22 | 22 | 22 | -
WMTS 66kV
WMTS-JA1 | S | 145.2 |  | 0.9174 |  |  | 56.9 | 86.2 | 89.1 | 90.8 | 89.2 | 90.5 | -
| W | 153.2 |  | 0.9641 |  |  | 39 | 61.2 | 66 | 68.3 | 68.9 | 68.4 | -
WMTS-JA3 | S | 114.9 |  | 0.93182 |  |  | 52.8 | 77.8 | 80.2 | 81.8 | 80.4 | 81.1 | -
| W | 121.2 |  | 0.97245 |  |  | 36.3 | 56.3 | 60.9 | 62.4 | 63.2 | 62.7 | -
WMTS-VM1 | S | 130.3 |  | 0.95965 |  |  | 34.7 | 51.2 | 52.7 | 52.6 | 52 | 52.5 | -
| W | 164.6 |  | 0.98333 |  |  | 24 | 38 | 40.3 | 41.1 | 41.2 | 40.8 | -
WMTS-VM2 | S | 144 |  | 0.93411 |  |  | 25.8 | 38.1 | 39.3 | 39.2 | 38.7 | 39.1 | -
| W | 155.5 |  | 0.97191 |  |  | 17.8 | 28.3 | 30 | 30.6 | 30.7 | 30.4 | -
WMTS-VM3 | S | 120 |  | 0.92326 |  |  | 41.7 | 61.4 | 63 | 63.5 | 62.3 | 63.3 | -
| W | 129.7 |  | 0.96154 |  |  | 28.6 | 45.1 | 48.3 | 49.1 | 49.3 | 48.9 | -
VM-LQ1 | S | 76.6 |  | 0.9698 |  |  | 29.8 | 42.2 | 41.9 | 40.8 | 40 | 40.6 | -
| W | 86.9 |  | 0.96262 |  |  | 21.4 | 33.5 | 34.4 | 34.2 | 33.1 | 32.6 | -
VM-LQ3 | S | 76.6 |  | 0.85754 |  |  | 35.8 | 53.4 | 55.1 | 51.7 | 50.8 | 51.4 | -
| W | 86.9 |  | 0.92857 |  |  | 22.4 | 41.5 | 42.5 | 42.4 | 40.8 | 40.4 | -
VM-JA | S | 91.5 |  | 0.94565 |  |  | 64.4 | 94.8 | 98.2 | 101.2 | 99.7 | 100.8 | 3.607%
| W | 98.3 |  | 0.97978 |  |  | 44.5 | 67.7 | 73.9 | 76.3 | 77.9 | 77.4 | -
JA-LQ2 | S | 76.6 |  | 0.85994 |  |  | 35.7 | 53.3 | 55.1 | 51.6 | 50.7 | 51.4 | -
| W | 86.9 |  | 0.93274 |  |  | 22.3 | 41.5 | 42.5 | 42.4 | 41.2 | 40.4 | -
JA-WP | S | 47.4 |  | 0 |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | -
| W | 57.2 |  | 0 |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | -
WMTS-NC | S | 54.9 |  | 0.95161 |  |  | 49.6 | 56.4 | 57.4 | 56.7 | 55.2 | 56.6 | 2.732%
| W | 70.3 |  | 0.96043 |  |  | 55.6 | 54.8 | 57.6 | 58 | 56.9 | 56.9 | -
WMTS-WB | S | 54.9 |  | 0.9479 |  |  | 49.9 | 56.2 | 57.1 | 57 | 55.4 | 56.4 | 2.368%
| W | 70.3 |  | 0.95691 |  |  | 55.7 | 55.1 | 57.5 | 58.4 | 57.4 | 57.3 | -
WB-NC | S | 74.3 |  | 0.94386 |  |  | 28.5 | 31.4 | 31.2 | 31.7 | 30.8 | 31.4 | -
| W | 97.2 |  | 0.9619 |  |  | 31.5 | 31 | 30.9 | 31.3 | 31 | 31 | -
Note 1: Generation capacity is specified at the location (sub-transmission line/ loop) where the generation is connected to the network.
Note 2: Forecast demand worst case N-1 scenario refers to the expected load that the sub-transmission line would supply in the event of the worst case outage of a sub-transmission line within the loop system.
Note 3: Cut in of new WP Zone substation requires new BTS-WP & JA-WP and creates new WP-MP1, 2 & 3 and FR-WP1, 2 & 3 from FR-MP1 & 2 and BQ-MP3; and also creates new BQ-WP2 & 3 from BQ-FR3 and BQ-MP3
Note 4: WMTS-BS216 & 218 to be used for supply new HV customer. J-LS cable to be retired
Note 5: No load on lines RTS-RP124 and RTS-RP125 after planned RP offload to WP
Note 6: ZSS DA is planned to be transferred to WMTS66 by end of 2022