## TsSummer10_maximum
2023 Terminal Station Maximum Demand Forecast - MW, MVAr & MVA Forecasts aggregated by Terminal Station
Forecasts at time of Station peak - station diversity factors are applied.
Summer, 10% POE
Note: Summer years at end of season
LOCATIONID | LocationType | VOLTAGE | UNIT | 2023 (Actual Note 1) | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033
ATS_BLTS | Hybrid | 66 | MW | 259.6 | 310.6 | 339.5 | 378 | 389.3 | 411.8 | 414.7 | 418.9 | 423.6 | 428.6 | 449.3
ATS_BLTS | Hybrid | 66 | MVAr | 74 | 116.7 | 134.3 | 148.7 | 155.6 | 169.9 | 171.2 | 173.1 | 175.2 | 177.5 | 185.1
ATS_BLTS | Hybrid | 66 | MVA | 270 | 331.8 | 365.1 | 406.2 | 419.3 | 445.4 | 448.7 | 453.3 | 458.4 | 464 | 486
ATS_WEST | Hybrid | 66 | MW | 201 | 259.1 | 268.7 | 274.8 | 282.3 | 290.1 | 299.6 | 311.8 | 323.5 | 335.4 | 348.8
ATS_WEST | Hybrid | 66 | MVAr | 52.7 | 43.7 | 46.4 | 48.1 | 50.2 | 52.4 | 55.1 | 58.5 | 61.8 | 65.2 | 68.9
ATS_WEST | Hybrid | 66 | MVA | 207.8 | 262.8 | 272.7 | 278.9 | 286.7 | 294.8 | 304.6 | 317.3 | 329.4 | 341.7 | 355.6
BATS | Entire | 66 | MW | 156.6 | 196.9 | 201.9 | 200.2 | 201 | 201.5 | 203.8 | 206.8 | 209.6 | 213.4 | 219.3
BATS | Entire | 66 | MVAr | 22.7 | 31.5 | 32.8 | 32.4 | 32.6 | 32.7 | 33.3 | 34.1 | 34.8 | 35.8 | 37.3
BATS | Entire | 66 | MVA | 158.3 | 199.4 | 204.5 | 202.8 | 203.6 | 204.1 | 206.5 | 209.6 | 212.5 | 216.4 | 222.4
BETS | Entire | 22 | MW | 71.5 | 82.5 | 83.5 | 82.6 | 82.2 | 82.4 | 83 | 83 | 84.6 | 86.6 | 87.4
BETS | Entire | 22 | MVAr | 0 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.6 | 5.6
BETS | Entire | 22 | MVA | 71.5 | 82.7 | 83.6 | 82.8 | 82.4 | 82.6 | 83.2 | 83.2 | 84.8 | 86.7 | 87.6
BETS | Entire | 66 | MW | 144 | 175.3 | 179.2 | 178.5 | 177.9 | 177.9 | 178 | 179 | 180.8 | 181.5 | 184.7
BETS | Entire | 66 | MVAr | 14.7 | 27.5 | 28.8 | 28.6 | 28.4 | 28.4 | 28.4 | 28.8 | 29.3 | 29.6 | 30.7
BETS | Entire | 66 | MVA | 144.8 | 177.4 | 181.5 | 180.7 | 180.2 | 180.2 | 180.2 | 181.3 | 183.1 | 183.9 | 187.2
BLTS | Entire | 22 | MW | 40.2 | 68.5 | 73.6 | 78.7 | 78.1 | 77.4 | 77 | 77 | 77.2 | 77.3 | 77.9
BLTS | Entire | 22 | MVAr | 12.8 | 27 | 29.2 | 30.8 | 30.6 | 30.3 | 30.1 | 30.1 | 30.2 | 30.3 | 30.5
BLTS | Entire | 22 | MVA | 42.2 | 73.6 | 79.2 | 84.5 | 83.9 | 83.1 | 82.7 | 82.7 | 82.9 | 83.1 | 83.6
BLTS-SCI | Hybrid | 66 | MW
BLTS-SCI | Hybrid | 66 | MVAr
BLTS-SCI | Hybrid | 66 | MVA
BTS | Entire | 22 | MW | 87.7365 | 93.2048 | 95.5671 | 98.9209 | 103.5433 | 108.6422 | 112.8396 | 117.8727 | 123.6691 | 129.6281 | 135.4245
BTS | Entire | 22 | MVAr | 23.1415 | 22.9062 | 23.5162 | 24.471 | 25.7916 | 27.2129 | 28.3139 | 29.6324 | 31.1502 | 32.707 | 34.2231
BTS | Entire | 22 | MVA | 90.7371 | 95.9783 | 98.4179 | 101.9027 | 106.7071 | 111.9986 | 116.3377 | 121.5403 | 127.5319 | 133.6906 | 139.6818
BTS | Entire | 66 | MW | 243.2 | 336.1 | 356.7 | 368.6 | 387 | 392.5 | 398.9 | 408.8 | 423.6 | 440.3 | 457.8
BTS | Entire | 66 | MVAr | 67 | 115 | 126 | 132.4 | 142.2 | 145.2 | 148.6 | 153.9 | 161.8 | 170.7 | 180.1
BTS | Entire | 66 | MVA | 252.2 | 355.2 | 378.3 | 391.7 | 412.3 | 418.5 | 425.7 | 436.8 | 453.5 | 472.3 | 492
CBTS | Entire | 66 | MW | 431.55 | 494.6297 | 510.1785 | 527.6393 | 545.2347 | 566.2001 | 588.5663 | 609.0576 | 629.676 | 651.4031 | 671.9448
CBTS | Entire | 66 | MVAr | 87.72 | 109.7579 | 114.2633 | 119.2527 | 123.7907 | 129.053 | 135.1813 | 140.4065 | 145.6847 | 151.4679 | 156.7624
CBTS | Entire | 66 | MVA | 440.3751 | 506.661 | 522.8176 | 540.9477 | 559.1109 | 580.7212 | 603.8909 | 625.0321 | 646.3094 | 668.7813 | 689.9886
DPTS | Hybrid | 66 | MW | 258.19 | 315.53 | 356.13 | 360.89 | 370.18 | 377.18 | 389.44 | 402.16 | 413.05 | 427.71 | 441.07
DPTS | Hybrid | 66 | MVAr | 61.99 | 72.18 | 88.63 | 90.56 | 94.32 | 97.16 | 102.12 | 107.28 | 111.69 | 117.63 | 123.04
DPTS | Hybrid | 66 | MVA | 265.53 | 323.68 | 366.99 | 372.08 | 382.01 | 389.49 | 402.61 | 416.22 | 427.88 | 443.59 | 457.91
ERTS | Entire | 66 | MW | 403.4 | 478.1 | 487.8 | 489.1 | 491.6 | 503.7 | 504.3 | 509.2 | 512.6 | 516 | 522.4
ERTS | Entire | 66 | MVAr | 88.1 | 115.8 | 119.2 | 118.9 | 118.8 | 122.1 | 120.8 | 121.4 | 121.4 | 121.5 | 122.7
ERTS | Entire | 66 | MVA | 412.9 | 491.9 | 502.2 | 503.4 | 505.8 | 518.3 | 518.6 | 523.5 | 526.7 | 530.1 | 536.6
ERTS12 | Split Bus | 66 | MW | 183.6 | 232.6 | 236.7 | 237.2 | 238.5 | 244.3 | 245.3 | 248 | 249.8 | 251.6 | 254.7
ERTS12 | Split Bus | 66 | MVAr | 32.4 | 44.7 | 45.9 | 46 | 46.2 | 47.7 | 47.6 | 48.2 | 48.5 | 48.7 | 49.5
ERTS12 | Split Bus | 66 | MVA | 186.4 | 236.9 | 241.1 | 241.6 | 242.9 | 248.9 | 249.9 | 252.6 | 254.4 | 256.3 | 259.4
ERTS34 | Split Bus | 66 | MW | 232.9 | 257.3 | 263 | 263.9 | 265.4 | 272.1 | 272 | 274.6 | 276.5 | 278.4 | 282
ERTS34 | Split Bus | 66 | MVAr | 62.5 | 65 | 67.5 | 67.3 | 67.1 | 69.5 | 68.6 | 69 | 68.9 | 68.9 | 69.8
ERTS34 | Split Bus | 66 | MVA | 241.2 | 265.4 | 271.5 | 272.4 | 273.7 | 280.8 | 280.5 | 283.1 | 284.9 | 286.8 | 290.5
FBTS | Entire | 66 | MW | 247.8 | 296 | 314.9 | 319.9 | 321.4 | 321.9 | 323 | 331.8 | 342.3 | 350.8 | 359.5
FBTS | Entire | 66 | MVAr | 78.2 | 93.1 | 102 | 104.4 | 105.1 | 105.3 | 105.9 | 110 | 115 | 119 | 123.1
FBTS | Entire | 66 | MVA | 259.8 | 310.3 | 331.1 | 336.5 | 338.1 | 338.7 | 339.9 | 349.5 | 361.1 | 370.4 | 380
GNTS | Entire | 66 | MW | 77.5 | 92.018 | 93.445 | 95.161 | 97.128 | 99.385 | 101.401 | 103.445 | 105.499 | 107.569 | 109.498
GNTS | Entire | 66 | MVAr | 24 | 28.4959 | 28.9378 | 29.4692 | 30.0783 | 30.7773 | 31.4016 | 32.0346 | 32.6707 | 33.3117 | 33.9091
GNTS | Entire | 66 | MVA | 81.1311 | 96.3293 | 97.8231 | 99.6195 | 101.6787 | 104.0414 | 106.1519 | 108.2917 | 110.4419 | 112.6089 | 114.6283
GTS | Entire | 66 | MW | 407.12 | 492.6239 | 515.895 | 515.7104 | 516.3035 | 520.44 | 524.9186 | 532.6923 | 539.1014 | 547.5175 | 558.3795
GTS | Entire | 66 | MVAr | 111.07 | 112.5041 | 120.5656 | 120.3573 | 120.2123 | 121.2471 | 122.3429 | 124.4939 | 126.362 | 128.8352 | 132.2383
GTS | Entire | 66 | MVA | 422.56 | 507.5071 | 532.2121 | 531.9646 | 532.4969 | 536.7721 | 541.3995 | 549.5046 | 556.2061 | 565.0153 | 576.4611
HOTS | Entire | 66 | MW | 81.7 | 87.35 | 91.1 | 89.77 | 88.54 | 87.63 | 86.88 | 86.13 | 85.55 | 85.46 | 85.16
HOTS | Entire | 66 | MVAr | -1.24 | 1 | 1.42 | 1.27 | 1.13 | 1.03 | 0.94 | 0.86 | 0.8 | 0.79 | 0.75
HOTS | Entire | 66 | MVA | 81.71 | 87.36 | 91.11 | 89.78 | 88.55 | 87.64 | 86.89 | 86.13 | 85.55 | 85.46 | 85.16
HTS | Entire | 66 | MW | 325.7 | 398 | 400.9 | 402.3 | 404.9 | 411.5 | 421.8 | 425.3 | 430.8 | 439.6 | 447.3
HTS | Entire | 66 | MVAr | 83.9 | 106.1 | 107.4 | 108.1 | 109.2 | 112.1 | 116.7 | 118.2 | 120.7 | 124.6 | 127.9
HTS | Entire | 66 | MVA | 336.4 | 411.9 | 415.1 | 416.6 | 419.3 | 426.5 | 437.6 | 441.4 | 447.4 | 456.9 | 465.2
HYTS | Entire | 22 | MW | 1.48 | 2.31 | 2.28 | 2.24 | 2.19 | 2.14 | 2.1 | 2.07 | 2.03 | 2.01 | 2
HYTS | Entire | 22 | MVAr | 0.42 | 0.71 | 0.7 | 0.68 | 0.66 | 0.65 | 0.63 | 0.62 | 0.61 | 0.6 | 0.6
HYTS | Entire | 22 | MVA | 1.54 | 2.42 | 2.39 | 2.34 | 2.29 | 2.24 | 2.19 | 2.16 | 2.12 | 2.1 | 2.09
KGTS | Entire | 22 | MW | 8.58 | 11.92 | 12.68 | 12.47 | 12.34 | 12.19 | 12.02 | 11.93 | 11.81 | 11.85 | 11.93
KGTS | Entire | 22 | MVAr | 0 | -1.09 | -1.22 | -1.16 | -1.12 | -1.07 | -1.04 | -1.03 | -0.99 | -0.98 | -0.99
KGTS | Entire | 22 | MVA | 8.58 | 11.9697 | 12.7386 | 12.5238 | 12.3907 | 12.2369 | 12.0649 | 11.9744 | 11.8514 | 11.8905 | 11.971
KGTS | Entire | 66 | MW | 52.81 | 60.73 | 62.3 | 60.85 | 59.42 | 58.43 | 57.65 | 56.84 | 56.27 | 55.85 | 55.41
KGTS | Entire | 66 | MVAr | -4.63 | 1.29 | 1.72 | 1.32 | 0.93 | 0.65 | 0.44 | 0.22 | 0.06 | -0.05 | -0.17
KGTS | Entire | 66 | MVA | 53.01 | 60.74 | 62.32 | 60.86 | 59.43 | 58.43 | 57.65 | 56.84 | 56.27 | 55.85 | 55.41
KTS | Entire | 66 | MW | 494.6845 | 523.5755 | 541.1061 | 589.1907 | 611.747 | 635.0786 | 686.0504 | 732.443 | 792.0747 | 829.7414 | 858.1664
KTS | Entire | 66 | MVAr | 111.7123 | 183.7501 | 189.7634 | 197.1258 | 200.8551 | 205.7837 | 215.1941 | 225.88 | 236.7282 | 243.0797 | 249.5762
KTS | Entire | 66 | MVA | 507.7888 | 559.1359 | 577.6168 | 624.5761 | 646.8406 | 670.3164 | 721.205 | 768.3915 | 828.1992 | 865.8741 | 894.86
KTS_East | Split Bus | 66 | MW | 286.8556 | 294.8456 | 305.9788 | 350.316 | 368.5702 | 387.361 | 432.28 | 471.5814 | 523.9887 | 553.258 | 573.1235
KTS_East | Split Bus | 66 | MVAr | 77.7259 | 139.4317 | 143.6029 | 150.0903 | 152.6545 | 156.2934 | 163.8612 | 172.3855 | 181.1063 | 184.8851 | 188.7
KTS_East | Split Bus | 66 | MVA | 297.1993 | 326.152 | 338.0012 | 381.1147 | 398.9328 | 417.7034 | 462.2948 | 502.1013 | 554.4038 | 583.3326 | 603.3889
KTS_West | Split Bus | 66 | MW | 207.8289 | 228.73 | 235.1274 | 238.8746 | 243.1769 | 247.7177 | 253.7704 | 260.8616 | 268.086 | 276.4834 | 285.043
KTS_West | Split Bus | 66 | MVAr | 33.9864 | 44.3184 | 46.1605 | 47.0355 | 48.2006 | 49.4903 | 51.3329 | 53.4945 | 55.622 | 58.1945 | 60.8762
KTS_West | Split Bus | 66 | MVA | 210.5895 | 232.984 | 239.6157 | 243.4613 | 247.9078 | 252.613 | 258.9101 | 266.2901 | 273.7954 | 282.5415 | 291.4711
LY* | Entire | 66 | MW | 25.76 | 26.632 | 26.633 | 26.634 | 26.636 | 26.637 | 26.639 | 26.64 | 26.642 | 26.643 | 26.645
LY* | Entire | 66 | MVAr | 11.2 | 11.5791 | 11.5796 | 11.58 | 11.5809 | 11.5813 | 11.5822 | 11.5826 | 11.5835 | 11.5839 | 11.5848
LY* | Entire | 66 | MVA | 28.0895 | 29.0403 | 29.0414 | 29.0425 | 29.0447 | 29.0458 | 29.0479 | 29.049 | 29.0512 | 29.0523 | 29.0545
MBTS | Entire | 66 | MW | 28.9 | 32.818 | 33.084 | 33.391 | 33.711 | 34.022 | 34.438 | 34.891 | 35.4 | 35.93 | 36.402
MBTS | Entire | 66 | MVAr | -4.2 | 4.7694 | 4.8081 | 4.8527 | 4.8992 | 4.9444 | 5.0048 | 5.0707 | 5.1446 | 5.2217 | 5.2903
MBTS | Entire | 66 | MVA | 29.2036 | 33.1628 | 33.4315 | 33.7418 | 34.0651 | 34.3794 | 34.7998 | 35.2575 | 35.7719 | 36.3074 | 36.7844
MTS | Entire | 22 | MW | 34.3 | 38 | 38.7 | 39.4 | 40 | 40.4 | 40.8 | 41.2 | 41.7 | 42.3 | 42.9
MTS | Entire | 22 | MVAr | 4.2 | 3.4 | 3.5 | 3.6 | 3.8 | 3.8 | 3.9 | 4 | 4.1 | 4.2 | 4.3
MTS | Entire | 22 | MVA | 34.5 | 38.2 | 38.8 | 39.6 | 40.2 | 40.6 | 41 | 41.4 | 41.9 | 42.5 | 43.1
MTS | Entire | 66 | MW | 166.5 | 203.9 | 210.8 | 218.5 | 223.1 | 225.7 | 229 | 233.8 | 239 | 246.6 | 251.3
MTS | Entire | 66 | MVAr | 30.8 | 32.1 | 34.3 | 36.8 | 38.2 | 39 | 40.1 | 41.7 | 43.3 | 45.7 | 47.2
MTS | Entire | 66 | MVA | 169.3 | 206.4 | 213.6 | 221.6 | 226.3 | 229 | 232.5 | 237.5 | 242.9 | 250.8 | 255.7
MTS6622 | Entire | 66 | MW | 200.8 | 241.9 | 249.5 | 257.9 | 263 | 266 | 269.8 | 275.1 | 280.7 | 288.9 | 294.1
MTS6622 | Entire | 66 | MVAr | 35 | 35.5 | 37.8 | 40.4 | 42 | 42.9 | 44 | 45.6 | 47.4 | 49.9 | 51.5
MTS6622 | Entire | 66 | MVA | 203.8 | 244.5 | 252.3 | 261.1 | 266.4 | 269.5 | 273.3 | 278.8 | 284.7 | 293.1 | 298.6
MWTS | Entire | 66 | MW | 379 | 444.341 | 451.274 | 459.958 | 469.265 | 479.728 | 490.098 | 500.1 | 510.45 | 521.216 | 531.708
MWTS | Entire | 66 | MVAr | 42.8 | 50.1789 | 50.9618 | 51.9425 | 52.9935 | 54.1751 | 55.3462 | 56.4757 | 57.6445 | 58.8603 | 60.0451
MWTS | Entire | 66 | MVA | 381.409 | 447.1653 | 454.1424 | 462.8816 | 472.2478 | 482.7773 | 493.2132 | 503.2788 | 513.6945 | 524.529 | 535.0877
RCTS | Entire | 22 | MW | 35.59 | 44.92 | 46.39 | 45.98 | 45.66 | 45.25 | 45 | 44.8 | 44.69 | 44.78 | 44.92
RCTS | Entire | 22 | MVAr | -10.9 | 0.37 | 0.38 | 0.38 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37
RCTS | Entire | 22 | MVA | 37.2217 | 44.92 | 46.39 | 45.98 | 45.66 | 45.25 | 45 | 44.8 | 44.69 | 44.78 | 44.92
RCTS | Entire | 66 | MW | 119.59 | 146.2 | 150.65 | 149.11 | 148.18 | 147.05 | 146.79 | 147.16 | 146.79 | 147.13 | 147.78
RCTS | Entire | 66 | MVAr | 26.48 | 24.84 | 26.22 | 25.74 | 25.45 | 25.1 | 25.02 | 25.13 | 25.02 | 25.13 | 25.33
RCTS | Entire | 66 | MVA | 122.4866 | 148.2952 | 152.9147 | 151.3154 | 150.3496 | 149.1768 | 148.907 | 149.2903 | 148.907 | 149.2607 | 149.9351
RTS | Entire | 22 | MW | 39.2 | 63 | 60.9 | 86.3 | 86.4 | 86.3 | 86.4 | 86.6 | 87 | 87.6 | 88.1
RTS | Entire | 22 | MVAr | 8.6 | 14.3 | 13.6 | 21.7 | 21.7 | 21.7 | 21.7 | 21.8 | 21.9 | 22.1 | 22.3
RTS | Entire | 22 | MVA | 40.2 | 64.6 | 62.3 | 89 | 89.1 | 89 | 89 | 89.3 | 89.7 | 90.3 | 90.9
RTS | Entire | 66 | MW | 437.35 | 587.45 | 618.09 | 629.46 | 633.52 | 635.31 | 638.93 | 648.41 | 658.11 | 671.69 | 683.63
RTS | Entire | 66 | MVAr | 123.73 | 142.51 | 156.12 | 160.88 | 162.36 | 162.84 | 164.23 | 168.29 | 172.44 | 178.34 | 183.46
RTS | Entire | 66 | MVA | 454.5153 | 604.4887 | 637.5019 | 649.694 | 653.9942 | 655.8473 | 659.6992 | 669.8933 | 680.3266 | 694.9623 | 707.8189
RWTS | Entire | 66 | MW | 403.14 | 444.894 | 453.666 | 462.6772 | 472.4641 | 485.6608 | 496.427 | 507.6279 | 522.6693 | 537.7805 | 550.1287
RWTS | Entire | 66 | MVAr | 85.19 | 94.6797 | 97.2363 | 99.6578 | 102.0017 | 105.2378 | 107.7599 | 110.2845 | 114.1967 | 118.0391 | 120.9327
RWTS | Entire | 66 | MVA | 412.0427 | 454.857 | 463.9695 | 473.2883 | 483.3495 | 496.932 | 507.9882 | 519.4697 | 534.9991 | 550.5825 | 563.264
RWTS13 | Split Bus | 66 | MW | 244.7 | 270.8918 | 276.915 | 283.1649 | 288.405 | 295.8484 | 301.7502 | 307.8609 | 317.7657 | 327.7249 | 335.007
RWTS13 | Split Bus | 66 | MVAr | 45.85 | 51.4757 | 53.3497 | 55.0857 | 56.3005 | 58.1082 | 59.4224 | 60.6831 | 63.32 | 65.8832 | 67.5189
RWTS13 | Split Bus | 66 | MVA | 248.9585 | 275.7392 | 282.0073 | 288.4732 | 293.8489 | 301.501 | 307.5455 | 313.7846 | 324.0131 | 334.2816 | 341.7433
RWTS22 | Entire | 22 | MW | 76.81 | 83.48 | 84.2572 | 85.8714 | 87.7006 | 89.943 | 92.0777 | 94.1341 | 96.4016 | 99.0975 | 101.4194
RWTS22 | Entire | 22 | MVAr | 7 | 7.5654 | 7.6505 | 7.8115 | 7.9992 | 8.2191 | 8.4193 | 8.6138 | 8.8206 | 9.0603 | 9.2905
RWTS22 | Entire | 22 | MVA | 77.1283 | 83.8221 | 84.6038 | 86.2259 | 88.0646 | 90.3178 | 92.4618 | 94.5274 | 96.8043 | 99.5108 | 101.844
RWTS24 | Split Bus | 66 | MW | 164.16 | 174.0022 | 176.7509 | 179.5122 | 184.0591 | 189.8124 | 194.6768 | 199.767 | 204.9036 | 210.0556 | 215.1217
RWTS24 | Split Bus | 66 | MVAr | 34 | 43.204 | 43.8865 | 44.5722 | 45.7011 | 47.1296 | 48.3374 | 49.6013 | 50.8767 | 52.1559 | 53.4138
RWTS24 | Split Bus | 66 | MVA | 167.644 | 179.2857 | 182.1178 | 184.963 | 189.6479 | 195.5759 | 200.588 | 205.8328 | 211.1254 | 216.4338 | 221.6537
SHTS | Entire | 66 | MW | 243.51 | 289.01 | 301.75 | 299.62 | 298.41 | 296.01 | 293.79 | 293.65 | 294.92 | 297.05 | 299.46
SHTS | Entire | 66 | MVAr | 62.4 | 72.57 | 78.93 | 77.87 | 77.26 | 76.06 | 74.95 | 74.88 | 75.52 | 76.58 | 77.79
SHTS | Entire | 66 | MVA | 251.38 | 297.9819 | 311.9022 | 309.5737 | 308.2493 | 305.6257 | 303.1997 | 303.0468 | 304.4357 | 306.7624 | 309.3987
SMTS | Entire | 66 | MW | 349.695 | 381.7462 | 397.763 | 416.3992 | 434.2094 | 454.3248 | 473.0542 | 491.8762 | 512.2052 | 532.7655 | 554.0892
SMTS | Entire | 66 | MVAr | 70.0663 | 78.5693 | 81.9617 | 85.9279 | 89.6499 | 93.8034 | 97.6529 | 101.5443 | 105.7624 | 110.0387 | 114.4512
SMTS | Entire | 66 | MVA | 356.6453 | 389.7477 | 406.1196 | 425.1728 | 443.3677 | 463.9074 | 483.0283 | 502.2484 | 523.0104 | 544.0106 | 565.7861
SVTS | Entire | 66 | MW | 336.6 | 402.9 | 407.9 | 410.9 | 408.2 | 417.9 | 422.8 | 427.9 | 432.4 | 443.6 | 455.4
SVTS | Entire | 66 | MVAr | 69.6 | 52.4 | 53.5 | 54.1 | 53.5 | 55.5 | 56.5 | 57.6 | 58.5 | 60.8 | 63.2
SVTS | Entire | 66 | MVA | 343.7 | 406.3 | 411.4 | 414.4 | 411.7 | 421.6 | 426.5 | 431.8 | 436.4 | 447.8 | 459.7
SVTS12 | Split Bus | 66 | MW | 186.7 | 206.2 | 208.6 | 210.2 | 208.4 | 213.5 | 215.5 | 217.6 | 219.3 | 224.7 | 230.3
SVTS12 | Split Bus | 66 | MVAr | 41 | 27.4 | 28 | 28.3 | 27.9 | 29.1 | 29.5 | 30 | 30.3 | 31.5 | 32.8
SVTS12 | Split Bus | 66 | MVA | 191.2 | 208 | 210.5 | 212.1 | 210.3 | 215.4 | 217.5 | 219.7 | 221.4 | 226.9 | 232.6
SVTS34 | Split Bus | 66 | MW | 153.7 | 201 | 203.5 | 205 | 204 | 208.8 | 211.6 | 214.8 | 217.6 | 223.5 | 229.8
SVTS34 | Split Bus | 66 | MVAr | 25.2 | 25 | 25.5 | 25.8 | 25.6 | 26.5 | 27 | 27.6 | 28.1 | 29.3 | 30.4
SVTS34 | Split Bus | 66 | MVA | 155.7 | 202.5 | 205.1 | 206.6 | 205.6 | 210.5 | 213.3 | 216.5 | 219.4 | 225.4 | 231.8
TBTS | Entire | 66 | MW | 292.6 | 296.1 | 298.9 | 302.2 | 304.7 | 306.8 | 310 | 313.8 | 318.3 | 323.7 | 327.9
TBTS | Entire | 66 | MVAr | 68.6 | 58.3 | 59.4 | 60.6 | 61.5 | 62.3 | 63.5 | 65 | 66.7 | 68.7 | 70.3
TBTS | Entire | 66 | MVA | 300.5 | 301.8 | 304.7 | 308.2 | 310.9 | 313 | 316.4 | 320.5 | 325.2 | 330.9 | 335.3
TGTS | Entire | 66 | MW | 136.97 | 170.67 | 174.73 | 172.47 | 170.6 | 169.71 | 168.26 | 168.6 | 167.86 | 168.68 | 169.68
TGTS | Entire | 66 | MVAr | 5.14 | 12.11 | 12.81 | 12.42 | 12.09 | 11.94 | 11.69 | 11.74 | 11.62 | 11.76 | 11.93
TGTS | Entire | 66 | MVA | 137.0664 | 171.0991 | 175.1989 | 172.9166 | 171.0279 | 170.1295 | 168.6656 | 169.0082 | 168.2617 | 169.0894 | 170.0989
TSTS | Entire | 66 | MW | 294.2 | 329.4 | 333.8 | 340.7 | 344.9 | 351 | 359.1 | 367.4 | 377.3 | 389.5 | 400.5
TSTS | Entire | 66 | MVAr | 64.2 | 83.5 | 85.3 | 87.9 | 89.6 | 92 | 95.4 | 98.9 | 103.1 | 108.2 | 112.9
TSTS | Entire | 66 | MVA | 301.2 | 339.9 | 344.6 | 351.8 | 356.3 | 362.9 | 371.5 | 380.4 | 391.1 | 404.2 | 416.1
TTS | Entire | 66 | MW | 458.6502 | 465.199 | 479.6087 | 497.0344 | 503.6118 | 511.7644 | 523.1847 | 536.7492 | 555.8786 | 571.461 | 586.244
TTS | Entire | 66 | MVAr | 97.9715 | 125.1569 | 129.3681 | 134.5637 | 136.3093 | 138.4386 | 141.5227 | 145.2113 | 150.622 | 154.8675 | 158.8705
TTS | Entire | 66 | MVA | 469.1286 | 481.7409 | 496.7501 | 514.9277 | 521.7328 | 530.1586 | 541.9879 | 556.045 | 575.9236 | 592.074 | 607.3894
TTS12 | Split Bus | 66 | MW | 217.6421 | 222.0476 | 229.986 | 242.0441 | 244.9899 | 249.221 | 254.2667 | 260.0471 | 270.4632 | 277.0301 | 283.4714
TTS12 | Split Bus | 66 | MVAr | 42.1375 | 55.5026 | 57.8621 | 61.5204 | 62.2253 | 63.2298 | 64.4883 | 65.948 | 68.8637 | 70.528 | 72.1423
TTS12 | Split Bus | 66 | MVA | 221.6837 | 228.8792 | 237.1531 | 249.7401 | 252.7688 | 257.1169 | 262.3172 | 268.279 | 279.0923 | 285.8669 | 292.5074
TTS34 | Split Bus | 66 | MW | 241.0081 | 244.9702 | 251.4615 | 256.8652 | 260.5291 | 264.4991 | 270.9156 | 278.7433 | 287.5074 | 296.5708 | 304.9641
TTS34 | Split Bus | 66 | MVAr | 55.8341 | 70.0415 | 71.8975 | 73.4425 | 74.4901 | 75.6251 | 77.4598 | 79.6978 | 82.2036 | 84.795 | 87.1948
TTS34 | Split Bus | 66 | MVA | 247.3911 | 254.7866 | 261.5381 | 267.1583 | 270.969 | 275.098 | 281.7717 | 289.9131 | 299.0283 | 308.4549 | 317.1845
WETS | Entire | 66 | MW | 57.4 | 77.17 | 76.54 | 75.13 | 73.83 | 72.56 | 71.38 | 70.42 | 69.67 | 69.15 | 68.58
WETS | Entire | 66 | MVAr | 6.9 | 17.05 | 16.76 | 16.1 | 15.5 | 14.91 | 14.36 | 13.91 | 13.56 | 13.32 | 13.05
WETS | Entire | 66 | MVA | 57.9 | 79.03 | 78.35 | 76.84 | 75.44 | 74.08 | 72.81 | 71.78 | 70.98 | 70.42 | 69.81
WMTS | Entire | 22 | MW | 13.51 | 46.51 | 47.67 | 48.39 | 48.14 | 48.13 | 48.23 | 48.46 | 48.89 | 49.46 | 50.22
WMTS | Entire | 22 | MVAr | 1.32 | 8.62 | 8.73 | 8.79 | 8.77 | 8.77 | 8.78 | 8.8 | 8.84 | 8.89 | 8.96
WMTS | Entire | 22 | MVA | 13.5743 | 47.3 | 48.46 | 49.18 | 48.93 | 48.92 | 49.02 | 49.25 | 49.68 | 50.25 | 51.01
WMTS | Entire | 66 | MW | 288.16 | 338.1046 | 369.7988 | 383.3157 | 396.067 | 410.5023 | 424.7421 | 439.2418 | 454.0653 | 470.552 | 489.5784
WMTS | Entire | 66 | MVAr | 68.43 | 97.5959 | 114.4093 | 121.0298 | 127.1947 | 134.3359 | 141.6658 | 148.9776 | 156.3851 | 164.6839 | 174.4731
WMTS | Entire | 66 | MVA | 296.17 | 351.9086 | 387.0925 | 401.9691 | 415.9898 | 431.9239 | 447.7444 | 463.8186 | 480.2412 | 498.5379 | 519.7383
WOTS | Entire | 66 | MW | 48.64 | 52.5255 | 53.2495 | 54.1087 | 55.1032 | 56.2742 | 57.239 | 58.2461 | 59.2284 | 60.2378 | 61.1451
WOTS | Entire | 66 | MVAr | 11.72 | 12.5985 | 12.8188 | 13.0731 | 13.3585 | 13.691 | 13.9757 | 14.2682 | 14.5596 | 14.8603 | 15.1396
WOTS | Entire | 66 | MVA | 50.0321 | 53.7643 | 54.5113 | 55.3969 | 56.4208 | 57.626 | 58.6203 | 59.6577 | 60.6702 | 61.7109 | 62.6474
WOTS22 | Entire | 22 | MW | 32 | 32.6055 | 33.5245 | 34.5423 | 35.6298 | 36.8758 | 38.01 | 39.1469 | 40.3176 | 41.5332 | 42.7159
WOTS22 | Entire | 22 | MVAr | 2.64 | 2.5613 | 2.6335 | 2.7134 | 2.7989 | 2.8967 | 2.9858 | 3.0751 | 3.1671 | 3.2626 | 3.3555
WOTS22 | Entire | 22 | MVA | 32.1087 | 32.7059 | 33.6278 | 34.6487 | 35.7396 | 36.9894 | 38.1271 | 39.2675 | 40.4418 | 41.6612 | 42.8475
Note 1: Note that this is the observed actual and have not been weather normalised.

## TsSummer50_maximum
2023 Terminal Station Maximum Demand Forecast - MW, MVAr & MVA Forecasts aggregated by Terminal Station
Forecasts at time of Station peak - station diversity factors are applied.
Summer, 50% POE
Note: Summer years at end of season
LOCATIONID | LocationType | VOLTAGE | UNIT | 2023 (Actual Note 1) | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033
ATS_BLTS | Hybrid | 66 | MW | 259.6 | 295.6 | 324.6 | 363 | 374.3 | 396.4 | 399.8 | 403.8 | 408.1 | 412.9 | 432.9
ATS_BLTS | Hybrid | 66 | MVAr | 74 | 109.3 | 127 | 141.5 | 148.4 | 162.4 | 164 | 165.8 | 167.8 | 170 | 177.2
ATS_BLTS | Hybrid | 66 | MVA | 270 | 315.2 | 348.5 | 389.6 | 402.7 | 428.4 | 432.1 | 436.5 | 441.3 | 446.5 | 467.8
ATS_WEST | Hybrid | 66 | MW | 201 | 240.2 | 251.1 | 256.2 | 263.6 | 271.4 | 281.1 | 293.2 | 304.8 | 316.7 | 329
ATS_WEST | Hybrid | 66 | MVAr | 52.7 | 38.4 | 41.4 | 42.9 | 45 | 47.2 | 49.9 | 53.3 | 56.5 | 59.9 | 63.4
ATS_WEST | Hybrid | 66 | MVA | 207.8 | 243.2 | 254.5 | 259.8 | 267.4 | 275.5 | 285.5 | 298 | 310 | 322.3 | 335.1
BATS | Entire | 66 | MW | 156.6 | 169.7 | 174.2 | 173.9 | 174.3 | 175.9 | 178.1 | 181.7 | 185 | 189 | 193.4
BATS | Entire | 66 | MVAr | 22.7 | 24.5 | 25.7 | 25.6 | 25.7 | 26.1 | 26.7 | 27.6 | 28.5 | 29.5 | 30.6
BATS | Entire | 66 | MVA | 158.3 | 171.4 | 176 | 175.7 | 176.2 | 177.8 | 180.1 | 183.7 | 187.2 | 191.3 | 195.8
BETS | Entire | 22 | MW | 71.5 | 75.7 | 76.8 | 76.5 | 76.5 | 76.6 | 77.3 | 77.5 | 78.6 | 80.1 | 81.7
BETS | Entire | 22 | MVAr | 0 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.4 | 5.4 | 5.4 | 5.5
BETS | Entire | 22 | MVA | 71.5 | 75.9 | 77 | 76.7 | 76.7 | 76.8 | 77.5 | 77.7 | 78.8 | 80.3 | 81.8
BETS | Entire | 66 | MW | 144 | 160.7 | 164.4 | 163.8 | 163.2 | 162.9 | 163 | 163.9 | 165.3 | 166.8 | 168.2
BETS | Entire | 66 | MVAr | 14.7 | 22.6 | 23.9 | 23.7 | 23.5 | 23.4 | 23.4 | 23.7 | 24.2 | 24.7 | 25.2
BETS | Entire | 66 | MVA | 144.8 | 162.3 | 166.2 | 165.5 | 164.9 | 164.5 | 164.7 | 165.6 | 167.1 | 168.6 | 170.1
BLTS | Entire | 22 | MW | 40.2 | 61.3 | 66.2 | 71.6 | 71.1 | 70.5 | 70.2 | 70.1 | 70.3 | 70.6 | 71.1
BLTS | Entire | 22 | MVAr | 12.8 | 24 | 26.1 | 27.8 | 27.7 | 27.4 | 27.3 | 27.2 | 27.3 | 27.4 | 27.6
BLTS | Entire | 22 | MVA | 42.2 | 65.9 | 71.2 | 76.8 | 76.3 | 75.6 | 75.3 | 75.2 | 75.4 | 75.7 | 76.2
BLTS-SCI | Hybrid | 66 | MW
BLTS-SCI | Hybrid | 66 | MVAr
BLTS-SCI | Hybrid | 66 | MVA
BTS | Entire | 22 | MW | 87.7365 | 87.2195 | 89.3383 | 92.6429 | 97.1992 | 102.0586 | 106.3502 | 111.107 | 116.6508 | 122.262 | 127.9165
BTS | Entire | 22 | MVAr | 23.1415 | 21.1618 | 21.702 | 22.6335 | 23.9177 | 25.2651 | 26.3888 | 27.6285 | 29.0677 | 30.5309 | 31.9874
BTS | Entire | 22 | MVA | 90.7371 | 89.75 | 91.9364 | 95.3676 | 100.0986 | 105.1394 | 109.5752 | 114.4906 | 120.2178 | 126.0164 | 131.8554
BTS | Entire | 66 | MW | 243.2 | 304.1 | 324.2 | 335.3 | 352.7 | 357.3 | 364.6 | 376.6 | 391.3 | 408 | 424
BTS | Entire | 66 | MVAr | 67 | 97.9 | 108.6 | 114.6 | 123.9 | 126.3 | 130.3 | 136.7 | 144.5 | 153.5 | 162
BTS | Entire | 66 | MVA | 252.2 | 319.5 | 341.9 | 354.3 | 373.9 | 379 | 387.2 | 400.7 | 417.1 | 435.9 | 453.9
CBTS | Entire | 66 | MW | 431.55 | 463.4081 | 475.0714 | 492.0646 | 508.395 | 527.5639 | 546.1709 | 564.0343 | 583.8999 | 604.3919 | 624.9905
CBTS | Entire | 66 | MVAr | 87.72 | 99.571 | 103.0957 | 107.9177 | 112.2923 | 117.1882 | 121.913 | 126.2524 | 131.4651 | 136.9778 | 142.5029
CBTS | Entire | 66 | MVA | 440.3751 | 473.9846 | 486.1291 | 503.7597 | 520.6487 | 540.4227 | 559.6118 | 577.9916 | 598.5166 | 619.7197 | 641.0305
DPTS | Hybrid | 66 | MW | 258.19 | 289.98 | 328.99 | 333.19 | 340.52 | 346.83 | 358.2 | 369.32 | 380.16 | 393.55 | 405.88
DPTS | Hybrid | 66 | MVAr | 61.99 | 61.83 | 77.63 | 79.33 | 82.3 | 84.86 | 89.46 | 93.97 | 98.36 | 103.79 | 108.78
DPTS | Hybrid | 66 | MVA | 265.53 | 296.5 | 338.02 | 342.5 | 350.32 | 357.06 | 369.2 | 381.09 | 392.68 | 407.01 | 420.2
ERTS | Entire | 66 | MW | 403.4 | 432.3 | 435.3 | 442 | 444.1 | 450.7 | 456.6 | 459.7 | 462.7 | 470.5 | 476.8
ERTS | Entire | 66 | MVAr | 88.1 | 99.6 | 100.4 | 102.3 | 102 | 103.2 | 104.2 | 104.1 | 104 | 105.7 | 107
ERTS | Entire | 66 | MVA | 412.9 | 443.6 | 446.7 | 453.7 | 455.7 | 462.4 | 468.4 | 471.4 | 474.2 | 482.2 | 488.7
ERTS12 | Split Bus | 66 | MW | 183.6 | 210.6 | 211.5 | 214.3 | 215.3 | 218.6 | 221.6 | 223.3 | 225.1 | 228.9 | 232.1
ERTS12 | Split Bus | 66 | MVAr | 32.4 | 38.7 | 39 | 39.8 | 39.9 | 40.6 | 41.3 | 41.5 | 41.8 | 42.7 | 43.4
ERTS12 | Split Bus | 66 | MVA | 186.4 | 214.1 | 215.1 | 217.9 | 219 | 222.3 | 225.4 | 227.2 | 228.9 | 232.9 | 236.1
ERTS34 | Split Bus | 66 | MW | 232.9 | 232.4 | 234.5 | 238.6 | 239.9 | 243.6 | 246.8 | 248.5 | 250 | 254.3 | 257.8
ERTS34 | Split Bus | 66 | MVAr | 62.5 | 55.2 | 55.8 | 57.1 | 56.9 | 57.7 | 58.4 | 58.4 | 58.3 | 59.5 | 60.3
ERTS34 | Split Bus | 66 | MVA | 241.2 | 238.9 | 241.1 | 245.3 | 246.6 | 250.3 | 253.6 | 255.2 | 256.7 | 261.2 | 264.8
FBTS | Entire | 66 | MW | 247.8 | 280.5 | 299.2 | 304.2 | 305.5 | 305.6 | 306.3 | 314.3 | 324.4 | 332.2 | 340.4
FBTS | Entire | 66 | MVAr | 78.2 | 85.7 | 94.6 | 96.9 | 97.5 | 97.6 | 97.9 | 101.7 | 106.5 | 110.2 | 114.1
FBTS | Entire | 66 | MVA | 259.8 | 293.3 | 313.8 | 319.3 | 320.7 | 320.8 | 321.6 | 330.3 | 341.4 | 350 | 359
GNTS | Entire | 66 | MW | 77.5 | 85.934 | 87.219 | 88.801 | 90.643 | 92.776 | 94.671 | 96.593 | 98.53 | 100.485 | 102.307
GNTS | Entire | 66 | MVAr | 24 | 26.6118 | 27.0098 | 27.4997 | 28.0701 | 28.7306 | 29.3175 | 29.9127 | 30.5125 | 31.1179 | 31.6822
GNTS | Entire | 66 | MVA | 81.1311 | 89.9602 | 91.3054 | 92.9615 | 94.8898 | 97.1228 | 99.1066 | 101.1186 | 103.1464 | 105.193 | 107.1003
GTS | Entire | 66 | MW | 407.12 | 450.0374 | 473.6715 | 474.1002 | 474.6638 | 476.3903 | 481.677 | 487.8126 | 492.5531 | 501.0391 | 509.8239
GTS | Entire | 66 | MVAr | 111.07 | 97.1875 | 105.4555 | 105.3234 | 105.2191 | 105.3419 | 106.9333 | 108.4286 | 109.7009 | 112.3296 | 114.9066
GTS | Entire | 66 | MVA | 422.56 | 462.2217 | 487.2886 | 487.6655 | 488.1763 | 489.8789 | 495.4121 | 501.7524 | 506.6675 | 515.5826 | 524.7796
HOTS | Entire | 66 | MW | 81.7 | 81.1 | 84.91 | 83.64 | 82.44 | 81.48 | 80.79 | 80.13 | 79.63 | 79.48 | 79.34
HOTS | Entire | 66 | MVAr | -1.24 | 0.3 | 0.72 | 0.58 | 0.45 | 0.34 | 0.26 | 0.19 | 0.14 | 0.12 | 0.1
HOTS | Entire | 66 | MVA | 81.71 | 81.1 | 84.91 | 83.64 | 82.44 | 81.48 | 80.79 | 80.13 | 79.63 | 79.48 | 79.34
HTS | Entire | 66 | MW | 325.7 | 360.7 | 361.8 | 365.4 | 369.5 | 374.8 | 381.7 | 385.2 | 386.8 | 395.5 | 407.9
HTS | Entire | 66 | MVAr | 83.9 | 89.7 | 90.2 | 91.8 | 93.6 | 95.9 | 99 | 100.5 | 101.2 | 105.1 | 110.5
HTS | Entire | 66 | MVA | 336.4 | 371.7 | 372.8 | 376.8 | 381.1 | 386.9 | 394.4 | 398.1 | 399.8 | 409.2 | 422.6
HYTS | Entire | 22 | MW | 1.48 | 1.93 | 1.9 | 1.86 | 1.82 | 1.79 | 1.75 | 1.72 | 1.7 | 1.68 | 1.67
HYTS | Entire | 22 | MVAr | 0.42 | 0.57 | 0.56 | 0.55 | 0.54 | 0.52 | 0.51 | 0.5 | 0.49 | 0.49 | 0.48
HYTS | Entire | 22 | MVA | 1.54 | 2.01 | 1.98 | 1.94 | 1.9 | 1.86 | 1.82 | 1.79 | 1.77 | 1.75 | 1.74
KGTS | Entire | 22 | MW | 8.58 | 10.39 | 11.07 | 10.89 | 10.74 | 10.6 | 10.54 | 10.52 | 10.39 | 10.39 | 10.39
KGTS | Entire | 22 | MVAr | 0 | -0.89 | -1.03 | -0.98 | -0.94 | -0.9 | -0.86 | -0.85 | -0.82 | -0.82 | -0.81
KGTS | Entire | 22 | MVA | 8.58 | 10.428 | 11.1178 | 10.934 | 10.7811 | 10.6381 | 10.575 | 10.5543 | 10.4223 | 10.4223 | 10.4215
KGTS | Entire | 66 | MW | 52.8 | 52.7 | 55.3 | 54.41 | 53.49 | 52.69 | 52.1 | 51.59 | 51.2 | 50.93 | 50.64
KGTS | Entire | 66 | MVAr | -4.6 | -0.92 | -0.2 | -0.45 | -0.7 | -0.92 | -1.08 | -1.22 | -1.33 | -1.4 | -1.48
KGTS | Entire | 66 | MVA | 53 | 52.71 | 55.3 | 54.41 | 53.49 | 52.7 | 52.11 | 51.6 | 51.22 | 50.95 | 50.66
KTS | Entire | 66 | MW | 494.6845 | 488.1692 | 505.702 | 553.7867 | 575.853 | 598.0687 | 649.1264 | 695.0585 | 753.931 | 789.9757 | 817.1362
KTS | Entire | 66 | MVAr | 111.7123 | 122.101 | 127.7691 | 135.5852 | 139.2903 | 143.845 | 153.2797 | 163.488 | 173.7431 | 179.0343 | 184.4474
KTS | Entire | 66 | MVA | 507.7888 | 503.9824 | 522.3683 | 570.7134 | 592.9493 | 615.5648 | 667.2977 | 714.287 | 773.8584 | 810.1128 | 837.7682
KTS_East | Split Bus | 66 | MW | 286.8556 | 277.2464 | 288.4582 | 333.028 | 351.1325 | 369.4517 | 414.4756 | 453.3254 | 505.1797 | 533.8447 | 553.2719
KTS_East | Split Bus | 66 | MVAr | 77.7259 | 83.5813 | 87.3752 | 94.3653 | 96.9984 | 100.4744 | 108.0436 | 116.0371 | 124.1583 | 127.1979 | 130.2018
KTS_East | Split Bus | 66 | MVA | 297.1993 | 289.571 | 301.401 | 346.1394 | 364.2839 | 382.8703 | 428.3263 | 467.9407 | 520.2132 | 548.7891 | 568.3857
KTS_West | Split Bus | 66 | MW | 207.8289 | 210.9229 | 217.2439 | 220.7587 | 224.7205 | 228.6169 | 234.6508 | 241.7331 | 248.7514 | 256.131 | 263.8643
KTS_West | Split Bus | 66 | MVAr | 33.9864 | 38.5197 | 40.3939 | 41.22 | 42.2919 | 43.3706 | 45.236 | 47.4509 | 49.5848 | 51.8364 | 54.2456
KTS_West | Split Bus | 66 | MVA | 210.5895 | 214.4113 | 220.9674 | 224.574 | 228.6654 | 232.6945 | 238.9714 | 246.3462 | 253.6452 | 261.3237 | 269.3825
LY* | Entire | 66 | MW | 25.76 | 24.234 | 24.235 | 24.237 | 24.238 | 24.24 | 24.243 | 24.245 | 24.247 | 24.248 | 24.249
LY* | Entire | 66 | MVAr | 11.2 | 10.5365 | 10.537 | 10.5378 | 10.5383 | 10.5391 | 10.5404 | 10.5413 | 10.5422 | 10.5426 | 10.543
LY* | Entire | 66 | MVA | 28.0895 | 26.4255 | 26.4266 | 26.4287 | 26.4298 | 26.432 | 26.4353 | 26.4375 | 26.4396 | 26.4407 | 26.4418
MBTS | Entire | 66 | MW | 28.9 | 30.197 | 30.459 | 30.682 | 31.035 | 31.435 | 31.859 | 32.33 | 32.815 | 33.286 | 33.687
MBTS | Entire | 66 | MVAr | -4.2 | 4.3885 | 4.4266 | 4.459 | 4.5103 | 4.5684 | 4.63 | 4.6985 | 4.769 | 4.8374 | 4.8957
MBTS | Entire | 66 | MVA | 29.2036 | 30.5142 | 30.779 | 31.0043 | 31.361 | 31.7652 | 32.1937 | 32.6696 | 33.1597 | 33.6357 | 34.0409
MTS | Entire | 22 | MW | 34.3 | 35.2 | 35.8 | 36.5 | 37.1 | 37.4 | 37.8 | 38.2 | 38.7 | 39.2 | 39.7
MTS | Entire | 22 | MVAr | 4.2 | 2.9 | 3 | 3.1 | 3.2 | 3.3 | 3.3 | 3.4 | 3.5 | 3.6 | 3.7
MTS | Entire | 22 | MVA | 34.5 | 35.3 | 35.9 | 36.7 | 37.2 | 37.6 | 38 | 38.4 | 38.8 | 39.3 | 39.9
MTS | Entire | 66 | MW | 166.5 | 185.9 | 190.9 | 197.7 | 202.4 | 206.1 | 210.2 | 214.7 | 218.5 | 225.2 | 230.3
MTS | Entire | 66 | MVAr | 30.8 | 26.3 | 28 | 30.1 | 31.6 | 32.8 | 34.1 | 35.5 | 36.8 | 38.9 | 40.5
MTS | Entire | 66 | MVA | 169.3 | 187.7 | 192.9 | 200 | 204.9 | 208.7 | 213 | 217.6 | 221.6 | 228.5 | 233.8
MTS6622 | Entire | 66 | MW | 200.8 | 221.1 | 226.7 | 234.2 | 239.5 | 243.5 | 248.1 | 252.9 | 257.2 | 264.4 | 270
MTS6622 | Entire | 66 | MVAr | 35 | 29.2 | 30.9 | 33.2 | 34.8 | 36.1 | 37.5 | 39 | 40.3 | 42.5 | 44.2
MTS6622 | Entire | 66 | MVA | 203.8 | 223 | 228.8 | 236.6 | 242 | 246.1 | 250.9 | 255.9 | 260.3 | 267.7 | 273.6
MWTS | Entire | 66 | MW | 379 | 412.209 | 418.944 | 425.935 | 434.129 | 444.162 | 453.756 | 464.29 | 473.756 | 483.638 | 492.917
MWTS | Entire | 66 | MVAr | 42.8 | 46.5503 | 47.3108 | 48.1003 | 49.0256 | 50.1587 | 51.2421 | 52.4317 | 53.5007 | 54.6166 | 55.6645
MWTS | Entire | 66 | MVA | 381.409 | 414.8291 | 421.6069 | 428.6424 | 436.8884 | 446.9852 | 456.6402 | 467.2411 | 476.7673 | 486.7121 | 496.0501
RCTS | Entire | 22 | MW | 35.59 | 42.28 | 43.88 | 43.52 | 43.13 | 42.79 | 42.49 | 42.36 | 42.21 | 42.26 | 42.29
RCTS | Entire | 22 | MVAr | -10.9 | 0.35 | 0.36 | 0.36 | 0.35 | 0.35 | 0.35 | 0.35 | 0.34 | 0.35 | 0.35
RCTS | Entire | 22 | MVA | 37.2217 | 42.28 | 43.88 | 43.52 | 43.13 | 42.79 | 42.49 | 42.36 | 42.21 | 42.26 | 42.29
RCTS | Entire | 66 | MW | 119.59 | 132.65 | 137.03 | 135.84 | 134.72 | 133.97 | 133.65 | 133.93 | 133.91 | 134.61 | 135.21
RCTS | Entire | 66 | MVAr | 26.48 | 20.63 | 21.99 | 21.62 | 21.27 | 21.04 | 20.94 | 21.02 | 21.02 | 21.24 | 21.42
RCTS | Entire | 66 | MVA | 122.4866 | 134.2446 | 138.7832 | 137.5497 | 136.3888 | 135.6121 | 135.2805 | 135.5695 | 135.5497 | 136.2754 | 136.8962
RTS | Entire | 22 | MW | 39.2 | 58.3 | 56.3 | 81.4 | 81.4 | 81.3 | 81.3 | 81.5 | 81.8 | 82.2 | 82.6
RTS | Entire | 22 | MVAr | 8.6 | 12.7 | 12.1 | 20.1 | 20.1 | 20.1 | 20.1 | 20.2 | 20.3 | 20.4 | 20.5
RTS | Entire | 22 | MVA | 40.2 | 59.6 | 57.6 | 83.8 | 83.8 | 83.8 | 83.8 | 83.9 | 84.3 | 84.7 | 85.1
RTS | Entire | 66 | MW | 437.35 | 497.6 | 527.8 | 538 | 541.5 | 541.3 | 544.4 | 549.4 | 561.6 | 576.1 | 595.4
RTS | Entire | 66 | MVAr | 123.73 | 101.6 | 115.1 | 119.4 | 120.6 | 120.2 | 121.2 | 123.2 | 128.5 | 134.9 | 143.5
RTS | Entire | 66 | MVA | 454.5153 | 507.8 | 540.2 | 551.1 | 554.8 | 554.5 | 557.7 | 563.1 | 576.1 | 591.7 | 612.4
RWTS | Entire | 66 | MW | 403.14 | 420.0176 | 426.5357 | 434.9665 | 444.7742 | 456.3067 | 467.0203 | 477.064 | 488.7433 | 503.8625 | 516.0516
RWTS | Entire | 66 | MVAr | 85.19 | 88.6568 | 90.6394 | 92.8745 | 95.2678 | 97.9701 | 100.4502 | 102.7325 | 105.5528 | 109.6227 | 112.548
RWTS | Entire | 66 | MVA | 412.0427 | 429.2725 | 436.0599 | 444.7714 | 454.8627 | 466.7054 | 477.701 | 488 | 500.0114 | 515.6497 | 528.1821
RWTS13 | Split Bus | 66 | MW | 244.7 | 254.7366 | 259.4672 | 264.3733 | 269.7258 | 276.1063 | 282.7923 | 288.6221 | 295.9312 | 306.4592 | 313.9277
RWTS13 | Split Bus | 66 | MVAr | 45.85 | 47.6183 | 49.157 | 50.5169 | 51.804 | 53.2271 | 54.7071 | 55.9432 | 57.6783 | 60.6082 | 62.3614
RWTS13 | Split Bus | 66 | MVA | 248.9585 | 259.1491 | 264.0826 | 269.1565 | 274.6555 | 281.19 | 288.0353 | 293.9938 | 301.4997 | 312.3949 | 320.0618
RWTS22 | Entire | 22 | MW | 76.81 | 78.2986 | 79.112 | 80.4467 | 82.0274 | 84.0366 | 86.0025 | 88.0777 | 90.3816 | 92.8842 | 94.9876
RWTS22 | Entire | 22 | MVAr | 7 | 7.0972 | 7.1823 | 7.3136 | 7.4757 | 7.6751 | 7.8599 | 8.0529 | 8.2632 | 8.4851 | 8.6903
RWTS22 | Entire | 22 | MVA | 77.1283 | 78.6196 | 79.4373 | 80.7785 | 82.3673 | 84.3864 | 86.3609 | 88.4451 | 90.7585 | 93.2709 | 95.3843
RWTS24 | Split Bus | 66 | MW | 164.16 | 165.281 | 167.0685 | 170.5932 | 175.0484 | 180.2004 | 184.228 | 188.4419 | 192.8121 | 197.4033 | 202.1239
RWTS24 | Split Bus | 66 | MVAr | 34 | 41.0386 | 41.4824 | 42.3576 | 43.4638 | 44.743 | 45.743 | 46.7893 | 47.8745 | 49.0144 | 50.1865
RWTS24 | Split Bus | 66 | MVA | 167.644 | 170.2997 | 172.1414 | 175.7732 | 180.3636 | 185.6721 | 189.822 | 194.1638 | 198.6667 | 203.3973 | 208.2613
SHTS | Entire | 66 | MW | 243.51 | 264.63 | 278.21 | 277.46 | 275.71 | 274.5 | 273.3 | 273.55 | 274.15 | 276.52 | 278.16
SHTS | Entire | 66 | MVAr | 62.4 | 60.39 | 67.18 | 66.8 | 65.92 | 65.32 | 64.72 | 64.85 | 65.15 | 66.33 | 67.15
SHTS | Entire | 66 | MVA | 251.38 | 271.4332 | 286.2061 | 285.388 | 283.481 | 282.1648 | 280.8586 | 281.1319 | 281.7849 | 284.3642 | 286.1505
SMTS | Entire | 66 | MW | 349.695 | 356.9799 | 370.7176 | 387.2933 | 403.9503 | 423.011 | 440.3632 | 458.8757 | 477.3799 | 496.2654 | 517.0001
SMTS | Entire | 66 | MVAr | 70.0663 | 73.6146 | 76.5635 | 80.1121 | 83.6128 | 87.5442 | 91.1299 | 94.9563 | 98.8085 | 102.7447 | 107.0419
SMTS | Entire | 66 | MVA | 356.6453 | 364.4911 | 378.5413 | 395.4921 | 412.513 | 431.9749 | 449.6937 | 468.5974 | 487.4984 | 506.7897 | 527.965
SVTS | Entire | 66 | MW | 336.6 | 372.5 | 376.4 | 380.4 | 381.3 | 386.1 | 392.4 | 395.4 | 398.8 | 411.9 | 424.8
SVTS | Entire | 66 | MVAr | 69.6 | 46.2 | 47 | 47.8 | 48 | 49 | 50.2 | 50.8 | 51.5 | 54.2 | 56.9
SVTS | Entire | 66 | MVA | 343.7 | 375.4 | 379.3 | 383.4 | 384.3 | 389.2 | 395.6 | 398.7 | 402.1 | 415.5 | 428.6
SVTS12 | Split Bus | 66 | MW | 186.7 | 192.1 | 194 | 196 | 196.1 | 198.3 | 201 | 201.8 | 202.9 | 209.2 | 215.4
SVTS12 | Split Bus | 66 | MVAr | 41 | 24.3 | 24.7 | 25.2 | 25.2 | 25.7 | 26.3 | 26.5 | 26.7 | 28.1 | 29.5
SVTS12 | Split Bus | 66 | MVA | 191.2 | 193.6 | 195.5 | 197.6 | 197.7 | 199.9 | 202.7 | 203.6 | 204.6 | 211.1 | 217.5
SVTS34 | Split Bus | 66 | MW | 153.7 | 184.4 | 186.4 | 188.4 | 189.2 | 191.9 | 195.5 | 197.7 | 200 | 207 | 213.7
SVTS34 | Split Bus | 66 | MVAr | 25.2 | 21.9 | 22.3 | 22.6 | 22.8 | 23.3 | 24 | 24.4 | 24.8 | 26.1 | 27.4
SVTS34 | Split Bus | 66 | MVA | 155.7 | 185.7 | 187.7 | 189.8 | 190.5 | 193.3 | 197 | 199.2 | 201.6 | 208.6 | 215.5
TBTS | Entire | 66 | MW | 292.6 | 274 | 277.1 | 280.2 | 282.5 | 284.1 | 286.6 | 291.5 | 296.3 | 301.3 | 304.8
TBTS | Entire | 66 | MVAr | 68.6 | 50 | 51.2 | 52.4 | 53.2 | 53.8 | 54.8 | 56.6 | 58.4 | 60.3 | 61.6
TBTS | Entire | 66 | MVA | 300.5 | 278.5 | 281.8 | 285.1 | 287.5 | 289.2 | 291.8 | 296.9 | 302 | 307.3 | 310.9
TGTS | Entire | 66 | MW | 136.97 | 154.71 | 160.47 | 159.08 | 157.65 | 156.17 | 155.34 | 155.22 | 154.99 | 155.81 | 156.66
TGTS | Entire | 66 | MVAr | 5.14 | 9.33 | 10.33 | 10.09 | 9.84 | 9.58 | 9.44 | 9.42 | 9.38 | 9.52 | 9.67
TGTS | Entire | 66 | MVA | 137.0664 | 154.9911 | 160.8021 | 159.3997 | 157.9568 | 156.4636 | 155.6266 | 155.5056 | 155.2736 | 156.1006 | 156.9582
TSTS | Entire | 66 | MW | 294.2 | 299.9 | 304.9 | 310.8 | 315.6 | 321.4 | 328.8 | 337.1 | 345.3 | 357.1 | 368.4
TSTS | Entire | 66 | MVAr | 64.2 | 71.6 | 73.6 | 76 | 77.8 | 80.2 | 83.3 | 86.8 | 90.4 | 95.3 | 100.2
TSTS | Entire | 66 | MVA | 301.2 | 308.4 | 313.6 | 319.9 | 325 | 331.2 | 339.2 | 348.1 | 356.9 | 369.6 | 381.8
TTS | Entire | 66 | MW | 458.6502 | 442.2167 | 456.1369 | 473.3718 | 480.1581 | 487.7879 | 499.0922 | 512.115 | 529.9225 | 544.5956 | 558.5974
TTS | Entire | 66 | MVAr | 97.9715 | 119.1521 | 123.2337 | 128.3894 | 130.1711 | 132.1658 | 135.2375 | 138.7856 | 143.8546 | 147.8415 | 151.6432
TTS | Entire | 66 | MVA | 469.1286 | 457.9878 | 472.4906 | 490.4739 | 497.49 | 505.3759 | 517.0901 | 530.5876 | 549.1011 | 564.3062 | 578.8149
TTS12 | Split Bus | 66 | MW | 217.6421 | 208.2289 | 215.9052 | 227.7756 | 231.0183 | 234.9386 | 239.7294 | 245.1788 | 254.81 | 261.0579 | 267.0212
TTS12 | Split Bus | 66 | MVAr | 42.1375 | 52.1277 | 54.4227 | 58.0422 | 58.808 | 59.7388 | 60.9455 | 62.3253 | 65.0534 | 66.6279 | 68.1279
TTS12 | Split Bus | 66 | MVA | 221.6837 | 214.6546 | 222.6587 | 235.0545 | 238.3859 | 242.4147 | 247.3551 | 252.9764 | 262.983 | 269.4263 | 275.5753
TTS34 | Split Bus | 66 | MW | 241.0081 | 235.6729 | 241.9344 | 247.3314 | 250.9131 | 254.6675 | 261.2179 | 268.8313 | 277.0499 | 285.5229 | 293.6078
TTS34 | Split Bus | 66 | MVAr | 55.8341 | 67.3832 | 69.1735 | 70.7166 | 71.7407 | 72.8141 | 74.687 | 76.8638 | 79.2136 | 81.6362 | 83.9479
TTS34 | Split Bus | 66 | MVA | 247.3911 | 245.1167 | 251.6291 | 257.2424 | 260.9677 | 264.8724 | 271.6854 | 279.6039 | 288.1517 | 296.9643 | 305.3732
WETS | Entire | 66 | MW | 57.44 | 70.83 | 70.31 | 69 | 67.83 | 66.71 | 65.69 | 64.83 | 64.14 | 63.54 | 63.06
WETS | Entire | 66 | MVAr | 6.88 | 14.1 | 13.86 | 13.25 | 12.71 | 12.19 | 11.71 | 11.31 | 10.99 | 10.71 | 10.49
WETS | Entire | 66 | MVA | 57.85 | 72.22 | 71.66 | 70.26 | 69.01 | 67.81 | 66.73 | 65.81 | 65.07 | 64.44 | 63.93
WMTS | Entire | 22 | MW | 13.51 | 40.5 | 41.54 | 42.13 | 42.44 | 42.43 | 42.51 | 42.7 | 43.05 | 43.52 | 44.15
WMTS | Entire | 22 | MVAr | 1.32 | 8.09 | 8.18 | 8.23 | 8.26 | 8.26 | 8.27 | 8.28 | 8.31 | 8.36 | 8.41
WMTS | Entire | 22 | MVA | 13.5743 | 41.3 | 42.34 | 42.93 | 43.24 | 43.23 | 43.31 | 43.5 | 43.84 | 44.32 | 44.94
WMTS | Entire | 66 | MW | 288.2 | 314.8509 | 343.9775 | 355.7274 | 367.0413 | 380.5383 | 394.0921 | 408.1165 | 422.1446 | 437.6533 | 455.8883
WMTS | Entire | 66 | MVAr | 68.4 | 86.2155 | 101.6496 | 107.3062 | 112.74 | 119.4145 | 126.3486 | 133.4351 | 140.4692 | 148.3025 | 157.6916
WMTS | Entire | 66 | MVA | 296.2 | 326.4417 | 358.6826 | 371.5597 | 383.9657 | 398.8348 | 413.8509 | 429.3763 | 444.9018 | 462.0974 | 482.3907
WOTS | Entire | 66 | MW | 48.64 | 49.3794 | 50.0978 | 50.9462 | 51.9358 | 53.038 | 53.9234 | 54.8739 | 55.8105 | 56.7881 | 57.6835
WOTS | Entire | 66 | MVAr | 11.72 | 11.8992 | 12.1053 | 12.3439 | 12.6165 | 12.9329 | 13.2016 | 13.4791 | 13.7562 | 14.0431 | 14.3123
WOTS | Entire | 66 | MVA | 50.0321 | 50.551 | 51.2906 | 52.1636 | 53.181 | 54.3158 | 55.2292 | 56.2084 | 57.1738 | 58.1811 | 59.1045
WOTS22 | Entire | 22 | MW | 32 | 31.2086 | 31.9942 | 32.8738 | 33.8422 | 35.049 | 36.1646 | 37.2521 | 38.3605 | 39.4939 | 40.5975
WOTS22 | Entire | 22 | MVAr | 2.64 | 2.4516 | 2.5133 | 2.5824 | 2.6584 | 2.7532 | 2.8409 | 2.9263 | 3.0134 | 3.1024 | 3.1891
WOTS22 | Entire | 22 | MVA | 32.1087 | 31.3048 | 32.0928 | 32.9751 | 33.9465 | 35.1569 | 36.276 | 37.3669 | 38.4787 | 39.6156 | 40.7226
Note 1: Note that this is the observed actual and have not been weather normalised.

## TsWinter10_maximum
2023 Terminal Station Maximum Demand Forecast - MW, MVAr & MVA Forecasts aggregated by Terminal Station
Forecasts at time of Station peak - station diversity factors are applied.
Winter, 10% POE
LOCATIONID | LocationType | VOLTAGE | UNIT | 2022 (Actual Note 1) | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033
ATS_BLTS | Hybrid | 66 | MW | 255 | 277.4 | 311.1 | 339.5 | 376.3 | 390.6 | 415.3 | 418.6 | 421.8 | 425.5 | 429.2 | 445.7
ATS_BLTS | Hybrid | 66 | MVAr | 59.7 | 94.6 | 114.4 | 130.3 | 144.1 | 152.2 | 167.4 | 169 | 170.7 | 172.5 | 174.4 | 180.6
ATS_BLTS | Hybrid | 66 | MVA | 261.9 | 293.1 | 331.4 | 363.6 | 402.9 | 419.2 | 447.7 | 451.4 | 455.1 | 459.1 | 463.3 | 480.9
ATS_WEST | Hybrid | 66 | MW | 159 | 177.5 | 200.3 | 213.9 | 225.9 | 238.8 | 253.4 | 268.6 | 284.9 | 298.2 | 311.8 | 327.5
ATS_WEST | Hybrid | 66 | MVAr | 25.9 | 20.7 | 27.1 | 31 | 34.3 | 38 | 42.1 | 46.4 | 50.9 | 54.7 | 58.5 | 62.9
ATS_WEST | Hybrid | 66 | MVA | 161.1 | 178.7 | 202.1 | 216.2 | 228.5 | 241.8 | 256.9 | 272.6 | 289.4 | 303.2 | 317.3 | 333.5
BATS | Entire | 66 | MW | 171 | 188.5 | 202.7 | 207.7 | 211.2 | 215.9 | 222.3 | 228.5 | 234.8 | 239.1 | 245.3 | 251.7
BATS | Entire | 66 | MVAr | 16.5 | 29.4 | 33 | 34.3 | 35.2 | 36.4 | 38.1 | 39.7 | 41.3 | 42.4 | 44.1 | 45.7
BATS | Entire | 66 | MVA | 171.8 | 190.7 | 205.4 | 210.5 | 214.1 | 218.9 | 225.5 | 231.9 | 238.4 | 242.8 | 249.3 | 255.8
BETS | Entire | 22 | MW | 60.9 | 61.1 | 64.9 | 66.4 | 67.4 | 68.8 | 70.2 | 71.7 | 73.3 | 74.4 | 75.8 | 78
BETS | Entire | 22 | MVAr | 0 | 4.9 | 5 | 5 | 5.1 | 5.1 | 5.2 | 5.2 | 5.2 | 5.3 | 5.3 | 5.4
BETS | Entire | 22 | MVA | 60.9 | 61.3 | 65.1 | 66.6 | 67.6 | 69 | 70.4 | 71.8 | 73.5 | 74.6 | 76 | 78.1
BETS | Entire | 66 | MW | 131.8 | 139.6 | 149.4 | 152.2 | 153 | 154.3 | 155.8 | 157.7 | 160.1 | 161.5 | 163.3 | 166.6
BETS | Entire | 66 | MVAr | 12.5 | 15.6 | 18.8 | 19.8 | 20 | 20.5 | 21 | 21.6 | 22.4 | 22.9 | 23.5 | 24.6
BETS | Entire | 66 | MVA | 132.4 | 140.4 | 150.6 | 153.4 | 154.3 | 155.6 | 157.2 | 159.1 | 161.7 | 163.2 | 165 | 168.4
BLTS | Entire | 22 | MW | 40.6 | 64.4 | 69.2 | 73.4 | 79.3 | 80.2 | 81 | 82.2 | 83.6 | 84.3 | 85.2 | 85.2
BLTS | Entire | 22 | MVAr | 12.5 | 25.1 | 27.1 | 28.9 | 30.9 | 31.3 | 31.6 | 32.1 | 32.7 | 33 | 33.4 | 33.4
BLTS | Entire | 22 | MVA | 42.5 | 69.2 | 74.3 | 78.9 | 85.1 | 86.1 | 87 | 88.3 | 89.7 | 90.5 | 91.5 | 91.5
BLTS-SCI | Hybrid | 66 | MW
BLTS-SCI | Hybrid | 66 | MVAr
BLTS-SCI | Hybrid | 66 | MVA
BTS | Entire | 22 | MW | 93.259 | 85.3263 | 85.3808 | 89.2902 | 92.9085 | 96.8675 | 101.0971 | 104.7692 | 109.7074 | 115.7813 | 122.342 | 128.9872
BTS | Entire | 22 | MVAr | 14.1109 | 15.0759 | 15.1279 | 15.9626 | 16.7294 | 17.5874 | 18.5069 | 19.3088 | 20.3941 | 21.7074 | 23.1166 | 24.5529
BTS | Entire | 22 | MVA | 94.3205 | 86.6479 | 86.7107 | 90.7058 | 94.4027 | 98.4511 | 102.777 | 106.5336 | 111.5869 | 117.7987 | 124.5068 | 131.3033
BTS | Entire | 66 | MW | 172.5 | 289.9 | 330.9 | 352.9 | 366.7 | 379.2 | 397 | 417.4 | 437.5 | 454.7 | 472.9 | 492.4
BTS | Entire | 66 | MVAr | 19.5 | 90.3 | 112.2 | 124 | 131.4 | 138.1 | 147.6 | 158.5 | 169.2 | 178.4 | 188.2 | 198.6
BTS | Entire | 66 | MVA | 173.6 | 303.7 | 349.4 | 374.1 | 389.5 | 403.6 | 423.5 | 446.4 | 469 | 488.4 | 509 | 530.9
CBTS | Entire | 66 | MW | 382.8289 | 415.422 | 436.3347 | 457.4296 | 480.2962 | 505.3354 | 528.8738 | 551.6589 | 573.747 | 593.1901 | 614.4497 | 635.633
CBTS | Entire | 66 | MVAr | 49.9625 | 63.5041 | 69.4292 | 74.7527 | 80.2225 | 85.9702 | 91.7672 | 97.1091 | 102.1073 | 105.6559 | 110.144 | 114.6
CBTS | Entire | 66 | MVA | 386.0754 | 420.2478 | 441.8239 | 463.4973 | 486.9498 | 512.5961 | 536.7762 | 560.1408 | 582.762 | 602.5261 | 624.2437 | 645.8812
DPTS | Hybrid | 66 | MW | 206.79 | 249.11 | 315.01 | 335.64 | 350.14 | 366.15 | 383.98 | 403.89 | 424.3 | 440.99 | 458.09 | 476.41
DPTS | Hybrid | 66 | MVAr | 32.3 | 45.27 | 71.97 | 80.33 | 86.2 | 92.69 | 99.91 | 107.98 | 116.25 | 123.01 | 129.93 | 137.36
DPTS | Hybrid | 66 | MVA | 209.3 | 253.19 | 323.13 | 345.12 | 360.59 | 377.7 | 396.77 | 418.08 | 439.94 | 457.82 | 476.16 | 495.82
ERTS | Entire | 66 | MW | 409.7 | 428.8 | 441.8 | 457.6 | 467.3 | 477.8 | 492.6 | 502.1 | 512.5 | 521 | 525.3 | 538
ERTS | Entire | 66 | MVAr | 88.8 | 77.6 | 82.1 | 87.4 | 89.8 | 92.2 | 96.8 | 99.3 | 102.1 | 104.2 | 104.5 | 108.2
ERTS | Entire | 66 | MVA | 419.2 | 435.7 | 449.4 | 465.9 | 475.8 | 486.6 | 502.1 | 511.9 | 522.6 | 531.3 | 535.6 | 548.8
ERTS12 | Split Bus | 66 | MW | 163.4 | 211.2 | 217.5 | 225.3 | 230.5 | 236.1 | 243.7 | 248.8 | 254.3 | 258.9 | 261.6 | 267.9
ERTS12 | Split Bus | 66 | MVAr | 9.1 | 15.4 | 16.3 | 17.2 | 17.8 | 18.3 | 19.2 | 19.8 | 20.4 | 20.8 | 21 | 21.7
ERTS12 | Split Bus | 66 | MVA | 163.6 | 211.7 | 218.2 | 226 | 231.2 | 236.8 | 244.5 | 249.6 | 255.1 | 259.7 | 262.4 | 268.8
ERTS34 | Split Bus | 66 | MW | 256.8 | 226.8 | 234 | 242.6 | 247.4 | 252.4 | 260.3 | 264.9 | 270.1 | 274.2 | 275.7 | 282.4
ERTS34 | Split Bus | 66 | MVAr | 74.1 | 65.8 | 69.8 | 74.5 | 76.8 | 79.1 | 83.3 | 85.5 | 88.1 | 90 | 90.4 | 93.8
ERTS34 | Split Bus | 66 | MVA | 267.3 | 236.2 | 244.2 | 253.8 | 259 | 264.6 | 273.3 | 278.4 | 284.1 | 288.6 | 290.1 | 297.6
FBTS | Entire | 66 | MW | 191.3 | 226.59 | 256.38 | 272.48 | 281.8 | 289.28 | 295.97 | 306.03 | 319.91 | 330.22 | 341.31 | 351.6
FBTS | Entire | 66 | MVAr | 39.8 | 60.21 | 74.3 | 81.92 | 86.34 | 89.87 | 93.04 | 97.8 | 104.37 | 109.25 | 114.5 | 119.37
FBTS | Entire | 66 | MVA | 195.4 | 234.45 | 266.93 | 284.53 | 294.73 | 302.92 | 310.25 | 321.28 | 336.5 | 347.82 | 360 | 371.31
GNTS | Entire | 66 | MW | 101.5 | 103.036 | 104.476 | 106.141 | 108.017 | 110.161 | 111.906 | 113.68 | 115.448 | 117.232 | 118.91 | 120.557
GNTS | Entire | 66 | MVAr | 26.7 | 27.1041 | 27.4828 | 27.9208 | 28.4143 | 28.9783 | 29.4373 | 29.904 | 30.3691 | 30.8384 | 31.2798 | 31.713
GNTS | Entire | 66 | MVA | 104.953 | 106.5413 | 108.0303 | 109.7519 | 111.6917 | 113.9087 | 115.713 | 117.5474 | 119.3755 | 121.2202 | 122.9553 | 124.6584
GTS | Entire | 66 | MW | 381.56 | 434.47 | 487.49 | 505.56 | 512.68 | 522.62 | 533.3 | 543.75 | 557.4 | 567.68 | 578.4 | 591.47
GTS | Entire | 66 | MVAr | 84.27 | 83.17 | 102.85 | 109.71 | 112.36 | 115.59 | 118.99 | 122.46 | 126.94 | 130.17 | 133.37 | 137.65
GTS | Entire | 66 | MVA | 390.82 | 443.5 | 499.86 | 519.15 | 526.74 | 537.21 | 548.45 | 559.49 | 573.9 | 584.71 | 595.94 | 609.74
HOTS | Entire | 66 | MW | 71.65 | 75.57 | 83.01 | 83.24 | 82.34 | 81.63 | 81 | 80.6 | 80.4 | 79.89 | 79.92 | 79.99
HOTS | Entire | 66 | MVAr | 0.55 | -0.32 | 0.51 | 0.54 | 0.44 | 0.36 | 0.29 | 0.24 | 0.22 | 0.16 | 0.17 | 0.18
HOTS | Entire | 66 | MVA | 71.65 | 75.57 | 83.01 | 83.24 | 82.34 | 81.63 | 81 | 80.6 | 80.4 | 79.89 | 79.92 | 79.99
HTS | Entire | 66 | MW | 279.2 | 287.8 | 299.9 | 312.8 | 321.2 | 330.6 | 342.7 | 352.3 | 360.8 | 368.1 | 375.5 | 384.8
HTS | Entire | 66 | MVAr | 53.4 | 57.5 | 62.8 | 68.5 | 72.2 | 76.4 | 81.7 | 86 | 89.7 | 92.9 | 96.2 | 100.3
HTS | Entire | 66 | MVA | 284.2 | 293.5 | 306.4 | 320.2 | 329.2 | 339.3 | 352.3 | 362.6 | 371.8 | 379.6 | 387.6 | 397.7
HYTS | Entire | 22 | MW | 1.51 | 2.48 | 2.45 | 2.41 | 2.37 | 2.32 | 2.28 | 2.24 | 2.21 | 2.19 | 2.17 | 2.14
HYTS | Entire | 22 | MVAr | 0.38 | 0.76 | 0.75 | 0.74 | 0.72 | 0.71 | 0.69 | 0.68 | 0.67 | 0.66 | 0.66 | 0.65
HYTS | Entire | 22 | MVA | 1.56 | 2.59 | 2.56 | 2.52 | 2.48 | 2.43 | 2.38 | 2.34 | 2.31 | 2.29 | 2.27 | 2.24
KGTS | Entire | 22 | MW | 7.14 | 9.94 | 11.19 | 11.16 | 11.02 | 10.82 | 10.73 | 10.61 | 10.51 | 10.4 | 10.42 | 10.57
KGTS | Entire | 22 | MVAr | 0 | -0.46 | -0.7 | -0.7 | -0.65 | -0.61 | -0.58 | -0.55 | -0.54 | -0.52 | -0.52 | -0.51
KGTS | Entire | 22 | MVA | 7.14 | 9.9506 | 11.2119 | 11.1819 | 11.0392 | 10.8372 | 10.7457 | 10.6242 | 10.5239 | 10.413 | 10.433 | 10.5823
KGTS | Entire | 66 | MW | 56.27 | 54.85 | 59.29 | 59.76 | 58.67 | 57.63 | 56.61 | 55.77 | 55.15 | 54.69 | 54.21 | 53.88
KGTS | Entire | 66 | MVAr | -4.99 | -0.32 | 0.89 | 1.02 | 0.72 | 0.44 | 0.16 | -0.07 | -0.24 | -0.37 | -0.5 | -0.59
KGTS | Entire | 66 | MVA | 56.49 | 54.85 | 59.3 | 59.77 | 58.67 | 57.63 | 56.61 | 55.77 | 55.15 | 54.69 | 54.21 | 53.88
KTS | Entire | 66 | MW | 444.9138 | 457.97 | 476.2002 | 505.6181 | 567.454 | 601.5745 | 635.4665 | 693.569 | 744.85 | 805.4037 | 842.3135 | 871.5803
KTS | Entire | 66 | MVAr | 129.0024 | 88.3393 | 94.3111 | 102.0074 | 112.9837 | 119.4022 | 126.7067 | 137.4976 | 148.716 | 158.6292 | 163.3354 | 168.687
KTS | Entire | 66 | MVA | 468.4185 | 466.8367 | 485.8284 | 516.203 | 578.8942 | 613.5661 | 648.2048 | 707.2341 | 759.6923 | 820.9676 | 858.0539 | 887.7848
KTS_East | Split Bus | 66 | MW | 232.9624 | 249.0194 | 253.5585 | 271.9115 | 324.1597 | 348.9233 | 373.1063 | 421.0463 | 461.6425 | 513.7151 | 541.9057 | 561.3822
KTS_East | Split Bus | 66 | MVAr | 103.5673 | 58.1233 | 59.9697 | 65.154 | 73.9627 | 78.1705 | 83.0418 | 91.1198 | 99.4117 | 107.1617 | 109.605 | 112.2489
KTS_East | Split Bus | 66 | MVA | 254.9464 | 255.7127 | 260.5538 | 279.6085 | 332.4905 | 357.5725 | 382.2359 | 430.7932 | 472.2251 | 524.7732 | 552.8788 | 572.4943
KTS_West | Split Bus | 66 | MW | 211.9514 | 208.9506 | 222.6417 | 233.7066 | 243.2944 | 252.6513 | 262.3602 | 272.5227 | 283.2075 | 291.6886 | 300.4078 | 310.1981
KTS_West | Split Bus | 66 | MVAr | 25.4351 | 30.216 | 34.3414 | 36.8534 | 39.021 | 41.2317 | 43.665 | 46.3779 | 49.3042 | 51.4675 | 53.7304 | 56.4381
KTS_West | Split Bus | 66 | MVA | 213.4721 | 211.1241 | 225.2746 | 236.5945 | 246.4037 | 255.9936 | 265.9689 | 276.4409 | 287.4672 | 296.1944 | 305.1751 | 315.2905
LY* | Entire | 66 | MW | 25.88 | 29.426 | 29.427 | 29.429 | 29.431 | 29.433 | 29.436 | 29.438 | 29.441 | 29.443 | 29.445 | 29.446
LY* | Entire | 66 | MVAr | 12.2 | 13.8716 | 13.8721 | 13.873 | 13.874 | 13.8749 | 13.8763 | 13.8773 | 13.8787 | 13.8796 | 13.8806 | 13.881
LY* | Entire | 66 | MVA | 28.6114 | 32.5317 | 32.5328 | 32.535 | 32.5372 | 32.5394 | 32.5427 | 32.545 | 32.5483 | 32.5505 | 32.5527 | 32.5538
MBTS | Entire | 66 | MW | 40.2 | 43.177 | 43.661 | 44.176 | 44.674 | 45.207 | 45.736 | 46.265 | 46.81 | 47.339 | 47.802 | 48.233
MBTS | Entire | 66 | MVAr | 2.4 | 2.5777 | 2.6066 | 2.6374 | 2.6671 | 2.6989 | 2.7305 | 2.7621 | 2.7946 | 2.8262 | 2.8539 | 2.8796
MBTS | Entire | 66 | MVA | 40.2716 | 43.2539 | 43.7387 | 44.2547 | 44.7535 | 45.2875 | 45.8174 | 46.3474 | 46.8933 | 47.4233 | 47.8871 | 48.3189
MTS | Entire | 22 | MW | 33.3 | 34.5 | 35.1 | 35.8 | 36.4 | 36.9 | 37.3 | 37.7 | 38.2 | 38.6 | 39.2 | 39.6
MTS | Entire | 22 | MVAr | 3.1 | 2.7 | 2.8 | 3 | 3.1 | 3.2 | 3.2 | 3.3 | 3.4 | 3.5 | 3.6 | 3.7
MTS | Entire | 22 | MVA | 33.4 | 34.6 | 35.2 | 35.9 | 36.6 | 37 | 37.4 | 37.8 | 38.3 | 38.8 | 39.3 | 39.8
MTS | Entire | 66 | MW | 132.5 | 139 | 148.8 | 160.2 | 169.2 | 177.5 | 187.6 | 196.1 | 205.3 | 210.5 | 216.4 | 223
MTS | Entire | 66 | MVAr | 8.6 | 11.4 | 14.5 | 18.1 | 21 | 23.6 | 26.9 | 29.6 | 32.5 | 34.2 | 36.1 | 38.2
MTS | Entire | 66 | MVA | 132.8 | 139.5 | 149.5 | 161.2 | 170.5 | 179 | 189.5 | 198.3 | 207.9 | 213.2 | 219.3 | 226.2
MTS6622 | Entire | 66 | MW | 163.1 | 173.6 | 183.9 | 196 | 205.6 | 214.4 | 224.8 | 233.8 | 243.5 | 249.1 | 255.5 | 262.6
MTS6622 | Entire | 66 | MVAr | 10.3 | 14.1 | 17.3 | 21.1 | 24.1 | 26.8 | 30.1 | 32.9 | 36 | 37.7 | 39.7 | 41.9
MTS6622 | Entire | 66 | MVA | 163.5 | 174.1 | 184.7 | 197.1 | 207 | 216 | 226.8 | 236.1 | 246.1 | 252 | 258.6 | 265.9
MWTS | Entire | 66 | MW | 422.32 | 456.728 | 467.961 | 480.268 | 493.455 | 507.83 | 520.423 | 533.069 | 546.098 | 559.65 | 572.966 | 586.039
MWTS | Entire | 66 | MVAr | 47.3 | 51.1537 | 52.4118 | 53.7902 | 55.2671 | 56.8772 | 58.2876 | 59.7039 | 61.1632 | 62.681 | 64.1724 | 65.6366
MWTS | Entire | 66 | MVA | 424.9606 | 459.5837 | 470.8869 | 483.2709 | 496.5403 | 511.0052 | 523.6769 | 536.402 | 549.5125 | 563.1492 | 576.5485 | 589.7032
RCTS | Entire | 22 | MW | 26.21 | 31.36 | 34.17 | 35.22 | 34.93 | 34.65 | 34.34 | 34.14 | 34.11 | 34.04 | 34.06 | 34.27
RCTS | Entire | 22 | MVAr | -0.63 | 0.25 | 0.28 | 0.29 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28
RCTS | Entire | 22 | MVA | 26.2176 | 31.36 | 34.17 | 35.22 | 34.93 | 34.65 | 34.34 | 34.14 | 34.11 | 34.04 | 34.06 | 34.27
RCTS | Entire | 66 | MW | 86.28 | 118.62 | 126.37 | 126.37 | 124.95 | 123.59 | 122.56 | 121.67 | 121.26 | 121.1 | 121.15 | 121.86
RCTS | Entire | 66 | MVAr | 4.72 | 16.27 | 18.68 | 18.68 | 18.23 | 17.81 | 17.49 | 17.22 | 17.09 | 17.04 | 17.05 | 17.28
RCTS | Entire | 66 | MVA | 86.41 | 119.7306 | 127.7432 | 127.7432 | 126.2729 | 124.8667 | 123.8017 | 122.8825 | 122.4584 | 122.293 | 122.3439 | 123.0791
RTS | Entire | 22 | MW | 33.2 | 48.7 | 60.3 | 78.4 | 80.6 | 81.7 | 82.8 | 84 | 85.4 | 86.2 | 87.2 | 88
RTS | Entire | 22 | MVAr | 5.1 | 9.7 | 13.4 | 19.2 | 19.9 | 20.2 | 20.6 | 21 | 21.4 | 21.7 | 22 | 22.2
RTS | Entire | 22 | MVA | 33.5 | 49.7 | 61.8 | 80.7 | 83 | 84.2 | 85.3 | 86.5 | 88 | 88.9 | 89.9 | 90.8
RTS | Entire | 66 | MW | 348.72 | 470.169 | 519.14 | 551.7469 | 574.5305 | 588.6284 | 604.5879 | 622.8018 | 647.0983 | 666.2118 | 688.9655 | 712.1297
RTS | Entire | 66 | MVAr | 47.69 | 94.2602 | 116.3243 | 130.8481 | 140.8885 | 146.9698 | 153.8998 | 161.8784 | 172.6997 | 181.2559 | 191.5079 | 201.9057
RTS | Entire | 66 | MVA | 351.9659 | 479.5246 | 532.0129 | 567.0501 | 591.5529 | 606.6989 | 623.8683 | 643.4957 | 669.7473 | 690.4288 | 715.0866 | 740.199
RWTS | Entire | 66 | MW | 344.47 | 373.9439 | 387.0259 | 401.4437 | 415.749 | 432.3403 | 447.5865 | 462.4154 | 476.9609 | 490.8018 | 504.1739 | 517.7104
RWTS | Entire | 66 | MVAr | 69.13 | 88.3371 | 92.3623 | 96.6514 | 100.6919 | 105.2621 | 109.6059 | 113.7801 | 117.8595 | 121.6707 | 125.3169 | 128.9735
RWTS | Entire | 66 | MVA | 351.3382 | 384.2362 | 397.8942 | 412.9147 | 427.7687 | 444.9699 | 460.8114 | 476.2079 | 491.307 | 505.6582 | 519.5148 | 533.5337
RWTS13 | Split Bus | 66 | MW | 207.18 | 222.3074 | 232.583 | 243.2471 | 252.8881 | 263.5699 | 274.1677 | 284.2518 | 293.996 | 302.8859 | 311.2781 | 319.5659
RWTS13 | Split Bus | 66 | MVAr | 27.84 | 49.3815 | 52.6858 | 56.0106 | 58.8527 | 61.9049 | 65.0545 | 68.0098 | 70.8557 | 73.395 | 75.7618 | 78.0701
RWTS13 | Split Bus | 66 | MVA | 209.0421 | 227.726 | 238.4757 | 249.6124 | 259.646 | 270.7421 | 281.7801 | 292.2746 | 302.4139 | 311.6516 | 320.3653 | 328.964
RWTS22 | Entire | 22 | MW | 65.57 | 67.82 | 69.907 | 72.418 | 75.2284 | 78.1759 | 80.9619 | 83.7783 | 86.5414 | 88.9303 | 91.3308 | 93.7487
RWTS22 | Entire | 22 | MVAr | 2.63 | 2.7806 | 2.858 | 2.9537 | 3.0663 | 3.1891 | 3.2947 | 3.4054 | 3.5141 | 3.6181 | 3.7229 | 3.8279
RWTS22 | Entire | 22 | MVA | 65.6227 | 67.8769 | 69.9654 | 72.4782 | 75.2909 | 78.2409 | 81.0289 | 83.8475 | 86.6127 | 89.0038 | 91.4067 | 93.8268
RWTS24 | Split Bus | 66 | MW | 146.36 | 151.6365 | 154.4428 | 158.1966 | 162.861 | 168.7703 | 173.4188 | 178.1636 | 182.9649 | 187.916 | 192.8958 | 198.1445
RWTS24 | Split Bus | 66 | MVAr | 37.6 | 38.9555 | 39.6765 | 40.6408 | 41.8391 | 43.3572 | 44.5514 | 45.7704 | 47.0038 | 48.2758 | 49.5551 | 50.9035
RWTS24 | Split Bus | 66 | MVA | 151.1126 | 156.5604 | 159.4578 | 163.3335 | 168.1494 | 174.2506 | 179.05 | 183.9489 | 188.9061 | 194.018 | 199.1595 | 204.5786
SHTS | Entire | 66 | MW | 202.57 | 211.13 | 233.22 | 239.68 | 239.56 | 239.61 | 239.75 | 240.58 | 242.07 | 243.23 | 245.3 | 247.97
SHTS | Entire | 66 | MVAr | 39.4 | 33.67 | 44.71 | 47.93 | 47.87 | 47.9 | 47.97 | 48.38 | 49.13 | 49.71 | 50.74 | 52.08
SHTS | Entire | 66 | MVA | 206.37 | 213.7979 | 237.467 | 244.4254 | 244.296 | 244.3509 | 244.5019 | 245.3963 | 247.0053 | 248.2578 | 250.4928 | 253.38
SMTS | Entire | 66 | MW | 299.8706 | 339.8513 | 358.2325 | 381.8261 | 407.8264 | 434.6151 | 458.4045 | 481.4997 | 504.0251 | 526.5639 | 550.8391 | 575.4648
SMTS | Entire | 66 | MVAr | 30.2347 | 42.8237 | 45.4004 | 48.9972 | 52.9486 | 56.6818 | 60.0461 | 63.0872 | 66.081 | 69.0176 | 72.1168 | 75.2444
SMTS | Entire | 66 | MVA | 301.391 | 342.5387 | 361.098 | 384.957 | 411.2492 | 438.2957 | 462.3204 | 485.6151 | 508.3385 | 531.0678 | 555.5399 | 580.3632
SVTS | Entire | 66 | MW | 303 | 323.6 | 342.1 | 357.2 | 368.1 | 379.1 | 394.3 | 407.8 | 422.1 | 431.9 | 439.4 | 451.7
SVTS | Entire | 66 | MVAr | 48.9 | 34.3 | 38 | 40.9 | 43 | 45.1 | 48 | 50.6 | 53.3 | 55.1 | 56.4 | 58.8
SVTS | Entire | 66 | MVA | 306.9 | 325.4 | 344.2 | 359.5 | 370.6 | 381.7 | 397.2 | 410.9 | 425.5 | 435.4 | 443 | 455.5
SVTS12 | Split Bus | 66 | MW | 173.9 | 169.1 | 178.5 | 185.9 | 191.1 | 196.1 | 203.4 | 209.6 | 216.1 | 220.5 | 223.6 | 229.3
SVTS12 | Split Bus | 66 | MVAr | 29.2 | 19.2 | 21.3 | 22.9 | 24.1 | 25.2 | 26.8 | 28.2 | 29.6 | 30.6 | 31.3 | 32.6
SVTS12 | Split Bus | 66 | MVA | 176.4 | 170.1 | 179.7 | 187.3 | 192.6 | 197.7 | 205.1 | 211.5 | 218.2 | 222.6 | 225.8 | 231.6
SVTS34 | Split Bus | 66 | MW | 129 | 157.6 | 166.9 | 174.7 | 180.7 | 186.9 | 195.1 | 202.6 | 210.8 | 216.3 | 221 | 227.8
SVTS34 | Split Bus | 66 | MVAr | 19.7 | 15 | 16.6 | 17.9 | 18.9 | 19.8 | 21.2 | 22.3 | 23.6 | 24.4 | 25.1 | 26.2
SVTS34 | Split Bus | 66 | MVA | 130.5 | 158.3 | 167.8 | 175.7 | 181.7 | 188 | 196.2 | 203.9 | 212.1 | 217.7 | 222.4 | 229.3
TBTS | Entire | 66 | MW | 218.8 | 225.8 | 234.3 | 243.5 | 250.3 | 256.8 | 265.4 | 273 | 281.6 | 286.1 | 288.1 | 293.1
TBTS | Entire | 66 | MVAr | 27 | 32 | 35.2 | 38.6 | 41.1 | 43.6 | 46.8 | 49.7 | 52.9 | 54.6 | 55.3 | 57.2
TBTS | Entire | 66 | MVA | 220.4596 | 228.0562 | 236.9294 | 246.5405 | 253.6519 | 260.475 | 269.4947 | 277.4871 | 286.5257 | 291.2634 | 293.3593 | 298.6293
TGTS | Entire | 66 | MW | 161.05 | 168.47 | 177.08 | 177.8 | 176.72 | 175.99 | 175.76 | 176.02 | 176.67 | 176.71 | 177.05 | 178.84
TGTS | Entire | 66 | MVAr | 1.2 | 11.72 | 13.22 | 13.34 | 13.16 | 13.03 | 12.99 | 13.04 | 13.15 | 13.16 | 13.22 | 13.53
TGTS | Entire | 66 | MVA | 161.0545 | 168.8772 | 177.5728 | 178.2997 | 177.2093 | 176.4717 | 176.2394 | 176.5024 | 177.1587 | 177.1994 | 177.5429 | 179.3511
TSTS | Entire | 66 | MW | 246.7 | 240.3 | 254 | 269.7 | 282.6 | 295.8 | 310.9 | 325.6 | 341.2 | 352.2 | 364.8 | 376.4
TSTS | Entire | 66 | MVAr | 28.4 | 39.1 | 44.8 | 51.1 | 56.2 | 61.3 | 67.4 | 73.4 | 79.9 | 84.4 | 89.5 | 94.2
TSTS | Entire | 66 | MVA | 248.3 | 243.4 | 258 | 274.5 | 288.1 | 302.1 | 318.2 | 333.7 | 350.4 | 362.2 | 375.6 | 388
TTS | Entire | 66 | MW | 399.1533 | 433.9226 | 452.0546 | 480.6912 | 510.1896 | 526.4434 | 540.0057 | 553.2431 | 565.0426 | 582.3587 | 595.2644 | 608.0827
TTS | Entire | 66 | MVAr | 101.164 | 119.579 | 124.6547 | 132.911 | 141.6059 | 146.1266 | 149.904 | 153.5817 | 156.8444 | 161.8437 | 165.4202 | 168.972
TTS | Entire | 66 | MVA | 412.1914 | 450.0977 | 468.9266 | 498.7277 | 529.4768 | 546.3476 | 560.4261 | 574.1648 | 586.4072 | 604.4295 | 617.8216 | 631.1229
TTS12 | Split Bus | 66 | MW | 186.2316 | 198.6793 | 205.7886 | 218.942 | 235.0577 | 241.7061 | 247.1789 | 252.6609 | 257.7768 | 267.2078 | 272.6791 | 278.1184
TTS12 | Split Bus | 66 | MVAr | 37.9713 | 48.7601 | 50.5173 | 54.115 | 58.7859 | 60.4158 | 61.7585 | 63.1021 | 64.3534 | 66.9812 | 68.3204 | 69.6514
TTS12 | Split Bus | 66 | MVA | 190.0632 | 204.5752 | 211.8984 | 225.5306 | 242.2971 | 249.1424 | 254.7774 | 260.4216 | 265.6883 | 275.475 | 281.1077 | 286.7075
TTS34 | Split Bus | 66 | MW | 212.9217 | 240.6566 | 251.9346 | 267.8268 | 281.6248 | 291.4349 | 299.6976 | 307.6187 | 314.4439 | 322.5555 | 330.1474 | 337.6823
TTS34 | Split Bus | 66 | MVAr | 63.1927 | 72.3545 | 75.7453 | 80.5234 | 84.6718 | 87.6213 | 90.1055 | 92.487 | 94.5391 | 96.9779 | 99.2604 | 101.5258
TTS34 | Split Bus | 66 | MVA | 222.1012 | 251.2982 | 263.0749 | 279.6699 | 294.0779 | 304.3219 | 312.9499 | 321.2213 | 328.3483 | 336.8186 | 344.7462 | 352.6143
WETS | Entire | 66 | MW | 29.22 | 45.95 | 47.9 | 47.38 | 46.59 | 45.88 | 45.21 | 44.6 | 44.11 | 43.71 | 43.38 | 43.1
WETS | Entire | 66 | MVAr | 3.54 | 2.52 | 3.43 | 3.19 | 2.82 | 2.49 | 2.18 | 1.89 | 1.67 | 1.48 | 1.33 | 1.2
WETS | Entire | 66 | MVA | 29.44 | 46.02 | 48.02 | 47.49 | 46.68 | 45.95 | 45.26 | 44.64 | 44.14 | 43.74 | 43.4 | 43.12
WMTS | Entire | 22 | MW | 26.91 | 42.81 | 43.6 | 44.2 | 44.72 | 44.99 | 44.9 | 44.91 | 45.01 | 45.3 | 45.7 | 45.93
WMTS | Entire | 22 | MVAr | 4.57 | 8.29 | 8.36 | 8.42 | 8.46 | 8.49 | 8.48 | 8.48 | 8.49 | 8.52 | 8.55 | 8.57
WMTS | Entire | 22 | MVA | 27.2953 | 43.61 | 44.39 | 44.99 | 45.51 | 45.78 | 45.69 | 45.7 | 45.8 | 46.09 | 46.49 | 46.72
WMTS | Entire | 66 | MW | 211.54 | 256.8405 | 278.7106 | 299.0157 | 314.3193 | 337.047 | 357.4102 | 377.6671 | 398.0438 | 416.7285 | 433.8878 | 457.185
WMTS | Entire | 66 | MVAr | 24.75 | 55.5076 | 65.2576 | 74.6609 | 81.284 | 92.14 | 101.8558 | 112.1323 | 122.5444 | 132.0819 | 140.8203 | 152.9939
WMTS | Entire | 66 | MVA | 212.98 | 262.7701 | 286.2484 | 308.1958 | 324.6594 | 349.4144 | 371.6405 | 393.962 | 416.4805 | 437.1593 | 456.1677 | 482.1051
WOTS | Entire | 66 | MW | 42.76 | 43.603 | 44.423 | 45.371 | 46.448 | 47.61 | 48.491 | 49.401 | 50.38 | 51.376 | 52.341 | 53.3
WOTS | Entire | 66 | MVAr | 7.44 | 6.9925 | 7.1509 | 7.3307 | 7.5311 | 7.7565 | 7.94 | 8.1263 | 8.3201 | 8.518 | 8.7099 | 8.8998
WOTS | Entire | 66 | MVA | 43.4024 | 43.9603 | 44.7885 | 45.7458 | 46.8332 | 48.0068 | 48.8974 | 49.817 | 50.8061 | 51.8124 | 52.7873 | 53.7562
WOTS22 | Entire | 22 | MW | 30.08 | 32.828 | 33.766 | 34.811 | 35.952 | 37.292 | 38.458 | 39.624 | 40.8 | 42.005 | 43.174 | 44.327
WOTS22 | Entire | 22 | MVAr | -0.4 | 0.43654 | 0.44902 | 0.46291 | 0.47809 | 0.4959 | 0.51141 | 0.52691 | 0.54255 | 0.55858 | 0.57412 | 0.58945
WOTS22 | Entire | 22 | MVA | 30.0827 | 32.8309 | 33.769 | 34.8141 | 35.9552 | 37.2953 | 38.4614 | 39.6275 | 40.8036 | 42.0087 | 43.1778 | 44.3309
Note 1: Note that this is the observed actual and have not been weather normalised.

## TsWinter50_maximum
2023 Terminal Station Maximum Demand Forecast - MW, MVAr & MVA Forecasts aggregated by Terminal Station
Forecasts at time of Station peak - station diversity factors are applied.
Winter, 50% POE
LOCATIONID | LocationType | VOLTAGE | UNIT | 2022 (Actual Note 1) | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033
ATS_BLTS | Hybrid | 66 | MW | 255 | 261 | 294.8 | 322.6 | 359 | 373.1 | 397.6 | 401.1 | 405.2 | 408.6 | 412.5 | 429
ATS_BLTS | Hybrid | 66 | MVAr | 59.7 | 88.2 | 107.9 | 123.7 | 137.4 | 145.4 | 160.5 | 162.2 | 164.2 | 165.9 | 167.9 | 174
ATS_BLTS | Hybrid | 66 | MVA | 261.9 | 275.5 | 313.9 | 345.5 | 384.4 | 400.5 | 428.7 | 432.6 | 437.2 | 441 | 445.3 | 462.9
ATS_WEST | Hybrid | 66 | MW | 159 | 183.8 | 206.9 | 220.7 | 232.8 | 245.7 | 260.5 | 276.2 | 292.7 | 306.3 | 319.8 | 335.8
ATS_WEST | Hybrid | 66 | MVAr | 25.9 | 22.5 | 29 | 32.9 | 36.3 | 39.9 | 44.1 | 48.5 | 53.1 | 57 | 60.8 | 65.3
ATS_WEST | Hybrid | 66 | MVA | 161.1 | 185.2 | 208.9 | 223.2 | 235.6 | 248.9 | 264.2 | 280.4 | 297.5 | 311.6 | 325.5 | 342.1
BATS | Entire | 66 | MW | 171 | 171.7 | 185.4 | 189.9 | 193 | 197.7 | 203.6 | 209.5 | 216.4 | 221.1 | 226.1 | 232.9
BATS | Entire | 66 | MVAr | 16.5 | 25 | 28.6 | 29.7 | 30.5 | 31.8 | 33.3 | 34.8 | 36.6 | 37.8 | 39.1 | 40.9
BATS | Entire | 66 | MVA | 171.8 | 173.5 | 187.6 | 192.2 | 195.4 | 200.3 | 206.3 | 212.3 | 219.5 | 224.3 | 229.5 | 236.5
BETS | Entire | 22 | MW | 60.9 | 58.4 | 62.2 | 63.6 | 64.7 | 66 | 67.3 | 68.8 | 70.5 | 71.6 | 73 | 75.2
BETS | Entire | 22 | MVAr | 0 | 4.8 | 4.9 | 5 | 5 | 5 | 5.1 | 5.1 | 5.2 | 5.2 | 5.2 | 5.3
BETS | Entire | 22 | MVA | 60.9 | 58.6 | 62.4 | 63.8 | 64.8 | 66.2 | 67.5 | 68.9 | 70.7 | 71.8 | 73.2 | 75.4
BETS | Entire | 66 | MW | 131.8 | 133.4 | 143.2 | 146.2 | 147 | 148.3 | 149.9 | 151.7 | 154.1 | 155.3 | 157.2 | 160.4
BETS | Entire | 66 | MVAr | 12.5 | 13.5 | 16.8 | 17.8 | 18.1 | 18.5 | 19 | 19.6 | 20.4 | 20.8 | 21.5 | 22.5
BETS | Entire | 66 | MVA | 132.4 | 134.1 | 144.2 | 147.2 | 148.1 | 149.4 | 151.1 | 153 | 155.4 | 156.7 | 158.6 | 162
BLTS | Entire | 22 | MW | 40.6 | 59.8 | 64.6 | 68.8 | 74.6 | 75.4 | 76.1 | 77.3 | 78.7 | 79.4 | 80.4 | 80.4
BLTS | Entire | 22 | MVAr | 12.5 | 23.2 | 25.2 | 27 | 28.9 | 29.2 | 29.6 | 30 | 30.6 | 30.9 | 31.3 | 31.3
BLTS | Entire | 22 | MVA | 42.5 | 64.1 | 69.3 | 73.9 | 80 | 80.8 | 81.7 | 82.9 | 84.5 | 85.2 | 86.3 | 86.3
BLTS-SCI | Hybrid | 66 | MW
BLTS-SCI | Hybrid | 66 | MVAr
BLTS-SCI | Hybrid | 66 | MVA
BTS | Entire | 22 | MW | 93.259 | 77.4682 | 83.1653 | 87.5222 | 93.3685 | 100.2177 | 106.9843 | 112.1626 | 118.1649 | 123.8673 | 129.6512 | 135.3986
BTS | Entire | 22 | MVAr | 14.1109 | 12.9682 | 13.9013 | 14.6492 | 15.6981 | 16.9784 | 18.2774 | 19.3179 | 20.5055 | 21.6392 | 22.7982 | 24.0079
BTS | Entire | 22 | MVA | 94.3205 | 78.5461 | 84.3191 | 88.7397 | 94.6789 | 101.6457 | 108.5344 | 113.814 | 119.9309 | 125.7432 | 131.6404 | 137.5105
BTS | Entire | 66 | MW | 172.5 | 263.1 | 303.7 | 326.3 | 340.8 | 353 | 371.1 | 392.3 | 412.7 | 428.2 | 446.4 | 465.8
BTS | Entire | 66 | MVAr | 19.5 | 75.9 | 97.7 | 109.8 | 117.5 | 124.1 | 133.7 | 145.1 | 156 | 164.2 | 174 | 184.4
BTS | Entire | 66 | MVA | 173.6 | 273.8 | 319 | 344.3 | 360.5 | 374.2 | 394.4 | 418.3 | 441.2 | 458.6 | 479.1 | 501
CBTS | Entire | 66 | MW | 382.8289 | 394.787 | 414.8837 | 435.874 | 458.7497 | 482.705 | 505.7396 | 528.2027 | 549.7707 | 569.2553 | 590.1623 | 611.2147
CBTS | Entire | 66 | MVAr | 49.9625 | 58.2783 | 63.9478 | 69.4265 | 75.1864 | 80.5928 | 86.2987 | 91.5498 | 96.3679 | 100.0393 | 104.5395 | 108.959
CBTS | Entire | 66 | MVA | 386.0754 | 399.0653 | 419.783 | 441.3686 | 464.8702 | 489.3866 | 513.0497 | 536.0778 | 558.1528 | 577.9787 | 599.3497 | 620.8506
DPTS | Hybrid | 66 | MW | 206.79 | 234.11 | 301.01 | 322.28 | 336.79 | 352.55 | 370.39 | 389.53 | 409.4 | 425.32 | 442 | 459.66
DPTS | Hybrid | 66 | MVAr | 32.3 | 39.19 | 66.3 | 74.91 | 80.79 | 87.18 | 94.4 | 102.16 | 110.21 | 116.66 | 123.42 | 130.57
DPTS | Hybrid | 66 | MVA | 209.3 | 237.37 | 308.23 | 330.87 | 346.34 | 363.17 | 382.23 | 402.7 | 423.97 | 441.03 | 458.91 | 477.85
ERTS | Entire | 66 | MW | 409.7 | 412.8 | 425.3 | 440.6 | 451.2 | 461.6 | 475.4 | 484.6 | 494.3 | 502.4 | 508.1 | 519.8
ERTS | Entire | 66 | MVAr | 88.8 | 73.8 | 78 | 83.1 | 85.9 | 88.3 | 92.5 | 94.8 | 97.3 | 99 | 99.8 | 103.1
ERTS | Entire | 66 | MVA | 419.2 | 419.4 | 432.4 | 448.4 | 459.3 | 469.9 | 484.3 | 493.8 | 503.8 | 512 | 517.8 | 529.9
ERTS12 | Split Bus | 66 | MW | 163.4 | 202.7 | 208.7 | 216.3 | 221.9 | 227.5 | 234.6 | 239.6 | 244.7 | 249.2 | 252.5 | 258.4
ERTS12 | Split Bus | 66 | MVAr | 9.1 | 14.6 | 15.4 | 16.3 | 16.9 | 17.5 | 18.3 | 18.8 | 19.4 | 19.8 | 20 | 20.7
ERTS12 | Split Bus | 66 | MVA | 163.6 | 203.2 | 209.3 | 217 | 222.5 | 228.1 | 235.3 | 240.3 | 245.5 | 250 | 253.2 | 259.2
ERTS34 | Split Bus | 66 | MW | 256.8 | 219.1 | 225.9 | 234.3 | 239.6 | 244.6 | 251.8 | 256.3 | 261 | 264.7 | 267.2 | 273.2
ERTS34 | Split Bus | 66 | MVAr | 74.1 | 62.3 | 66 | 70.6 | 73.2 | 75.5 | 79.3 | 81.4 | 83.7 | 85.3 | 86.2 | 89.2
ERTS34 | Split Bus | 66 | MVA | 267.3 | 227.8 | 235.4 | 244.7 | 250.6 | 256 | 264 | 268.9 | 274.1 | 278.1 | 280.7 | 287.4
FBTS | Entire | 66 | MW | 191.3 | 216.17 | 246.64 | 262.75 | 271.83 | 279.23 | 286.25 | 295.73 | 308.78 | 319.09 | 329.85 | 339.86
FBTS | Entire | 66 | MVAr | 39.8 | 55.28 | 69.7 | 77.32 | 81.61 | 85.12 | 88.44 | 92.93 | 99.1 | 103.98 | 109.07 | 113.81
FBTS | Entire | 66 | MVA | 195.4 | 223.13 | 256.3 | 273.89 | 283.82 | 291.92 | 299.6 | 309.99 | 324.29 | 335.6 | 347.42 | 358.41
GNTS | Entire | 66 | MW | 101.5 | 98.56 | 99.968 | 101.605 | 103.458 | 105.58 | 107.306 | 109.061 | 110.812 | 112.583 | 114.254 | 115.896
GNTS | Entire | 66 | MVAr | 26.7 | 25.9266 | 26.297 | 26.7276 | 27.2151 | 27.7733 | 28.2273 | 28.689 | 29.1496 | 29.6154 | 30.055 | 30.4869
GNTS | Entire | 66 | MVA | 104.953 | 101.913 | 103.3689 | 105.0616 | 106.9776 | 109.1718 | 110.9566 | 112.7713 | 114.5818 | 116.4131 | 118.1409 | 119.8388
GTS | Entire | 66 | MW | 381.56 | 413.11 | 465.59 | 483.03 | 489.96 | 499.35 | 510.41 | 521.16 | 534.03 | 543.66 | 553.85 | 566.35
GTS | Entire | 66 | MVAr | 84.27 | 76.45 | 95.95 | 102.58 | 105.2 | 108.26 | 111.81 | 115.3 | 119.56 | 122.47 | 125.64 | 129.67
GTS | Entire | 66 | MVA | 390.82 | 421.14 | 476.88 | 495.48 | 502.87 | 512.76 | 524.39 | 535.72 | 549.31 | 559.4 | 570.11 | 583.29
HOTS | Entire | 66 | MW | 71.65 | 70.24 | 77.83 | 78.17 | 77.3 | 76.5 | 76.02 | 75.73 | 75.7 | 75.49 | 75.41 | 75.59
HOTS | Entire | 66 | MVAr | 0.55 | -0.91 | -0.07 | -0.03 | -0.13 | -0.21 | -0.27 | -0.3 | -0.3 | -0.33 | -0.34 | -0.32
HOTS | Entire | 66 | MVA | 71.65 | 70.25 | 77.83 | 78.17 | 77.3 | 76.5 | 76.02 | 75.73 | 75.7 | 75.49 | 75.41 | 75.59
HTS | Entire | 66 | MW | 279.2 | 276.2 | 287.1 | 300 | 309.5 | 318.7 | 330.6 | 339.2 | 348.4 | 355 | 362.1 | 371.2
HTS | Entire | 66 | MVAr | 53.4 | 52.3 | 57.2 | 62.9 | 67 | 71.1 | 76.4 | 80.2 | 84.3 | 87.2 | 90.3 | 94.3
HTS | Entire | 66 | MVA | 284.2 | 281.1 | 292.7 | 306.5 | 316.6 | 326.5 | 339.3 | 348.6 | 358.5 | 365.5 | 373.2 | 383
HYTS | Entire | 22 | MW | 1.51 | 2.03 | 2.01 | 1.98 | 1.94 | 1.91 | 1.87 | 1.83 | 1.81 | 1.79 | 1.76 | 1.75
HYTS | Entire | 22 | MVAr | 0.38 | 0.61 | 0.6 | 0.59 | 0.58 | 0.57 | 0.55 | 0.54 | 0.53 | 0.52 | 0.52 | 0.51
HYTS | Entire | 22 | MVA | 1.56 | 2.12 | 2.1 | 2.07 | 2.02 | 1.99 | 1.95 | 1.91 | 1.89 | 1.86 | 1.84 | 1.82
KGTS | Entire | 22 | MW | 7.14 | 9.02 | 10.3 | 10.3 | 10.13 | 9.98 | 9.9 | 9.78 | 9.74 | 9.65 | 9.66 | 9.82
KGTS | Entire | 22 | MVAr | 0 | -0.39 | -0.64 | -0.63 | -0.59 | -0.55 | -0.52 | -0.49 | -0.48 | -0.46 | -0.46 | -0.46
KGTS | Entire | 22 | MVA | 7.14 | 9.0284 | 10.3199 | 10.3192 | 10.1472 | 9.9951 | 9.9136 | 9.7923 | 9.7518 | 9.661 | 9.6709 | 9.8308
KGTS | Entire | 66 | MW | 56.27 | 48.98 | 53.69 | 54.04 | 53.06 | 52.19 | 51.37 | 50.7 | 50.28 | 49.87 | 49.67 | 49.41
KGTS | Entire | 66 | MVAr | -4.99 | -1.93 | -0.64 | -0.55 | -0.82 | -1.06 | -1.28 | -1.46 | -1.58 | -1.69 | -1.74 | -1.82
KGTS | Entire | 66 | MVA | 56.49 | 49.02 | 53.69 | 54.04 | 53.07 | 52.2 | 51.39 | 50.72 | 50.3 | 49.9 | 49.7 | 49.44
KTS | Entire | 66 | MW | 437.1438 | 425.3122 | 444.3675 | 472.3052 | 533.406 | 566.8154 | 599.6841 | 657.0831 | 709.4509 | 768.8561 | 805.5073 | 834.6866
KTS | Entire | 66 | MVAr | 133.4724 | 85.7909 | 91.7119 | 99.2896 | 110.179 | 116.5235 | 123.7737 | 134.4102 | 145.6271 | 155.481 | 160.1747 | 165.5483
KTS | Entire | 66 | MVA | 461.6181 | 434.5167 | 454.3034 | 483.2191 | 545.1133 | 579.0522 | 612.6692 | 670.948 | 724.4589 | 784.5672 | 821.3693 | 851.0076
KTS_East | Split Bus | 66 | MW | 228.9224 | 228.8414 | 234.3848 | 252.0754 | 304.1284 | 328.6608 | 352.3364 | 400.1593 | 441.7122 | 493.1348 | 521.2564 | 540.7102
KTS_East | Split Bus | 66 | MVAr | 103.5673 | 58.1233 | 59.9697 | 65.154 | 73.9627 | 78.1705 | 83.0418 | 91.1198 | 99.4117 | 107.1617 | 109.605 | 112.2489
KTS_East | Split Bus | 66 | MVA | 251.2601 | 236.1073 | 241.9351 | 260.3595 | 312.9929 | 337.8292 | 361.9901 | 410.4026 | 452.7608 | 504.644 | 532.6551 | 552.2385
KTS_West | Split Bus | 66 | MW | 208.2214 | 196.4708 | 209.9827 | 220.2298 | 229.2777 | 238.1545 | 247.3478 | 256.9238 | 267.7387 | 275.7214 | 284.2509 | 293.9764
KTS_West | Split Bus | 66 | MVAr | 29.9051 | 27.6676 | 31.7422 | 34.1356 | 36.2164 | 38.353 | 40.732 | 43.2904 | 46.2154 | 48.3193 | 50.5696 | 53.2994
KTS_West | Split Bus | 66 | MVA | 210.3579 | 198.4094 | 212.3683 | 222.8596 | 232.1204 | 241.223 | 250.6791 | 260.5454 | 271.6982 | 279.9233 | 288.7141 | 298.7691
LY* | Entire | 66 | MW | 25.88 | 27.272 | 27.273 | 27.275 | 27.277 | 27.279 | 27.282 | 27.284 | 27.287 | 27.288 | 27.29 | 27.292
LY* | Entire | 66 | MVAr | 12.2 | 12.8562 | 12.8567 | 12.8576 | 12.8586 | 12.8595 | 12.8609 | 12.8619 | 12.8633 | 12.8637 | 12.8647 | 12.8656
LY* | Entire | 66 | MVA | 28.6114 | 30.1504 | 30.1515 | 30.1537 | 30.1559 | 30.1581 | 30.1614 | 30.1636 | 30.1669 | 30.168 | 30.1703 | 30.1725
MBTS | Entire | 66 | MW | 40.2 | 39.696 | 40.141 | 40.609 | 41.068 | 41.584 | 42.104 | 42.619 | 43.172 | 43.686 | 44.112 | 44.525
MBTS | Entire | 66 | MVAr | 2.4 | 2.3699 | 2.3965 | 2.4244 | 2.4518 | 2.4826 | 2.5137 | 2.5444 | 2.5774 | 2.6081 | 2.6336 | 2.6582
MBTS | Entire | 66 | MVA | 40.2716 | 39.7667 | 40.2125 | 40.6813 | 41.1411 | 41.658 | 42.179 | 42.6949 | 43.2489 | 43.7638 | 44.1905 | 44.6043
MTS | Entire | 22 | MW | 33.3 | 32.1 | 32.6 | 33.2 | 33.8 | 34.3 | 34.6 | 35 | 35.5 | 35.9 | 36.4 | 36.8
MTS | Entire | 22 | MVAr | 3.1 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 2.8 | 2.9 | 3 | 3.1 | 3.2
MTS | Entire | 22 | MVA | 33.4 | 32.1 | 32.7 | 33.3 | 33.9 | 34.4 | 34.7 | 35.2 | 35.6 | 36 | 36.5 | 37
MTS | Entire | 66 | MW | 132.5 | 132.9 | 142.4 | 154 | 162.5 | 170 | 180.4 | 189 | 197.8 | 203.3 | 208 | 214.5
MTS | Entire | 66 | MVAr | 8.6 | 9.4 | 12.5 | 16.1 | 18.9 | 21.3 | 24.6 | 27.3 | 30.1 | 31.9 | 33.4 | 35.5
MTS | Entire | 66 | MVA | 132.8 | 133.3 | 143 | 154.8 | 163.6 | 171.3 | 182 | 191 | 200 | 205.7 | 210.7 | 217.4
MTS6622 | Entire | 66 | MW | 163.1 | 165 | 175 | 187.2 | 196.3 | 204.2 | 215 | 224 | 233.2 | 239.2 | 244.4 | 251.3
MTS6622 | Entire | 66 | MVAr | 10.3 | 11.7 | 14.8 | 18.6 | 21.5 | 23.9 | 27.3 | 30.2 | 33 | 34.9 | 36.5 | 38.6
MTS6622 | Entire | 66 | MVA | 163.5 | 165.4 | 175.6 | 188.1 | 197.5 | 205.6 | 216.7 | 226.1 | 235.5 | 241.7 | 247.1 | 254.3
MWTS | Entire | 66 | MW | 422.32 | 426.302 | 436.604 | 448.134 | 460.606 | 474.221 | 486.106 | 498.264 | 510.289 | 522.539 | 534.601 | 546.332
MWTS | Entire | 66 | MVAr | 47.3 | 47.746 | 48.8998 | 50.1912 | 51.588 | 53.1129 | 54.4441 | 55.8058 | 57.1526 | 58.5246 | 59.8755 | 61.1894
MWTS | Entire | 66 | MVA | 424.9606 | 428.9675 | 439.3339 | 450.936 | 463.4859 | 477.1861 | 489.1454 | 501.3794 | 513.4796 | 525.8062 | 537.9436 | 549.7479
RCTS | Entire | 22 | MW | 26.21 | 28.78 | 31.69 | 32.72 | 32.45 | 32.18 | 31.87 | 31.64 | 31.78 | 31.65 | 31.74 | 31.92
RCTS | Entire | 22 | MVAr | -0.63 | 0.23 | 0.26 | 0.27 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
RCTS | Entire | 22 | MVA | 26.2176 | 28.78 | 31.69 | 32.72 | 32.45 | 32.18 | 31.87 | 31.64 | 31.78 | 31.65 | 31.74 | 31.92
RCTS | Entire | 66 | MW | 86.28 | 98.32 | 107.08 | 107.94 | 107.2 | 106.82 | 106.38 | 106.24 | 106.54 | 106.92 | 107.31 | 108.38
RCTS | Entire | 66 | MVAr | 4.72 | 9.96 | 12.68 | 12.95 | 12.72 | 12.6 | 12.47 | 12.42 | 12.52 | 12.64 | 12.76 | 13.09
RCTS | Entire | 66 | MVA | 86.41 | 98.8232 | 107.8281 | 108.7141 | 107.952 | 107.5606 | 107.1084 | 106.9635 | 107.2731 | 107.6646 | 108.066 | 109.1676
RTS | Entire | 22 | MW | 33.16 | 46.96 | 58.47 | 76.56 | 78.36 | 79.42 | 80.45 | 81.59 | 82.85 | 83.66 | 84.56 | 85.27
RTS | Entire | 22 | MVAr | 5.07 | 9.13 | 12.8 | 18.59 | 19.16 | 19.5 | 19.83 | 20.19 | 20.59 | 20.85 | 21.14 | 21.37
RTS | Entire | 22 | MVA | 33.5453 | 47.84 | 59.85 | 78.78 | 80.67 | 81.78 | 82.86 | 84.05 | 85.37 | 86.22 | 87.16 | 87.91
RTS | Entire | 66 | MW | 348.72 | 430.3424 | 475.6343 | 505.2721 | 525.4714 | 544.2277 | 562.0142 | 582.5391 | 608.5782 | 627.6863 | 648.079 | 668.6855
RTS | Entire | 66 | MVAr | 47.69 | 76.0244 | 96.3984 | 109.5591 | 118.4009 | 126.6551 | 134.4478 | 143.522 | 155.1576 | 163.7081 | 172.8245 | 182.0779
RTS | Entire | 66 | MVA | 351.9659 | 437.0061 | 485.3046 | 517.0137 | 538.6455 | 558.7712 | 577.8721 | 599.9586 | 628.0456 | 648.6836 | 670.727 | 693.0315
RWTS | Entire | 66 | MW | 344.47 | 354.9217 | 368.1734 | 382.4204 | 396.7396 | 412.9653 | 428.577 | 443.0893 | 457.7622 | 471.7276 | 484.7239 | 497.9974
RWTS | Entire | 66 | MVAr | 69.13 | 83.3411 | 87.4321 | 91.6615 | 95.6933 | 100.1394 | 104.6268 | 108.7241 | 112.8381 | 116.6919 | 120.17 | 123.7936
RWTS | Entire | 66 | MVA | 351.3382 | 364.5753 | 378.4125 | 393.2521 | 408.117 | 424.9332 | 441.1633 | 456.2335 | 471.4644 | 485.9464 | 499.3977 | 513.1532
RWTS13 | Split Bus | 66 | MW | 207.18 | 209.2452 | 219.5179 | 229.9477 | 239.4903 | 249.8077 | 260.8453 | 270.7051 | 280.6263 | 289.7051 | 297.4647 | 305.7057
RWTS13 | Split Bus | 66 | MVAr | 27.84 | 45.9167 | 49.2423 | 52.4912 | 55.2958 | 58.2241 | 61.5364 | 64.4385 | 67.3317 | 69.9302 | 72.0629 | 74.3937
RWTS13 | Split Bus | 66 | MVA | 209.0421 | 214.2239 | 224.9731 | 235.8628 | 245.791 | 256.5033 | 268.0056 | 278.2689 | 288.5909 | 298.0256 | 306.0691 | 314.6274
RWTS22 | Entire | 22 | MW | 65.57 | 64.5946 | 66.7089 | 69.2219 | 71.975 | 74.9466 | 77.7244 | 80.5266 | 83.3518 | 85.728 | 88.2006 | 90.5589
RWTS22 | Entire | 22 | MVAr | 2.63 | 2.6422 | 2.7206 | 2.8173 | 2.9283 | 3.0531 | 3.1596 | 3.2678 | 3.3776 | 3.4801 | 3.5862 | 3.6887
RWTS22 | Entire | 22 | MVA | 65.6227 | 64.6486 | 66.7643 | 69.2792 | 72.0346 | 75.0088 | 77.7886 | 80.5929 | 83.4203 | 85.7986 | 88.2735 | 90.634
RWTS24 | Split Bus | 66 | MW | 146.36 | 145.6765 | 148.6555 | 152.4727 | 157.2492 | 163.1576 | 167.7317 | 172.3842 | 177.1359 | 182.0225 | 187.2593 | 192.2917
RWTS24 | Split Bus | 66 | MVAr | 37.6 | 37.4244 | 38.1897 | 39.1704 | 40.3974 | 41.9153 | 43.0904 | 44.2856 | 45.5063 | 46.7617 | 48.1071 | 49.3999
RWTS24 | Split Bus | 66 | MVA | 151.1126 | 150.4069 | 153.4826 | 157.4238 | 162.3554 | 168.4556 | 173.1783 | 177.9818 | 182.8878 | 187.9331 | 193.3399 | 198.5358
SHTS | Entire | 66 | MW | 202.57 | 199.3 | 222.6 | 228.2 | 228.8 | 229.5 | 230.3 | 231.8 | 233.6 | 234.2 | 236.1 | 238.8
SHTS | Entire | 66 | MVAr | 39.4 | 27.8 | 39.4 | 42.2 | 42.5 | 42.9 | 43.2 | 44 | 44.9 | 45.2 | 46.1 | 47.5
SHTS | Entire | 66 | MVA | 206.37 | 201.3 | 226.1 | 232 | 232.7 | 233.5 | 234.3 | 235.9 | 237.9 | 238.5 | 240.5 | 243.5
SMTS | Entire | 66 | MW | 299.8706 | 312.1541 | 329.7312 | 351.4466 | 375.6121 | 400.5231 | 423.1361 | 445.1384 | 467.5279 | 489.0645 | 512.3696 | 535.9762
SMTS | Entire | 66 | MVAr | 30.2347 | 39.2694 | 41.777 | 45.0848 | 48.7742 | 52.2683 | 55.4232 | 58.3386 | 61.3775 | 64.1545 | 67.1328 | 70.1586
SMTS | Entire | 66 | MVA | 301.391 | 314.6145 | 332.3672 | 354.3266 | 378.7655 | 403.9193 | 426.7504 | 448.9449 | 471.5395 | 493.2544 | 516.7489 | 540.5485
SVTS | Entire | 66 | MW | 303 | 315.9 | 334.1 | 348.9 | 359.3 | 370.9 | 386.6 | 400.2 | 413.8 | 423 | 430.7 | 443.2
SVTS | Entire | 66 | MVAr | 48.9 | 32.7 | 36.4 | 39.3 | 41.3 | 43.5 | 46.5 | 49.1 | 51.6 | 53.3 | 54.7 | 57.1
SVTS | Entire | 66 | MVA | 306.9 | 317.6 | 336.1 | 351.1 | 361.7 | 373.4 | 389.4 | 403.2 | 417.1 | 426.3 | 434.1 | 446.9
SVTS12 | Split Bus | 66 | MW | 173.9 | 165.2 | 174.5 | 181.8 | 186.7 | 192.1 | 199.7 | 205.9 | 212 | 216 | 219.3 | 225.1
SVTS12 | Split Bus | 66 | MVAr | 29.2 | 18.3 | 20.4 | 22 | 23.1 | 24.3 | 26 | 27.4 | 28.7 | 29.6 | 30.3 | 31.6
SVTS12 | Split Bus | 66 | MVA | 176.4 | 166.2 | 175.7 | 183.2 | 188.1 | 193.6 | 201.4 | 207.7 | 214 | 218.1 | 221.4 | 227.3
SVTS34 | Split Bus | 66 | MW | 129 | 153.7 | 162.8 | 170.4 | 176.2 | 182.6 | 191 | 198.6 | 206.4 | 211.8 | 216.4 | 223.3
SVTS34 | Split Bus | 66 | MVAr | 19.7 | 14.4 | 15.9 | 17.2 | 18.1 | 19.1 | 20.5 | 21.7 | 22.9 | 23.7 | 24.3 | 25.4
SVTS34 | Split Bus | 66 | MVA | 130.5 | 154.3 | 163.6 | 171.3 | 177.1 | 183.6 | 192.1 | 199.8 | 207.7 | 213.1 | 217.8 | 224.8
TBTS | Entire | 66 | MW | 218.8 | 215.5 | 223.7 | 232 | 239.8 | 245.9 | 254.2 | 262.2 | 269.3 | 273.2 | 276.6 | 280.8
TBTS | Entire | 66 | MVAr | 27 | 28.1 | 31.1 | 34.3 | 37.2 | 39.5 | 42.6 | 45.6 | 48.3 | 49.7 | 51 | 52.6
TBTS | Entire | 66 | MVA | 220.4596 | 217.3243 | 225.8515 | 234.5218 | 242.6683 | 249.0523 | 257.7448 | 266.1357 | 273.5971 | 277.6839 | 281.2624 | 285.6841
TGTS | Entire | 66 | MW | 161.05 | 160.5 | 169.19 | 170.09 | 169.22 | 168.6 | 168.41 | 168.52 | 169.28 | 169.48 | 169.79 | 171.46
TGTS | Entire | 66 | MVAr | 1.2 | 10.34 | 11.85 | 12 | 11.85 | 11.74 | 11.71 | 11.73 | 11.86 | 11.9 | 11.95 | 12.24
TGTS | Entire | 66 | MVA | 161.0545 | 160.8327 | 169.6045 | 170.5128 | 169.6344 | 169.0082 | 168.8166 | 168.9277 | 169.695 | 169.8973 | 170.21 | 171.8963
TSTS | Entire | 66 | MW | 246.7 | 228.3 | 241.6 | 256.8 | 270.5 | 283.5 | 298.2 | 313.1 | 327.9 | 338.8 | 351.5 | 363.1
TSTS | Entire | 66 | MVAr | 28.4 | 35.4 | 40.9 | 47.1 | 52.5 | 57.6 | 63.5 | 69.7 | 75.8 | 80.2 | 85.3 | 90.1
TSTS | Entire | 66 | MVA | 248.3 | 231 | 245 | 261.1 | 275.5 | 289.2 | 304.9 | 320.7 | 336.5 | 348.2 | 361.7 | 374.1
TTS | Entire | 66 | MW | 399.1533 | 395.7202 | 414.3984 | 441.0147 | 469.9176 | 485.7375 | 498.757 | 511.85 | 525.5331 | 542.1163 | 555.1439 | 568.22
TTS | Entire | 66 | MVAr | 101.164 | 108.9986 | 114.235 | 121.9178 | 130.4301 | 134.8212 | 138.4304 | 142.0689 | 145.8717 | 150.6482 | 154.2532 | 157.8704
TTS | Entire | 66 | MVA | 412.1914 | 410.4573 | 429.8554 | 457.5565 | 487.6828 | 504.1008 | 517.6113 | 531.2005 | 545.4022 | 562.6588 | 576.176 | 589.7431
TTS12 | Split Bus | 66 | MW | 186.2316 | 181.8004 | 188.9851 | 201.4704 | 217.6073 | 224.219 | 229.7358 | 235.1447 | 240.7941 | 250.2184 | 255.8283 | 261.4737
TTS12 | Split Bus | 66 | MVAr | 37.9713 | 44.6 | 46.3763 | 49.8075 | 54.4815 | 56.1013 | 57.4525 | 58.7784 | 60.1633 | 62.7869 | 64.1594 | 65.5404
TTS12 | Split Bus | 66 | MVA | 190.0632 | 187.1911 | 194.5923 | 207.5358 | 224.3239 | 231.131 | 236.8108 | 242.3797 | 248.1964 | 257.9756 | 263.751 | 269.5627
TTS34 | Split Bus | 66 | MW | 212.9217 | 218.8222 | 230.5798 | 245.0889 | 258.257 | 267.6616 | 275.3248 | 283.1733 | 291.3789 | 298.7486 | 306.3237 | 313.9118
TTS34 | Split Bus | 66 | MVAr | 63.1927 | 65.7899 | 69.3249 | 73.6871 | 77.6462 | 80.4737 | 82.7777 | 85.1374 | 87.6044 | 89.8202 | 92.0977 | 94.3791
TTS34 | Split Bus | 66 | MVA | 222.1012 | 228.4983 | 240.7758 | 255.9265 | 269.6768 | 279.4973 | 287.4994 | 295.6949 | 304.2634 | 311.9589 | 319.869 | 327.7927
WETS | Entire | 66 | MW | 29.2 | 39.3 | 41.2 | 40.7 | 40.1 | 39.5 | 38.8 | 38.4 | 38 | 37.7 | 37.4 | 37.1
WETS | Entire | 66 | MVAr | 3.5 | -0.6 | 0.3 | 0.1 | -0.2 | -0.5 | -0.8 | -1 | -1.2 | -1.3 | -1.5 | -1.6
WETS | Entire | 66 | MVA | 29.4 | 39.3 | 41.2 | 40.7 | 40.1 | 39.5 | 38.9 | 38.4 | 38 | 37.8 | 37.4 | 37.2
WMTS | Entire | 22 | MW | 26.91 | 38.53 | 39.21 | 39.92 | 40.42 | 40.6 | 40.46 | 40.38 | 40.4 | 40.62 | 40.99 | 41.21
WMTS | Entire | 22 | MVAr | 4.57 | 7.91 | 7.97 | 8.03 | 8.08 | 8.09 | 8.08 | 8.08 | 8.08 | 8.1 | 8.13 | 8.15
WMTS | Entire | 22 | MVA | 27.2953 | 39.33 | 40.01 | 40.72 | 41.22 | 41.4 | 41.26 | 41.18 | 41.2 | 41.42 | 41.79 | 42.01
WMTS | Entire | 66 | MW | 211.54 | 242.2844 | 269.2228 | 287.4931 | 300.8802 | 321.5571 | 340.5046 | 359.057 | 378.2432 | 396.5092 | 413.0171 | 436.4783
WMTS | Entire | 66 | MVAr | 24.75 | 49.864 | 62.5185 | 70.9725 | 76.6648 | 86.5111 | 95.5889 | 104.942 | 114.5654 | 123.9716 | 132.3561 | 144.6104
WMTS | Entire | 66 | MVA | 212.98 | 247.3624 | 276.3865 | 296.1239 | 310.4937 | 332.9912 | 353.6674 | 374.0785 | 395.2128 | 415.4377 | 433.7065 | 459.8102
WOTS | Entire | 66 | MW | 42.76 | 43.603 | 44.423 | 45.371 | 46.448 | 47.61 | 48.491 | 49.401 | 50.38 | 51.376 | 52.341 | 53.3
WOTS | Entire | 66 | MVAr | 7.44 | 6.9925 | 7.1509 | 7.3307 | 7.5311 | 7.7565 | 7.94 | 8.1263 | 8.3201 | 8.518 | 8.7099 | 8.8998
WOTS | Entire | 66 | MVA | 43.4024 | 43.9603 | 44.7885 | 45.7458 | 46.8332 | 48.0068 | 48.8974 | 49.817 | 50.8061 | 51.8124 | 52.7873 | 53.7562
WOTS22 | Entire | 22 | MW | 30.08 | 32.828 | 33.766 | 34.811 | 35.952 | 37.292 | 38.458 | 39.624 | 40.8 | 42.005 | 43.174 | 44.327
WOTS22 | Entire | 22 | MVAr | -0.4 | 0.43654 | 0.44902 | 0.46291 | 0.47809 | 0.4959 | 0.51141 | 0.52691 | 0.54255 | 0.55858 | 0.57412 | 0.58945
WOTS22 | Entire | 22 | MVA | 30.0827 | 32.8309 | 33.769 | 34.8141 | 35.9552 | 37.2953 | 38.4614 | 39.6275 | 40.8036 | 42.0087 | 43.1778 | 44.3309
Note 1: Note that this is the observed actual and have not been weather normalised.

## TsAnnual10_minimum
2023 Terminal Station Minimum Demand Forecast - MW, MVAr & MVA Forecasts aggregated by Terminal Station
Forecasts at time of Station minimum - station diversity factors are applied.
Annual, 10% POE
LOCATIONID | LocationType | VOLTAGE | UNIT | 2023 (Actual Note 1) | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033
ATS_BLTS | Hybrid | 66 | MW | 86.1 | 102.3 | 125 | 138.5 | 146.4 | 156.9 | 161.8 | 157.9 | 154.9 | 151.6 | 147.3
ATS_BLTS | Hybrid | 66 | MVAr | 10.6 | 13.5 | 23.4 | 31.6 | 36.6 | 44.2 | 48.2 | 46.6 | 45 | 43.6 | 42
ATS_BLTS | Hybrid | 66 | MVA | 86.7 | 103.4 | 127.7 | 142.7 | 151.8 | 164.1 | 169.9 | 165.7 | 162.4 | 158.7 | 154
ATS_WEST | Hybrid | 66 | MW | -36.4 | -24.7 | -28.5 | -38 | -46.8 | -54.8 | -60.7 | -66 | -65.7 | -65.4 | -63.4
ATS_WEST | Hybrid | 66 | MVAr | -5.8 | -9.9 | -9.6 | -8.7 | -8 | -7.2 | -6.7 | -6.2 | -6.3 | -6.3 | -6.5
ATS_WEST | Hybrid | 66 | MVA | -36.8 | -26.6 | -30.1 | -39 | -47.4 | -55.2 | -61.1 | -66.3 | -66 | -65.7 | -63.7
BATS | Entire | 66 | MW | -108.8 | -166.9 | -164.4 | -171.9 | -180.4 | -190 | -197.8 | -209.3 | -214.9 | -221.2 | -226.1
BATS | Entire | 66 | MVAr | 19.2 | 23.8 | 23.1 | 25.1 | 27.3 | 29.8 | 31.8 | 34.7 | 36.2 | 37.8 | 39.1
BATS | Entire | 66 | MVA | -110.5 | -168.6 | -166.1 | -173.8 | -182.4 | -192.4 | -200.3 | -212.2 | -218 | -224.4 | -229.5
BETS | Entire | 22 | MW | -6.3 | -9.7 | -12.6 | -17.1 | -21.8 | -26.8 | -32 | -37.2 | -41.2 | -45.3 | -49.4
BETS | Entire | 22 | MVAr | 0 | 3.5 | 3.6 | 3.7 | 3.8 | 4 | 4.1 | 4.3 | 4.4 | 4.5 | 4.6
BETS | Entire | 22 | MVA | -6.3 | -10.3 | -13.1 | -17.5 | -22.2 | -27 | -32.3 | -37.4 | -41.4 | -45.5 | -49.6
BETS | Entire | 66 | MW | -11.9 | -12.1 | -13.3 | -20.8 | -29 | -36.9 | -45.8 | -54.8 | -59.3 | -64.9 | -69.6
BETS | Entire | 66 | MVAr | 14.7 | 0.4 | 0.3 | -0.1 | -0.6 | -1.1 | -1.7 | -2.2 | -2.5 | -2.8 | -3.1
BETS | Entire | 66 | MVA | -18.9 | -12.1 | -13.3 | -20.8 | -29 | -36.9 | -45.8 | -54.9 | -59.3 | -65 | -69.7
BLTS | Entire | 22 | MW | 1 | -3.1 | 2.4 | 2.9 | 2.8 | 2.5 | 2.2 | 2 | 2 | 2.1 | 2
BLTS | Entire | 22 | MVAr | 0.9 | -1.1 | -1.7 | -1.5 | -1.6 | -1.7 | -1.8 | -1.9 | -1.9 | -1.8 | -1.9
BLTS | Entire | 22 | MVA | 1.3 | -3.3 | 3 | 3.2 | 3.2 | 3 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
BLTS-SCI | Hybrid | 66 | MW
BLTS-SCI | Hybrid | 66 | MVAr
BLTS-SCI | Hybrid | 66 | MVA
BTS | Entire | 22 | MW | 15.52 | 13.9327 | 13.0765 | 12.0333 | 10.3247 | 8.2669 | 6.201 | 4.6302 | 2.9235 | 0.66331 | -2.5175
BTS | Entire | 22 | MVAr | -2.7723 | -1.8369 | -1.9138 | -2.0501 | -2.2655 | -2.4808 | -2.7259 | -2.8821 | -3.1173 | -3.0068 | -2.5309
BTS | Entire | 22 | MVA | 15.7657 | 14.0532 | 13.2159 | 12.2067 | 10.5703 | 8.6311 | 6.7737 | 5.4539 | 4.2737 | 3.0791 | 3.5698
BTS | Entire | 66 | MW | 57.3 | 85.8 | 99.9 | 102.8 | 104.4 | 107 | 109.6 | 115.5 | 120.3 | 121.3 | 106
BTS | Entire | 66 | MVAr | -3.9 | -1.2 | 0.6 | 1 | 1.2 | 1.5 | 1.8 | 2.6 | 3.2 | 3.3 | 1.4
BTS | Entire | 66 | MVA | 57.4 | 85.8 | 99.9 | 102.8 | 104.4 | 107 | 109.6 | 115.5 | 120.3 | 121.3 | 106
CBTS | Entire | 66 | MW | -4.5938 | -71.72 | -94.26 | -113.316 | -128.148 | -141.828 | -153.31 | -161.375 | -165.523 | -167.907 | -172.843
CBTS | Entire | 66 | MVAr | -38.6794 | -40.2528 | -48.5919 | -55.4167 | -60.7523 | -65.2402 | -68.8405 | -71.6927 | -73.5158 | -74.7495 | -76.281
CBTS | Entire | 66 | MVA | -38.9513 | -82.2438 | -106.0477 | -126.1409 | -141.8194 | -156.1136 | -168.0564 | -176.5835 | -181.1144 | -183.794 | -188.9272
DPTS | Hybrid | 66 | MW | -24.48 | 8.85 | 40.4 | 27.04 | 15.58 | 3.8 | -2.55 | -12.04 | -14.27 | -17.68 | -19.67
DPTS | Hybrid | 66 | MVAr | -11.8 | -12.7 | -11 | -11.72 | -12.34 | -12.97 | -13.04 | -12.53 | -12.41 | -12.22 | -12.12
DPTS | Hybrid | 66 | MVA | -27.17 | 15.48 | 41.87 | 29.47 | 19.87 | 13.52 | 13.29 | 17.38 | 18.91 | 21.49 | 23.1
ERTS | Entire | 66 | MW | 35.3 | -56.2 | -58.8 | -65.9 | -74.6 | -84.2 | -107.4 | -114.3 | -105.9 | -109.8 | -114.7
ERTS | Entire | 66 | MVAr | -12.8 | -29.4 | -31.4 | -31.4 | -30.4 | -28.7 | -22.8 | -21.7 | -24.6 | -23.7 | -22.6
ERTS | Entire | 66 | MVA | 37.5 | -63.5 | -66.7 | -73 | -80.6 | -89 | -109.8 | -116.3 | -108.7 | -112.4 | -116.9
ERTS12 | Split Bus | 66 | MW | 5.5 | -21.7 | -22.3 | -25.1 | -28.7 | -32.8 | -43.1 | -46 | -42.1 | -43.8 | -45.9
ERTS12 | Split Bus | 66 | MVAr | -10.4 | -9.1 | -10.1 | -10.2 | -9.9 | -9.2 | -7 | -6.5 | -7.5 | -7 | -6.3
ERTS12 | Split Bus | 66 | MVA | 11.8 | -23.5 | -24.5 | -27.1 | -30.4 | -34.1 | -43.7 | -46.4 | -42.8 | -44.4 | -46.3
ERTS34 | Split Bus | 66 | MW | 19.8 | -32.7 | -32.6 | -35.9 | -40.8 | -46.6 | -61.4 | -65.5 | -60 | -62.8 | -66.2
ERTS34 | Split Bus | 66 | MVAr | -6.9 | -19.8 | -21.5 | -21.5 | -20.5 | -18.9 | -13.9 | -12.8 | -14.9 | -13.8 | -12.5
ERTS34 | Split Bus | 66 | MVA | 21 | -38.2 | -39 | -41.8 | -45.6 | -50.3 | -62.9 | -66.8 | -61.9 | -64.3 | -67.4
FBTS | Entire | 66 | MW | 87.3 | 99.1 | 117.2 | 120 | 118.5 | 116.6 | 115.2 | 117.9 | 122.6 | 127.3 | 132.3
FBTS | Entire | 66 | MVAr | -1.1 | 2.2 | 10.1 | 11.3 | 10.7 | 9.9 | 9.2 | 10.4 | 12.5 | 14.5 | 16.7
FBTS | Entire | 66 | MVA | 87.3 | 99.2 | 117.6 | 120.5 | 118.9 | 117 | 115.6 | 118.4 | 123.2 | 128.1 | 133.4
GNTS | Entire | 66 | MW | -189.5 | -198.639 | -204.384 | -208.788 | -212.042 | -215.255 | -218.427 | -221.4 | -223.855 | -226.163 | -228.342
GNTS | Entire | 66 | MVAr | -4.7 | 4.9045 | 5.0463 | 5.1551 | 5.2354 | 5.3147 | 5.3931 | 5.4665 | 5.5271 | 5.5841 | 5.6379
GNTS | Entire | 66 | MVA | -189.5583 | -198.6995 | -204.4463 | -208.8516 | -212.1066 | -215.3206 | -218.4936 | -221.4675 | -223.9232 | -226.2319 | -228.4116
GTS | Entire | 66 | MW | 49.11 | 65.26 | 79.18 | 61.11 | 39.99 | 17.46 | -4.8 | -30.12 | -47.36 | -63.95 | -83.47
GTS | Entire | 66 | MVAr | -3.92 | 2.96 | 4.8 | 2.98 | 0.4 | -3.02 | -6.91 | -6.03 | -3.49 | -1.26 | 1.2
GTS | Entire | 66 | MVA | 50.15 | 65.3271 | 79.3254 | 61.1826 | 39.992 | 17.7193 | 8.4136 | 30.7177 | 47.4884 | 63.9624 | 83.4786
HOTS | Entire | 66 | MW | -22.65 | -26.42 | -20.75 | -22.82 | -25.17 | -27.55 | -30.09 | -34.13 | -36.11 | -38.13 | -41.06
HOTS | Entire | 66 | MVAr | 35.61 | -1.67 | 0.42 | -0.35 | -1.21 | -2.09 | -3.03 | -4.52 | -4.73 | -4.5 | -4.17
HOTS | Entire | 66 | MVA | -42.21 | 26.42 | 20.75 | 22.82 | 25.17 | 27.55 | 30.09 | 34.13 | 36.11 | 38.13 | 41.06
HTS | Entire | 66 | MW | 46.4 | 23.2 | 17.6 | 8.5 | 0.2 | -16.9 | -29.1 | -43.5 | -50.3 | -53.2 | -75.3
HTS | Entire | 66 | MVAr | -2.1 | -21.4 | -22.6 | -24.7 | -26.6 | -22.8 | -20 | -16.8 | -15.2 | -14.6 | -9.5
HTS | Entire | 66 | MVA | 46.4 | 31.5 | 28.7 | 26.1 | 26.6 | -28.4 | -35.3 | -46.6 | -52.5 | -55.2 | -75.9
HYTS | Entire | 22 | MW | 0.02 | -0.2 | -0.21 | -0.24 | -0.26 | -0.29 | -0.31 | -0.37 | -0.41 | -0.46 | -0.54
HYTS | Entire | 22 | MVAr | -0.04 | -0.03 | -0.02 | -0.01 | 0 | 0.01 | 0.01 | 0.04 | 0.05 | 0.06 | 0.09
HYTS | Entire | 22 | MVA | 0.05 | 0.2 | 0.21 | 0.24 | 0.26 | 0.29 | 0.31 | 0.37 | 0.41 | 0.46 | 0.55
KGTS | Entire | 22 | MW | 0.03 | -3 | -23.51 | -24.75 | -25.69 | -26.56 | -27.67 | -28.8 | -29.38 | -30.14 | -31.02
KGTS | Entire | 22 | MVAr | 0 | 0.18 | -3.1 | -3.33 | -3.49 | -3.66 | -3.86 | -4.08 | -4.18 | -4.34 | -4.48
KGTS | Entire | 22 | MVA | 0.03 | 3.355 | 32.5458 | 34.4523 | 35.9012 | 37.2515 | 38.9775 | 40.7454 | 41.6528 | 42.8509 | 44.232
KGTS | Entire | 66 | MW | -81.5 | -68.99 | -65.17 | -65.23 | -65.48 | -65.64 | -65.89 | -66.83 | -66.63 | -66.81 | -66.98
KGTS | Entire | 66 | MVAr | 21.09 | 3.55 | 2.5 | 2.52 | 2.59 | 2.63 | 2.7 | 2.96 | 2.9 | 2.95 | 3
KGTS | Entire | 66 | MVA | -84.18 | -69.08 | -65.22 | -65.28 | -65.53 | -65.69 | -65.95 | -66.9 | -66.69 | -66.88 | -67.05
KTS | Entire | 66 | MW | 52.14 | 34.0126 | 17.9289 | 1.4519 | -18.2065 | -38.0054 | -58.8136 | -73.8895 | -88.5299 | -102.6519 | -120.6737
KTS | Entire | 66 | MVAr | -16.3886 | -18.4321 | -19.4608 | -20.3369 | -21.2182 | -22.3124 | -23.5406 | -24.5458 | -25.3689 | -24.6916 | -23.4475
KTS | Entire | 66 | MVA | 45.2121 | 29.9337 | 15.057 | -0.56828 | -19.5176 | -38.6614 | -58.6045 | -72.7223 | -85.9419 | -98.8638 | -113.4688
KTS_East | Split Bus | 66 | MW | 67.17 | 59.0434 | 54.2059 | 49.3711 | 42.618 | 34.7289 | 26.7429 | 20.0868 | 14.3693 | 8.353 | 1.2992
KTS_East | Split Bus | 66 | MVAr | -0.37935 | -3.3827 | -4.2964 | -5.3002 | -6.3744 | -7.5883 | -8.9222 | -9.8907 | -10.8109 | -10.0883 | -9.2381
KTS_East | Split Bus | 66 | MVA | 67.1711 | 59.1402 | 54.3759 | 49.6548 | 43.0921 | 35.5483 | 28.192 | 22.3899 | 17.982 | 13.0976 | 9.329
KTS_West | Split Bus | 66 | MW | -15.03 | -25.0308 | -36.277 | -47.9192 | -60.8246 | -72.7343 | -85.5566 | -93.9763 | -102.8992 | -111.0049 | -121.9729
KTS_West | Split Bus | 66 | MVAr | -16.0093 | -15.0494 | -15.1644 | -15.0367 | -14.8439 | -14.7241 | -14.6184 | -14.655 | -14.5579 | -14.6034 | -14.2095
KTS_West | Split Bus | 66 | MVA | -21.959 | -29.2066 | -39.319 | -50.223 | -62.6097 | -74.2097 | -86.7965 | -95.1121 | -103.924 | -111.9614 | -122.7978
LY* | Entire | 66 | MW | 2.16 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9
LY* | Entire | 66 | MVAr | -5.08 | -4.4685 | -4.4685 | -4.4685 | -4.4685 | -4.4685 | -4.4685 | -4.4685 | -4.4685 | -4.4685 | -4.4685
LY* | Entire | 66 | MVA | 5.5201 | 4.8557 | 4.8557 | 4.8557 | 4.8557 | 4.8557 | 4.8557 | 4.8557 | 4.8557 | 4.8557 | 4.8557
MBTS | Entire | 66 | MW | -8.7 | -12.02 | -13.344 | -14.507 | -15.417 | -16.217 | -16.824 | -17.409 | -17.855 | -18.218 | -18.6
MBTS | Entire | 66 | MVAr | 2.8 | 3.9328 | 4.366 | 4.7465 | 5.0443 | 5.306 | 5.5046 | 5.696 | 5.842 | 5.9607 | 6.0857
MBTS | Entire | 66 | MVA | -9.1395 | -12.647 | -14.0401 | -15.2638 | -16.2212 | -17.063 | -17.7016 | -18.3172 | -18.7864 | -19.1684 | -19.5703
MTS | Entire | 22 | MW | 3 | 3.4 | 3.4 | 3.5 | 3.6 | 3.6 | 3.6 | 3.7 | 3.7 | 3.8 | 3.8
MTS | Entire | 22 | MVAr | -0.5 | bar: 2024 to 2033
MTS | Entire | 22 | MVA | 3.1 | 4.6 | 4.6 | 4.6 | 4.7 | 4.7 | 4.7 | 4.7 | 4.8 | 4.8 | 4.8
MTS | Entire | 66 | MW | 35.1 | 34.8 | 30.9 | 24.4 | 18.8 | 11.4 | 5 | -1.4 | -6.4 | -10.4 | -17.3
MTS | Entire | 66 | MVAr | -10.6 | -13.6 | -14.3 | -15.5 | -16.5 | -17.9 | -19.1 | -19.8 | -18.8 | -18.1 | -16.8
MTS | Entire | 66 | MVA | 36.6 | 37.3 | 34 | 28.9 | 25 | 21.2 | 19.7 | -19.8 | -19.9 | -20.9 | -24.1
MTS6622 | Entire | 66 | MW | 39.4 | 38.1 | 34.3 | 27.9 | 22.3 | 15 | 8.6 | 2.3 | -2.7 | -6.7 | -13.5
MTS6622 | Entire | 66 | MVAr | -11.4 | -16.6 | -17.3 | -18.5 | -19.5 | -20.9 | -22.1 | -22.8 | -21.8 | -21 | -19.8
MTS6622 | Entire | 66 | MVA | 41 | 41.6 | 38.4 | 33.5 | 29.7 | 25.7 | 23.7 | 22.9 | -22 | -22.1 | -23.9
MWTS | Entire | 66 | MW | -72.5 | -3.268 | -14.319 | -22.623 | -29.323 | -34.965 | -39.735 | -42.222 | -44.3 | -46.05 | -47.55
MWTS | Entire | 66 | MVAr | 51 | 0.3815 | 1.6716 | 2.641 | 3.4231 | 4.0817 | 4.6386 | 4.9289 | 5.1715 | 5.3758 | 5.5509
MWTS | Entire | 66 | MVA | -88.6411 | -3.2902 | -14.4162 | -22.7766 | -29.5221 | -35.2024 | -40.0048 | -42.5087 | -44.6008 | -46.3627 | -47.8729
RCTS | Entire | 22 | MW | 0.12 | 1.7 | 3.82 | 2.97 | 1.86 | 0.69 | -0.25 | -1.48 | -2.48 | -3.45 | -4.26
RCTS | Entire | 22 | MVAr | -1.6 | 0.01 | 0.03 | 0.02 | 0.01 | 0 | 0 | 0.01 | 0.01 | 0.02 | 0.03
RCTS | Entire | 22 | MVA | 1.6045 | 1.7 | 3.82 | 2.97 | 1.86 | 0.69 | 0.25 | 1.48 | 2.48 | 3.45 | 4.26
RCTS | Entire | 66 | MW | -156.31 | -148.28 | -147.07 | -150.48 | -154.36 | -156.93 | -159.91 | -163.03 | -163.21 | -163.93 | -166.61
RCTS | Entire | 66 | MVAr | 41.45 | 25.48 | 25.11 | 26.17 | 27.37 | 28.17 | 29.1 | 30.07 | 30.12 | 30.35 | 31.18
RCTS | Entire | 66 | MVA | -161.7125 | 150.4533 | 149.1982 | 152.7387 | 156.7677 | 159.4383 | 162.5362 | 165.7799 | 165.966 | 166.7158 | 169.5025
RTS | Entire | 22 | MW | 2.24 | 19.35 | 18.28 | 43.34 | 42.83 | 42.49 | 42.23 | 42.02 | 41.84 | 41.71 | 41.59
RTS | Entire | 22 | MVAr | 0.23 | 0.53 | 0.24 | 7.99 | 7.83 | 7.72 | 7.63 | 7.56 | 7.51 | 7.46 | 7.43
RTS | Entire | 22 | MVA | 2.2518 | 19.36 | 18.28 | 44.07 | 43.54 | 43.19 | 42.91 | 42.69 | 42.51 | 42.37 | 42.25
RTS | Entire | 66 | MW | 117.01 | 105.04 | 129.73 | 136.85 | 138.92 | 139.24 | 139.55 | 141.21 | 146.34 | 149.19 | 147.53
RTS | Entire | 66 | MVAr | -44.84 | -41.42 | -32.73 | -30.33 | -29.7 | -29.6 | -29.4 | -28.7 | -26.9 | -25.8 | -26.3
RTS | Entire | 66 | MVA | 125.31 | 112.91 | 133.7951 | 140.1707 | 142.1 | 142.4 | 142.6 | 144.1 | 148.8 | 151.4 | 149.9
RWTS | Entire | 66 | MW | 39.81 | 2.6063 | -0.29117 | -2.3768 | -6.3013 | -13.6122 | -20.925 | -27.3427 | -31.9997 | -33.7455 | -41.699
RWTS | Entire | 66 | MVAr | -1.06 | 2.2633 | 3.4451 | 4.3273 | 4.4819 | 4.7734 | 5.9195 | 6.7872 | 7.3905 | 7.5728 | 8.4894
RWTS | Entire | 66 | MVA | 39.8241 | 3.4518 | -3.4574 | -4.9371 | -7.7326 | -14.4249 | -21.7462 | -28.1725 | -32.842 | -34.5848 | -42.5544
RWTS13 | Split Bus | 66 | MW | 23.24 | 2.2491 | 2.067 | 1.6962 | -1.5589 | -8.1574 | -15.0341 | -21.952 | -27.4034 | -30.0027 | -38.7565
RWTS13 | Split Bus | 66 | MVAr | -5.96 | -10.4646 | -9.7248 | -9.3156 | -11.2223 | -11.8249 | -7.0153 | -2.0967 | 1.7878 | 3.683 | 9.9376
RWTS13 | Split Bus | 66 | MVA | 23.9921 | 10.7036 | 9.942 | 9.4688 | -11.3301 | -14.3657 | -16.5903 | -22.0519 | -27.4617 | -30.2279 | -40.0103
RWTS22 | Entire | 22 | MW | 13.89 | 4.8265 | 2.4255 | 0.29447 | -1.5768 | -4.261 | -6.6839 | -8.4502 | -10.385 | -11.3056 | -13.5131
RWTS22 | Entire | 22 | MVAr | -1.36 | 0.6257 | 1.9639 | 3.336 | 4.713 | 6.5537 | 8.2845 | 9.7353 | 11.3526 | 12.3861 | 14.2149
RWTS22 | Entire | 22 | MVA | 13.9564 | 4.8669 | 3.1209 | 3.349 | -4.9698 | -7.8171 | -10.6446 | -12.8912 | -15.3861 | -16.77 | -19.613
RWTS24 | Split Bus | 66 | MW | 11.6 | 0.35718 | -2.3582 | -4.073 | -4.7424 | -5.4547 | -5.8909 | -5.3907 | -4.5963 | -3.7429 | -2.9425
RWTS24 | Split Bus | 66 | MVAr | 3.14 | 0.011286 | 0.074514 | 0.1287 | 0.14985 | 0.17236 | 0.18614 | 0.17034 | 0.14524 | 0.11827 | 0.092977
RWTS24 | Split Bus | 66 | MVA | 12.0175 | 0.35736 | -2.3594 | -4.0751 | -4.7447 | -5.4574 | -5.8939 | -5.3934 | -4.5986 | -3.7447 | -2.9439
SHTS | Entire | 66 | MW | -140.96 | -232.56 | -223.75 | -233.35 | -242.6 | -251.75 | -262.89 | -276.08 | -277.58 | -284.77 | -289.23
SHTS | Entire | 66 | MVAr | 83.41 | 44.38 | 39.98 | 44.77 | 49.39 | 53.96 | 59.52 | 66.11 | 66.86 | 70.45 | 72.68
SHTS | Entire | 66 | MVA | -163.79 | 236.7567 | 227.2938 | 237.6059 | 247.5765 | 257.4679 | 269.5437 | 283.885 | 285.5187 | 293.355 | 298.222
SMTS | Entire | 66 | MW | -16.2244 | -44.4732 | -62.9789 | -79.1278 | -94.1257 | -108.0887 | -120.7745 | -128.8915 | -134.795 | -140.064 | -144.498
SMTS | Entire | 66 | MVAr | -22.3722 | 25.8328 | 46.3076 | 64.7159 | 81.2309 | 96.0121 | 109.5566 | 117.097 | 122.5376 | 127.3576 | 130.7163
SMTS | Entire | 66 | MVA | -27.636 | -51.4315 | -78.1712 | -102.2221 | -124.3307 | -144.5735 | -163.0617 | -174.14 | -182.168 | -189.3089 | -194.8497
SVTS | Entire | 66 | MW | 64.4 | 40.8 | 40.5 | 30.3 | 18.3 | -0.6 | -19 | -27.6 | -40.4 | -51 | -70.5
SVTS | Entire | 66 | MVAr | -4.1 | -21.5 | -21.5 | -23.4 | -25.5 | -29 | -27.6 | -27 | -25.7 | -24.9 | -23
SVTS | Entire | 66 | MVA | 64.5 | 46.2 | 45.9 | 38.2 | 31.4 | -29 | -33.6 | -38.6 | -47.9 | -56.8 | -74.1
SVTS12 | Split Bus | 66 | MW | 30.5 | 22.2 | 22.4 | 17.3 | 11.5 | 2.1 | -6.8 | -9.6 | -14.6 | -18.1 | -25.5
SVTS12 | Split Bus | 66 | MVAr | -7.6 | -12.7 | -12.7 | -13.7 | -14.9 | -16.8 | -15.9 | -15.3 | -14.3 | -13.5 | -12
SVTS12 | Split Bus | 66 | MVA | 31.5 | 25.6 | 25.7 | 22.1 | 18.8 | 16.9 | -17.2 | -18.1 | -20.4 | -22.6 | -28.2
SVTS34 | Split Bus | 66 | MW | 29 | 19.1 | 18.6 | 13.3 | 7.1 | -2.7 | -12.4 | -18.2 | -26.1 | -33.3 | -45.5
SVTS34 | Split Bus | 66 | MVAr | 7.4 | -8.8 | -8.8 | -9.7 | -10.7 | -12.2 | -11.8 | -11.7 | -11.4 | -11.4 | -11
SVTS34 | Split Bus | 66 | MVA | 29.9 | 21 | 20.6 | 16.4 | 12.8 | -12.5 | -17.1 | -21.7 | -28.5 | -35.2 | -46.8
TBTS | Entire | 66 | MW | 11.8 | -5.4 | -14.9 | -23.7 | -32.8 | -43.6 | -51.5 | -59.1 | -66.3 | -70.2 | -75
TBTS | Entire | 66 | MVAr | -11.3 | -27.5 | -25.7 | -24.1 | -22.4 | -20.4 | -18.9 | -17.5 | -16.1 | -15.4 | -14.5
TBTS | Entire | 66 | MVA | 16.3 | -28.0252 | -29.7069 | -33.8009 | -39.719 | -48.1365 | -54.8585 | -61.6365 | -68.2268 | -71.8693 | -76.3888
TGTS | Entire | 66 | MW | -123.71 | -126.61 | -121.46 | -125.62 | -129.94 | -135.22 | -141.76 | -150.15 | -155.89 | -163.53 | -170.67
TGTS | Entire | 66 | MVAr | 89.3 | 0.45 | 2.53 | 0.85 | -0.89 | -3.01 | -2.31 | -0.85 | 0.15 | 1.47 | 2.72
TGTS | Entire | 66 | MVA | -152.5734 | 126.6108 | 121.4863 | 125.6229 | 129.943 | 135.2535 | 141.7788 | 150.1524 | 155.8901 | 163.5366 | 170.6917
TSTS | Entire | 66 | MW | 49.9 | 7.9 | 2.1 | -2.5 | -9.3 | -22 | -33.2 | -47 | -59.3 | -69.3 | -86.8
TSTS | Entire | 66 | MVAr | -17.2 | -28.4 | -29.9 | -30.9 | -15.1 | -14.1 | -31.4 | -30 | -30.4 | -33.6 | -37.1
TSTS | Entire | 66 | MVA | 52.8 | 29.5 | 30 | -31 | -17.8 | -26.1 | -45.7 | -55.8 | -66.7 | -77 | -94.4
TTS | Entire | 66 | MW | 69.63 | 34.0107 | 24.9011 | 23.4299 | 12.401 | -0.61898 | -13.1855 | -25.3055 | -35.1931 | -44.5077 | -55.3289
TTS | Entire | 66 | MVAr | 0.76085 | 0.61448 | 0.29541 | -0.024471 | -0.34525 | -0.66702 | -0.98989 | -1.3139 | -1.6393 | -1.966 | -2.2943
TTS | Entire | 66 | MVA | 69.6342 | 34.0162 | 24.9029 | 23.4299 | 12.4058 | -0.90998 | -13.2226 | -25.3395 | -35.2312 | -44.5511 | -55.3764
TTS12 | Split Bus | 66 | MW | 36.41 | 21.2751 | 17.9707 | 14.7302 | 10.7409 | 6.8109 | 2.6026 | -1.5774 | -5.0962 | -8.4987 | -12.8393
TTS12 | Split Bus | 66 | MVAr | 1.6208 | 2.9704 | 2.8903 | 2.8108 | 2.732 | 2.6538 | 2.5763 | 2.4993 | 2.4229 | 2.3471 | 2.2718
TTS12 | Split Bus | 66 | MVA | 36.4461 | 21.4815 | 18.2016 | 14.996 | 11.0829 | 7.3096 | 3.6621 | -2.9554 | -5.6429 | -8.8168 | -13.0388
TTS34 | Split Bus | 66 | MW | 33.22 | 12.76 | 6.92 | 8.67 | 1.62 | -7.47 | -15.83 | -23.77 | -30.13 | -36.03 | -42.5
TTS34 | Split Bus | 66 | MVAr | -0.86 | -2.3184 | -2.5582 | -2.7994 | -3.0422 | -3.2867 | -3.5328 | -3.7807 | -4.0304 | -4.2821 | -4.5359
TTS34 | Split Bus | 66 | MVA | 33.2311 | 12.9689 | 7.3777 | 9.1108 | 3.4467 | -8.1611 | -16.2194 | -24.0688 | -30.3984 | -36.2836 | -42.7414
WETS | Entire | 66 | MW | -133.91 | -143.58 | -141.88 | -139.88 | -138.78 | -136.71 | -135.94 | -134.88 | -134.34 | -134.13 | -133.66
WETS | Entire | 66 | MVAr | 9.85 | 47.96 | 47.17 | 46.24 | 45.73 | 44.76 | 44.4 | 43.91 | 43.66 | 43.56 | 43.34
WETS | Entire | 66 | MVA | -134.28 | 151.38 | 149.52 | 147.32 | 146.12 | 143.85 | 143.01 | 141.85 | 141.26 | 141.03 | 140.51
WMTS | Entire | 22 | MW | 0.33 | -35 | -35.78 | -36.3 | -36.64 | -36.51 | -36.4 | -36.33 | -36.41 | -36.67 | -36.98
WMTS | Entire | 22 | MVAr | 0.03 | 7.59 | 7.66 | 7.71 | 7.74 | 7.73 | 7.72 | 7.71 | 7.72 | 7.74 | 7.77
WMTS | Entire | 22 | MVA | 0.33 | 35.81 | 36.59 | 37.11 | 37.45 | 37.32 | 37.21 | 37.14 | 37.22 | 37.48 | 37.79
WMTS | Entire | 66 | MW | 79.1 | 73.62 | 111.68 | 110.76 | 106.28 | 106.89 | 108.25 | 107.2 | 107.61 | 107.45 | 107.1
WMTS | Entire | 66 | MVAr | -17.84 | -15.6708 | -3.7718 | -4.5629 | -6.2542 | -6.0056 | -5.5573 | -5.8291 | -5.6511 | -5.6632 | -5.6356
WMTS | Entire | 66 | MVA | 81.09 | 75.2694 | 111.7437 | 110.8539 | 106.4639 | 107.0586 | 108.3926 | 107.3584 | 107.7583 | 107.5991 | 107.2482
WOTS | Entire | 66 | MW | 3.32 | -3.27 | -4.518 | -5.429 | -6.185 | -6.935 | -7.459 | -7.744 | -7.97 | -8.247 | -8.514
WOTS | Entire | 66 | MVAr | 0.6 | 2.0279 | 2.8019 | 3.3668 | 3.8357 | 4.3008 | 4.6257 | 4.8025 | 4.9426 | 5.1144 | 5.28
WOTS | Entire | 66 | MVA | 3.3738 | -3.8478 | -5.3163 | -6.3882 | -7.2778 | -8.1603 | -8.7769 | -9.1123 | -9.3782 | -9.7041 | -10.0183
WOTS22 | Entire | 22 | MW | -5.16 | -8.74 | -9.639 | -10.301 | -10.641 | -10.944 | -11.227 | -11.535 | -11.73 | -11.883 | -12.033
WOTS22 | Entire | 22 | MVAr | -3.2 | 5.4202 | 5.9777 | 6.3882 | 6.5991 | 6.787 | 6.9625 | 7.1535 | 7.2744 | 7.3693 | 7.4623
WOTS22 | Entire | 22 | MVA | -6.0717 | -10.2842 | -11.3421 | -12.1211 | -12.5211 | -12.8777 | -13.2107 | -13.5731 | -13.8025 | -13.9826 | -14.1591
Note 1: Note that this is the observed actual and have not been weather normalised.

## TsAnnual50_minimum
2023 Terminal Station Minimum Demand Forecast - MW, MVAr & MVA Forecasts aggregated by Terminal Station
Forecasts at time of Station minimum - station diversity factors are applied.
Annual, 50% POE
LOCATIONID | LocationType | VOLTAGE | UNIT | 2023 (Actual Note 1) | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033
ATS_BLTS | Hybrid | 66 | MW | 86.1 | 116.1 | 139.2 | 152.6 | 159.6 | 170.7 | 176 | 172.2 | 169 | 166.3 | 162.1
ATS_BLTS | Hybrid | 66 | MVAr | 10.6 | 16.1 | 26.8 | 35.4 | 40.3 | 48.2 | 52.5 | 50.9 | 49.6 | 48.6 | 47
ATS_BLTS | Hybrid | 66 | MVA | 86.7 | 117.6 | 142.4 | 157.8 | 165.9 | 178.9 | 185.3 | 181 | 177.6 | 174.6 | 170
ATS_WEST | Hybrid | 66 | MW | -36.4 | -5.5 | -8.9 | -18.8 | -27 | -35.1 | -40.1 | -45 | -44.4 | -44.3 | -41.6
ATS_WEST | Hybrid | 66 | MVAr | -5.8 | -11.6 | -11.3 | -10.5 | -9.7 | -9 | -8.6 | -8.1 | -8.2 | -8.2 | -8.4
ATS_WEST | Hybrid | 66 | MVA | -36.8 | -12.9 | -14.4 | -21.5 | -28.7 | -36.2 | -41 | -45.7 | -45.1 | -45 | -42.5
BATS | Entire | 66 | MW | -108.8 | -151 | -148.6 | -155.4 | -163.3 | -171.7 | -179.9 | -190.9 | -196.2 | -201.9 | -207.6
BATS | Entire | 66 | MVAr | 19.2 | 19.7 | 19 | 20.8 | 22.9 | 25 | 27.1 | 30 | 31.4 | 32.8 | 34.3
BATS | Entire | 66 | MVA | -110.5 | -152.3 | -149.8 | -156.8 | -164.9 | -173.5 | -182 | -193.2 | -198.7 | -204.6 | -210.4
BETS | Entire | 22 | MW | -6.3 | -5.3 | -8 | -12.4 | -17.4 | -22.5 | -27.7 | -33.3 | -37 | -40.7 | -44.8
BETS | Entire | 22 | MVAr | 0 | 3.4 | 3.4 | 3.6 | 3.7 | 3.8 | 4 | 4.1 | 4.2 | 4.3 | 4.5
BETS | Entire | 22 | MVA | -6.3 | -6.3 | -8.7 | -12.9 | -17.8 | -22.8 | -28 | -33.5 | -37.2 | -40.9 | -45
BETS | Entire | 66 | MW | -11.9 | -1.6 | -3.7 | -11.2 | -18.9 | -27 | -35 | -43.7 | -48.8 | -53.9 | -58.3
BETS | Entire | 66 | MVAr | 14.7 | 1.1 | 0.9 | 0.5 | 0 | -0.5 | -1 | -1.5 | -1.9 | -2.2 | -2.4
BETS | Entire | 66 | MVA | -18.9 | -1.9 | -3.8 | -11.3 | -18.9 | -27 | -35 | -43.7 | -48.9 | -53.9 | -58.4
BLTS | Entire | 22 | MW | 1 | 6.6 | 12 | 12.4 | 12.1 | 11.8 | 11.5 | 11.1 | 10.9 | 10.7 | 10.6
BLTS | Entire | 22 | MVAr | 0.9 | 0 | 2.2 | 2.4 | 2.3 | 2.2 | 2 | 1.9 | 1.8 | 1.7 | 1.6
BLTS | Entire | 22 | MVA | 1.3 | 6.6 | 12.2 | 12.6 | 12.4 | 12 | 11.6 | 11.3 | 11.1 | 10.9 | 10.7
BLTS-SCI | Hybrid | 66 | MW
BLTS-SCI | Hybrid | 66 | MVAr
BLTS-SCI | Hybrid | 66 | MVA
BTS | Entire | 22 | MW | 15.93 | 18.0894 | 17.4606 | 16.5337 | 15.2299 | 13.3211 | 11.1941 | 10.0139 | 8.8281 | 7.3173 | 4.8865
BTS | Entire | 22 | MVAr | -1.7 | -1.1795 | -1.2067 | -1.2733 | -1.3893 | -1.604 | -1.8482 | -2.0233 | -2.2675 | -2.6005 | -2.5383
BTS | Entire | 22 | MVA | 16.0205 | 18.1278 | 17.5022 | 16.5827 | 15.2931 | 13.4174 | 11.3456 | 10.2163 | 9.1146 | 7.7656 | 5.5064
BTS | Entire | 66 | MW | 57.3 | 101 | 117.5 | 120.2 | 122.6 | 125.4 | 128.2 | 133.8 | 137.3 | 139.5 | 127.7
BTS | Entire | 66 | MVAr | -3.9 | 0.7 | 2.9 | 3.2 | 3.5 | 3.9 | 4.2 | 6.8 | 8.7 | 9.9 | 4.2
BTS | Entire | 66 | MVA | 57.4 | 101 | 117.5 | 120.3 | 122.6 | 125.5 | 128.3 | 134 | 137.5 | 139.9 | 127.8
CBTS | Entire | 66 | MW | -4.5938 | -51.069 | -72.317 | -90.006 | -104.318 | -118.038 | -128.019 | -134.904 | -138.972 | -140.421 | -145.367
CBTS | Entire | 66 | MVAr | -38.6794 | -34.7376 | -42.6685 | -49.1174 | -54.1658 | -58.5491 | -61.8746 | -64.4669 | -65.9829 | -67.0218 | -68.4671
CBTS | Entire | 66 | MVA | -38.9513 | -61.7636 | -83.9664 | -102.5359 | -117.5422 | -131.761 | -142.1877 | -149.5161 | -153.8407 | -155.5956 | -160.6839
DPTS | Hybrid | 66 | MW | -24.48 | 26.27 | 56.47 | 43.36 | 32.37 | 21.68 | 15.03 | 7.35 | 5.56 | 2.96 | 1.44
DPTS | Hybrid | 66 | MVAr | -11.8 | -11.76 | -10.13 | -10.83 | -11.43 | -12.01 | -12.37 | -12.78 | -12.88 | -13.02 | -13.1
DPTS | Hybrid | 66 | MVA | -27.17 | 28.78 | 57.37 | 44.69 | 34.33 | 24.78 | 19.47 | 14.74 | 14.03 | 13.35 | 13.18
ERTS | Entire | 66 | MW | 35.3 | -3.9 | -6.7 | -14.4 | -23.4 | -33.1 | -52.6 | -52.3 | -53 | -56.7 | -62.1
ERTS | Entire | 66 | MVAr | -12.8 | -37.8 | -36.3 | -36.9 | -38.4 | -40.5 | -36.8 | -37.1 | -36.9 | -35.6 | -33.8
ERTS | Entire | 66 | MVA | 37.5 | -38 | -36.9 | -39.6 | -45 | -52.3 | -64.2 | -64.2 | -64.6 | -67 | -70.7
ERTS12 | Split Bus | 66 | MW | 5.5 | 1.4 | 0.5 | -2.5 | -6.3 | -10.5 | -19.1 | -18.8 | -18.9 | -20.5 | -22.8
ERTS12 | Split Bus | 66 | MVAr | -10.4 | -10.8 | -10.7 | -11.2 | -11.9 | -12.8 | -11.6 | -11.8 | -11.8 | -11.3 | -10.7
ERTS12 | Split Bus | 66 | MVA | 11.8 | 10.9 | 10.7 | -11.5 | -13.5 | -16.6 | -22.3 | -22.2 | -22.3 | -23.4 | -25.2
ERTS34 | Split Bus | 66 | MW | 19.8 | 0 | -0.1 | -4 | -9.1 | -14.9 | -27.3 | -26.9 | -27.4 | -29.9 | -33.7
ERTS34 | Split Bus | 66 | MVAr | -6.9 | -23.9 | -23.2 | -24.1 | -25.6 | -27.5 | -24.6 | -25 | -25 | -24 | -22.6
ERTS34 | Split Bus | 66 | MVA | 21 | 23.9 | -23.2 | -24.4 | -27.1 | -31.2 | -36.7 | -36.7 | -37 | -38.4 | -40.6
FBTS | Entire | 66 | MW | 87.3 | 107.5 | 125.2 | 127.7 | 126.3 | 124.3 | 123 | 125.9 | 130.5 | 135.2 | 140.3
FBTS | Entire | 66 | MVAr | -1.1 | 5.9 | 13.6 | 14.7 | 14.1 | 13.2 | 12.6 | 13.9 | 15.9 | 18 | 20.2
FBTS | Entire | 66 | MVA | 87.3 | 107.6 | 125.9 | 128.5 | 127.1 | 125 | 123.6 | 126.6 | 131.5 | 136.4 | 141.7
GNTS | Entire | 66 | MW | -189.5 | -191.966 | -196.12 | -200.133 | -203.653 | -206.864 | -209.527 | -212.043 | -214.057 | -215.839 | -217.561
GNTS | Entire | 66 | MVAr | -4.7 | 4.7397 | 4.8423 | 4.9414 | 5.0283 | 5.1076 | 5.1733 | 5.2354 | 5.2852 | 5.3292 | 5.3717
GNTS | Entire | 66 | MVA | -189.5583 | -192.0245 | -196.1798 | -200.194 | -203.7151 | -206.927 | -209.5909 | -212.1076 | -214.1222 | -215.9048 | -217.6273
GTS | Entire | 66 | MW | 49.11 | 85.37 | 100.88 | 82.95 | 62.37 | 40.02 | 18.71 | -6.47 | -22.02 | -39.8 | -57.2
GTS | Entire | 66 | MVAr | -3.92 | 4.26 | 6.28 | 4.49 | 2.07 | -0.86 | -3.63 | -7.77 | -5.5 | -3.23 | -1.08
GTS | Entire | 66 | MVA | 50.15 | 85.4762 | 101.0753 | 83.0714 | 62.4043 | 40.0292 | 19.0589 | 10.1111 | 22.6965 | 39.9309 | 57.2102
HOTS | Entire | 66 | MW | -22.65 | -19.04 | -13.81 | -15.7 | -17.93 | -20.42 | -23.14 | -26.83 | -28.41 | -30.94 | -33.64
HOTS | Entire | 66 | MVAr | 35.61 | 1.05 | 2.98 | 2.28 | 1.46 | 0.54 | -0.46 | -1.82 | -2.41 | -3.34 | -4.34
HOTS | Entire | 66 | MVA | -42.21 | -19.07 | -14.13 | -15.86 | -17.99 | -20.43 | -23.14 | -26.89 | -28.51 | -31.12 | -33.92
HTS | Entire | 66 | MW | 46.4 | 40.5 | 38.6 | 30.1 | 21 | 1.4 | -10.4 | -20.4 | -28.3 | -31 | -54.2
HTS | Entire | 66 | MVAr | -2.1 | -17.4 | -17.9 | -19.8 | -21.8 | -26.3 | -24.3 | -22 | -20.2 | -19.6 | -14.3
HTS | Entire | 66 | MVA | 46.4 | 44 | 42.5 | 36.1 | 30.3 | 26.3 | -26.4 | -30 | -34.8 | -36.6 | -56
HYTS | Entire | 22 | MW | 0.02 | -0.06 | -0.08 | -0.09 | -0.11 | -0.13 | -0.16 | -0.19 | -0.21 | -0.25 | -0.31
HYTS | Entire | 22 | MVAr | -0.04 | -0.07 | -0.07 | -0.06 | -0.05 | -0.05 | -0.04 | -0.03 | -0.02 | -0.01 | 0.01
HYTS | Entire | 22 | MVA | 0.05 | -0.09 | -0.11 | -0.11 | -0.12 | -0.14 | -0.16 | -0.19 | -0.21 | -0.25 | -0.31
KGTS | Entire | 22 | MW | 0.03 | -2.4 | -23.04 | -24.25 | -25.18 | -26.07 | -27.14 | -28.29 | -28.85 | -29.58 | -30.5
KGTS | Entire | 22 | MVAr | 0 | 0.18 | -2.9 | -3.15 | -3.32 | -3.49 | -3.7 | -3.92 | -4.02 | -4.16 | -4.33
KGTS | Entire | 22 | MVA | 0.03 | 2.4067 | 23.2218 | 24.4537 | 25.3979 | 26.3026 | 27.391 | 28.5603 | 29.1287 | 29.8711 | 30.8058
KGTS | Entire | 66 | MW | -81.5 | -61 | -57.38 | -57.59 | -58.16 | -58.64 | -59.2 | -60.01 | -60.06 | -60.2 | -60.52
KGTS | Entire | 66 | MVAr | 21.09 | 1.36 | 0.37 | 0.42 | 0.58 | 0.71 | 0.87 | 1.09 | 1.1 | 1.14 | 1.23
KGTS | Entire | 66 | MVA | -84.18 | -61.02 | -57.38 | -57.59 | -58.16 | -58.64 | -59.21 | -60.02 | -60.07 | -60.21 | -60.53
KTS | Entire | 66 | MW | 64.15 | 53.6358 | 36.9428 | 19.6288 | -0.083975 | -20.0522 | -40.3373 | -54.3161 | -66.4916 | -78.0657 | -93.1551
KTS | Entire | 66 | MVAr | -7.2 | -16.9296 | -18.0636 | -19.5281 | -20.5242 | -21.5747 | -22.7488 | -23.7294 | -24.5372 | -25.429 | -24.1395
KTS | Entire | 66 | MVA | 58.8324 | 47.2498 | 33.1183 | 16.9392 | -1.8833 | -21.1725 | -40.7618 | -54.1221 | -65.5244 | -75.9543 | -89.8868
KTS_East | Split Bus | 66 | MW | 69.61 | 66.0654 | 61.4181 | 56.5735 | 49.7916 | 42.2316 | 34.6041 | 28.0075 | 22.5384 | 16.7215 | 9.6884
KTS_East | Split Bus | 66 | MVAr | 2.13 | -2.7291 | -3.6427 | -4.6564 | -5.7801 | -6.9644 | -8.2388 | -9.1876 | -10.0483 | -10.8707 | -10.0007
KTS_East | Split Bus | 66 | MVA | 69.6426 | 66.1218 | 61.5261 | 56.7648 | 50.1259 | 42.802 | 35.5713 | 29.476 | 24.6769 | 19.9445 | 13.924
KTS_West | Split Bus | 66 | MW | -5.46 | -12.4296 | -24.4753 | -36.9446 | -49.8755 | -62.2838 | -74.9413 | -82.3236 | -89.0301 | -94.7872 | -102.8435
KTS_West | Split Bus | 66 | MVAr | -9.33 | -14.2006 | -14.4209 | -14.8717 | -14.7441 | -14.6104 | -14.51 | -14.5418 | -14.4889 | -14.5583 | -14.1388
KTS_West | Split Bus | 66 | MVA | -10.8102 | -18.8719 | -28.4078 | -39.8255 | -52.0092 | -63.9745 | -76.3331 | -83.5981 | -90.2013 | -95.8987 | -103.8108
LY* | Entire | 66 | MW | 2.16 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7
LY* | Entire | 66 | MVAr | -5.08 | -6.35 | -6.35 | -6.35 | -6.35 | -6.35 | -6.35 | -6.35 | -6.35 | -6.35 | -6.35
LY* | Entire | 66 | MVA | 5.5201 | 6.9002 | 6.9002 | 6.9002 | 6.9002 | 6.9002 | 6.9002 | 6.9002 | 6.9002 | 6.9002 | 6.9002
MBTS | Entire | 66 | MW | -8.7 | -10.617 | -11.784 | -12.805 | -13.663 | -14.419 | -14.992 | -15.535 | -15.9 | -16.209 | -16.541
MBTS | Entire | 66 | MVAr | 2.8 | 3.4738 | 3.8556 | 4.1897 | 4.4704 | 4.7177 | 4.9052 | 5.0829 | 5.2023 | 5.3034 | 5.412
MBTS | Entire | 66 | MVA | -9.1395 | -11.1708 | -12.3987 | -13.473 | -14.3757 | -15.1712 | -15.7741 | -16.3454 | -16.7294 | -17.0546 | -17.4039
MTS | Entire | 22 | MW | 3 | 4.8 | 4.9 | 5 | 5.1 | 5.2 | 5.2 | 5.3 | 5.3 | 5.4 | 5.5
MTS | Entire | 22 | MVAr | -0.5 | -2.8 | -2.8 | -2.7 | -2.7 | -2.7 | -2.7 | -2.7 | -2.7 | -2.7 | -2.7
MTS | Entire | 22 | MVA | 3.1 | 5.6 | 5.6 | 5.7 | 5.8 | 5.8 | 5.9 | 5.9 | 6 | 6 | 6.1
MTS | Entire | 66 | MW | 35.1 | 36.7 | 37.5 | 31.4 | 25.8 | 18.1 | 12.2 | 5.8 | 0.8 | -2.4 | -10
MTS | Entire | 66 | MVAr | -10.6 | -13.2 | -13.1 | -14.2 | -15.2 | -16.6 | -17.8 | -18.9 | -19.9 | -19.6 | -18.1
MTS | Entire | 66 | MVA | 36.6 | 39 | 39.7 | 34.5 | 29.9 | 24.6 | 21.5 | 19.8 | 19.9 | -19.7 | -20.7
MTS6622 | Entire | 66 | MW | 39.4 | 41.6 | 42.4 | 36.4 | 30.9 | 23.3 | 17.4 | 11 | 6.1 | 3 | -4.5
MTS6622 | Entire | 66 | MVAr | -11.4 | -16 | -15.8 | -16.9 | -18 | -19.4 | -20.5 | -21.6 | -22.6 | -22.2 | -20.8
MTS6622 | Entire | 66 | MVA | 41 | 44.5 | 45.2 | 40.2 | 35.7 | 30.3 | 26.8 | 24.3 | 23.4 | 22.4 | -21.3
MWTS | Entire | 66 | MW | -72.5 | 7.682 | -3.551 | -12.405 | -18.942 | -23.895 | -27.892 | -30.182 | -32.042 | -33.542 | -34.754
MWTS | Entire | 66 | MVAr | 51 | 0.89678 | 0.41454 | 1.4481 | 2.2112 | 2.7894 | 3.256 | 3.5234 | 3.7405 | 3.9156 | 4.0571
MWTS | Entire | 66 | MVA | -88.6411 | 7.7342 | -3.5751 | -12.4892 | -19.0706 | -24.0573 | -28.0814 | -30.387 | -32.2596 | -33.7698 | -34.99
RCTS | Entire | 22 | MW | 0.12 | 3.49 | 5.47 | 4.66 | 3.53 | 2.33 | 1.31 | 0.23 | -0.68 | -1.24 | -2.05
RCTS | Entire | 22 | MVAr | -1.6 | 0.02 | 0.04 | 0.03 | 0.02 | 0.01 | 0 | 0 | 0 | 0 | 0.01
RCTS | Entire | 22 | MVA | 1.6045 | 3.49 | 5.47 | 4.66 | 3.53 | 2.33 | 1.31 | 0.23 | -0.68 | -1.24 | -2.05
RCTS | Entire | 66 | MW | -156.31 | -117.07 | -115.67 | -118.43 | -122.2 | -125.82 | -128.81 | -132.51 | -132.42 | -133.59 | -136.01
RCTS | Entire | 66 | MVAr | 41.45 | 15.79 | 15.35 | 16.21 | 17.38 | 18.5 | 19.43 | 20.58 | 20.56 | 20.92 | 21.67
RCTS | Entire | 66 | MVA | -161.7125 | 118.1301 | 116.6841 | 119.5342 | 123.4298 | 127.1728 | 130.2672 | 134.0986 | 134.0066 | 135.2181 | 137.7255
RTS | Entire | 22 | MW | 2.24 | 20.55 | 19.77 | 44.75 | 44.29 | 43.97 | 43.72 | 43.54 | 43.4 | 43.29 | 43.22
RTS | Entire | 22 | MVAr | 0.23 | 0.86 | 0.65 | 8.44 | 8.29 | 8.19 | 8.11 | 8.05 | 8.01 | 7.97 | 7.95
RTS | Entire | 22 | MVA | 2.2518 | 20.57 | 19.78 | 45.54 | 45.06 | 44.73 | 44.47 | 44.28 | 44.13 | 44.02 | 43.95
RTS | Entire | 66 | MW | 117.01 | 121.23 | 146.15 | 152.51 | 153.81 | 154.61 | 155.33 | 157.48 | 163.37 | 168.28 | 170.54
RTS | Entire | 66 | MVAr | -44.84 | -35.7 | -26.93 | -24.81 | -24.5 | -24.3 | -24 | -23.2 | -21.1 | -19.3 | -18.4
RTS | Entire | 66 | MVA | 125.31 | 126.38 | 148.6104 | 154.5148 | 155.7 | 156.5 | 157.2 | 159.2 | 164.7 | 169.4 | 171.5
RWTS | Entire | 66 | MW | 39.81 | 16.2042 | 13.1168 | 9.0336 | 4.3707 | -1.9507 | -9.1169 | -15.2211 | -19.1735 | -20.6296 | -27.3702
RWTS | Entire | 66 | MVAr | -1.06 | 1.9429 | 3.0649 | 3.5314 | 3.4339 | 3.0713 | 3.3815 | 4.1697 | 4.6684 | 4.8359 | 5.6812
RWTS | Entire | 66 | MVA | 39.8241 | 16.3202 | 13.4701 | 9.6993 | 5.5584 | -3.6384 | -9.7238 | -15.7819 | -19.7337 | -21.1888 | -27.9536
RWTS13 | Split Bus | 66 | MW | 23.24 | 12.2892 | 11.8622 | 9.1537 | 4.835 | -1.0582 | -8.0744 | -14.8339 | -19.7288 | -22.0903 | -29.9815
RWTS13 | Split Bus | 66 | MVAr | -5.96 | -4.6111 | -3.9539 | -5.2405 | -7.9814 | -11.9026 | -11.4964 | -6.6699 | -3.1619 | -1.429 | 4.2357
RWTS13 | Split Bus | 66 | MVA | 23.9921 | 13.1258 | 12.5038 | 10.5476 | 9.3316 | -11.9495 | -14.0486 | -16.2645 | -19.9806 | -22.1365 | -30.2792
RWTS22 | Entire | 22 | MW | 13.89 | 9.5614 | 8.1865 | 7.0131 | 6.0085 | 4.4912 | 2.9966 | 1.9673 | 0.95054 | 0.64654 | -0.49515
RWTS22 | Entire | 22 | MVAr | -1.36 | -0.82253 | 0.46392 | 1.7727 | 3.0992 | 4.7937 | 6.5097 | 8.0458 | 9.6036 | 10.5754 | 12.3506
RWTS22 | Entire | 22 | MVA | 13.9564 | 9.5967 | 8.1996 | 7.2336 | 6.7607 | 6.5689 | 7.1663 | 8.2828 | 9.6505 | 10.5951 | -12.3605
RWTS24 | Split Bus | 66 | MW | 11.6 | 3.915 | 1.2546 | -0.12006 | -0.46423 | -0.89245 | -1.0425 | -0.38719 | 0.55528 | 1.4607 | 2.6113
RWTS24 | Split Bus | 66 | MVAr | 3.14 | 0.1237 | 0.039644 | 0.003794 | 0.014669 | 0.0282 | 0.032942 | 0.012235 | 0.017546 | 0.046156 | 0.082512
RWTS24 | Split Bus | 66 | MVA | 12.0175 | 3.9169 | 1.2553 | -0.12012 | -0.46446 | -0.8929 | -1.043 | -0.38738 | 0.55555 | 1.4615 | 2.6126
SHTS | Entire | 66 | MW | -141 | -170.89 | -162.9 | -172.82 | -183.68 | -195.63 | -205.67 | -217.89 | -221.35 | -227.05 | -232.88
SHTS | Entire | 66 | MVAr | 83.41 | 13.58 | 9.59 | 14.54 | 19.97 | 25.93 | 30.95 | 37.05 | 38.78 | 41.63 | 44.54
SHTS | Entire | 66 | MVA | -163.8 | 171.4287 | 163.182 | 173.4306 | 184.7624 | 197.341 | 207.9857 | 221.0175 | 224.7214 | 230.8349 | 237.101
SMTS | Entire | 66 | MW | -16.2244 | -22.9631 | -41.7954 | -57.6623 | -72.4181 | -86.073 | -98.0899 | -105.7251 | -111.1272 | -115.8735 | -119.8146
SMTS | Entire | 66 | MVAr | -22.3722 | 5.3351 | 26.287 | 44.454 | 60.5815 | 74.6829 | 87.4125 | 94.2482 | 99.0242 | 103.1906 | 105.9232
SMTS | Entire | 66 | MVA | -27.636 | -23.5747 | -49.3748 | -72.8086 | -94.4167 | -113.9565 | -131.3871 | -141.6352 | -148.8457 | -155.1611 | -159.9227
SVTS | Entire | 66 | MW | 64.4 | 67 | 69.8 | 61.1 | 49.5 | 26.9 | 10.6 | 2.7 | -7.5 | -17 | -40.9
SVTS | Entire | 66 | MVAr | -4.1 | -16.6 | -16 | -17.6 | -19.7 | -23.9 | -26.8 | -28 | -29.7 | -30.8 | -28
SVTS | Entire | 66 | MVA | 64.5 | 69 | 71.6 | 63.6 | 53.3 | 36 | 28.9 | 28.2 | -30.6 | -35.2 | -49.6
SVTS12 | Split Bus | 66 | MW | 30.5 | 35.8 | 37.5 | 33.2 | 27.4 | 15.9 | 8.3 | 6 | 2.4 | -0.4 | -10.3
SVTS12 | Split Bus | 66 | MVAr | -7.6 | -9.9 | -9.6 | -10.5 | -11.6 | -14 | -15.5 | -16 | -16.7 | -17.2 | -15.1
SVTS12 | Split Bus | 66 | MVA | 31.5 | 37.2 | 38.7 | 34.8 | 29.8 | 21.2 | 17.6 | 17.1 | 16.9 | -17.2 | -18.3
SVTS34 | Split Bus | 66 | MW | 29 | 31.9 | 33.1 | 28.6 | 22.7 | 11.3 | 2.5 | -3.2 | -9.9 | -16.6 | -30.8
SVTS34 | Split Bus | 66 | MVAr | 7.4 | -6.7 | -6.5 | -7.2 | -8.1 | -10 | -11.3 | -12 | -12.9 | -13.7 | -12.9
SVTS34 | Split Bus | 66 | MVA | 29.9 | 32.6 | 33.7 | 29.5 | 24.1 | 15.1 | 11.6 | -12.5 | -16.3 | -21.5 | -33.4
TBTS | Entire | 66 | MW | 11.8 | 8 | -1.5 | -10.2 | -18.5 | -28.2 | -36.8 | -44.2 | -51.1 | -55.1 | -59.4
TBTS | Entire | 66 | MVAr | -11.3 | -27 | -28.2 | -26.6 | -25 | -23.2 | -21.6 | -20.3 | -19 | -18.2 | -17.4
TBTS | Entire | 66 | MVA | 16.338 | 28.1603 | -28.2399 | -28.4886 | -31.1006 | -36.5168 | -42.6708 | -48.6388 | -54.518 | -58.028 | -61.896
TGTS | Entire | 66 | MW | -123.71 | -112.87 | -109.18 | -112.56 | -117.11 | -122.82 | -129.38 | -137.77 | -143.49 | -150.08 | -157.59
TGTS | Entire | 66 | MVAr | 89.3 | 5.99 | 7.47 | 6.11 | 4.28 | 1.98 | -0.66 | -3 | -2.01 | -0.86 | 0.44
TGTS | Entire | 66 | MVA | -152.5734 | 113.0288 | 109.4352 | 112.7257 | 117.1882 | 122.836 | 129.3817 | 137.8027 | 143.5041 | 150.0825 | 157.5906
TSTS | Entire | 66 | MW | 49.9 | 31 | 23.9 | 16 | 6.6 | -5.9 | -17.2 | -31.1 | -42.8 | -52.1 | -70.3
TSTS | Entire | 66 | MVAr | -17.2 | -20.8 | -22.8 | -25 | -27.4 | -29.8 | -30.2 | -28.4 | -25.3 | -22.6 | -17.7
TSTS | Entire | 66 | MVA | 52.8 | 37.3 | 33 | 29.7 | 28.2 | -30.4 | -34.7 | -42.1 | -49.8 | -56.8 | -72.5
TTS | Entire | 66 | MW | 71.44 | 56.145 | 47.4819 | 45.6872 | 34.6613 | 22.0677 | 10.1977 | -1.4193 | -11.0205 | -20.1451 | -30.6498
TTS | Entire | 66 | MVAr | 4.1303 | 0.61448 | 0.29541 | -0.024471 | -0.34525 | -0.66702 | -0.98989 | -1.3139 | -1.6393 | -1.966 | -2.2943
TTS | Entire | 66 | MVA | 71.5593 | 56.1484 | 47.4829 | 45.6872 | 34.663 | 22.0778 | 10.2457 | -1.9341 | -11.1417 | -20.2408 | -30.7355
TTS12 | Split Bus | 66 | MW | 38.22 | 29.1418 | 26.4656 | 23.4133 | 19.6305 | 15.6887 | 11.6687 | 7.7051 | 4.2645 | 0.89202 | -3.3204
TTS12 | Split Bus | 66 | MVAr | 4.9903 | 2.9704 | 2.8903 | 2.8108 | 2.732 | 2.6538 | 2.5763 | 2.4993 | 2.4229 | 2.3471 | 2.2718
TTS12 | Split Bus | 66 | MVA | 38.5444 | 29.2928 | 26.6229 | 23.5815 | 19.8196 | 15.9115 | 11.9497 | 8.1003 | 4.9047 | 2.5109 | -4.0232
TTS34 | Split Bus | 66 | MW | 33.22 | 27.08 | 21.06 | 22.3 | 15.05 | 6.4 | -1.45 | -9.1 | -15.25 | -20.99 | -27.27
TTS34 | Split Bus | 66 | MVAr | -0.86 | -2.3184 | -2.5582 | -2.7994 | -3.0422 | -3.2867 | -3.5328 | -3.7807 | -4.0304 | -4.2821 | -4.5359
TTS34 | Split Bus | 66 | MVA | 33.2311 | 27.1791 | 21.2148 | 22.475 | 15.3544 | 7.1946 | -3.8188 | -9.8541 | -15.7736 | -21.4223 | -27.6447
WETS | Entire | 66 | MW | -133.91 | -120.58 | -118.79 | -117.82 | -116.7 | -115.31 | -114.76 | -114.28 | -114.02 | -113.96 | -113.77
WETS | Entire | 66 | MVAr | 9.85 | 37.26 | 36.42 | 35.97 | 35.45 | 34.8 | 34.55 | 34.32 | 34.2 | 34.18 | 34.09
WETS | Entire | 66 | MVA | -134.28 | -126.21 | -124.25 | -123.19 | -121.97 | -120.45 | -119.85 | -119.32 | -119.04 | -118.98 | -118.77
WMTS | Entire | 22 | MW | 0.33 | -16.13 | -16.49 | -16.73 | -17.04 | -16.99 | -16.94 | -16.89 | -16.93 | -17.03 | -17.18
WMTS | Entire | 22 | MVAr | 0.03 | 2.69 | 2.79 | 2.86 | 2.94 | 2.93 | 2.91 | 2.9 | 2.91 | 2.94 | 2.98
WMTS | Entire | 22 | MVA | 0.33 | -16.35 | -16.72 | -16.97 | -17.29 | -17.24 | -17.19 | -17.14 | -17.18 | -17.28 | -17.44
WMTS | Entire | 66 | MW | 79.1 | 82.43 | 120 | 117.52 | 112.2 | 112.3 | 113.49 | 112.75 | 112.92 | 112.72 | 112.16
WMTS | Entire | 66 | MVAr | -17.8 | -14.9508 | -3.1018 | -4.0529 | -5.7042 | -5.5056 | -5.0773 | -5.3091 | -5.2311 | -5.2132 | -5.1956
WMTS | Entire | 66 | MVA | 81.1 | 83.7749 | 120.0401 | 117.5899 | 112.3449 | 112.4349 | 113.6035 | 112.8749 | 113.0411 | 112.8405 | 112.2803
WOTS | Entire | 66 | MW | 3.32 | -0.05 | -1.305 | -2.286 | -3.014 | -3.829 | -4.32 | -4.555 | -4.713 | -4.894 | -5.057
WOTS | Entire | 66 | MVAr | 0.6 | 0.031008 | 0.8093 | 1.4177 | 1.8691 | 2.3746 | 2.6791 | 2.8248 | 2.9228 | 3.035 | 3.1361
WOTS | Entire | 66 | MVA | 3.3738 | -0.058834 | -1.5356 | -2.6899 | -3.5465 | -4.5055 | -5.0833 | -5.3598 | -5.5457 | -5.7587 | -5.9505
WOTS22 | Entire | 22 | MW | -5.16 | -8 | -8.747 | -9.28 | -9.628 | -9.848 | -10.119 | -10.321 | -10.425 | -10.515 | -10.611
WOTS22 | Entire | 22 | MVAr | -3.2 | 4.9612 | 5.4245 | 5.755 | 5.9709 | 6.1073 | 6.2753 | 6.4006 | 6.4651 | 6.5209 | 6.5805
WOTS22 | Entire | 22 | MVA | -6.0717 | -9.4135 | -10.2925 | -10.9197 | -11.3291 | -11.588 | -11.9069 | -12.1446 | -12.267 | -12.3729 | -12.4858
Note 1: Note that this is the observed actual and have not been weather normalised.