## Terminal station minimum demand
Terminal Station Minimum Demand | On-load Capacity - N Export Rating (MVA) | Hot or Cold Spare Capacity - N Export Rating (MVA) | Total Capacity - N Export Rating (MVA) | Cyclic N-1 Export Rating (MVA) | Hours 95% of Minimum Demand | Station Power Factor at Minimum Demand | Generation Capacity <=1MW (MW) | Generation Capacity >1MW (MW) | Actual Minimum Demand (MVA) | 50% PoE Forecast Minimum Demand (MVA) |  |  |  |  | MW Above N-1 Export Rating (2023) | Energy at Risk (MWh) (N-1 50% PoE) |  |  |  |  | Hours at Risk (N-1 50% PoE)
[9 empty] | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2023 | 2024 | 2025 | 2026 | 2027
BTS 22kV | [8 empty] | 18.83 | 18.9025 | 18.5294 | 18.2321 | 16.2257 | 13.5488 | 0
BTS 66kV |  |  | -675 | -450 | 1 | 0.75 | 5.5 |  | 23.4914 | 53.8106 | 71.7276 | 78.1878 | 76.2294 | 73.2089 | 0
FBTS 66kV |  |  | -450 | -300 | 5 | 0.99 | 7.7 |  | 28.4637 | 99.5047 | 114.0754 | 137.977 | 138.1784 | 133.8308 | 0
RTS 66kV |  |  | -675 | -450 | 17 | 0.97 | 21 |  | 52.419 | 82.8193 | 95.1291 | 107.8393 | 107.1492 | 104.8573 | 0
RTS 22kV |  |  | -190 | -95 | 4 | -1 | 1.03 |  | -0.3143 | 10.0398 | 41.4062 | 34.5582 | 34.3572 | 34.0543 | 0
WMTS 66kV |  |  | -675 | -450 | 1 | 0.95 | 23.5 |  | 38.7063 | 81.853 | 100.6004 | 138.6717 | 136.9994 | 132.1756 | 0
WMTS 22kV |  |  | -330 | -165 | 4 | 0.23 | 1.3 |  | 2.5798 | -4.29 | -5.16 | -17.67 | 0 | 0 | 0

## Zone substations minimum demand
Zone Substation Minimum Demand |  | On-load Capacity - N Export Rating (MVA) | Cyclic N-1 Export Rating (MVA) | Hours 95% of Minimum Demand | Station Power Factor at Minimum Demand | Generation Capacity <=1MW (MW) | Generation Capacity >1MW (MW) | Actual Minimum Demand (MVA) | 50% PoE Forecast Minimum Demand (MVA) |  |  |  |  | MW Above N-1 Export Rating (2023) | Energy at Risk (MWh) (N-1 50% PoE) |  |  |  |  | Hours at Risk (N-1 50% PoE)
[8 empty] | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2023 | 2024 | 2025 | 2026 | 2027
BTS 22kV
BK | S | -23 | -20 |  | 0.96314 |  |  | 1.8402 | 1.9533 | 2.0646 | 2.5976 | 2.2945 | 1.864 | 0
BK | W | -23 | -20 |  | 1 |  |  | 3.56 | 3.4928 | 4.1239 | 4.5317 | 4.3278 | 4.2161 | 0
C | S | -22.5 | -15 |  | 0.93089 |  |  | 1.3693 | 0.89844 | 0.80957 | 0.87932 | 0.86977 | 0.44777 | 0
C | W | -22.5 | -15 |  | 0.9962 |  |  | 2.3355 | 0.067082 | -0.12728 | -0.12728 | -0.1 | -0.080623 | 0
F | S | -20 | -10 |  | 0.92213 |  |  | 1.6243 | 2.2755 | 1.9433 | 1.6621 | 1.322 | 0.96881 | 0
F | W | -20 | -10 |  | 0.99844 |  |  | 3.2785 | 2.6672 | 2.7577 | 2.868 | 2.9189 | 3.0095 | 0
BTS 66kV
BQ | S | -110 | -55 |  | 0.9997 |  | 12.4 | 9.7296 | 17.7974 | 19.0675 | 22.1508 | 22.6777 | 22.7168 | 0
BQ | W | -110 | -55 |  | 0.99971 |  |  | 14.4608 | 17.0043 | 19.5538 | 21.229 | 21.3776 | 21.7554 | 0
VM | S | -84 | -57 |  | 0.99874 |  |  | 9.4394 | 12.7061 | 26.1978 | 29.1281 | 28.6754 | 28.0367 | 0
VM | W | -84 | -57 |  | 0.9994 |  |  | 10.687 | 23.3377 | 28.6441 | 28.2934 | 27.7058 | 27.1611 | 0
WA | S | -84 | -54 |  | 0.98291 |  |  | 3.3005 | 3.5893 | 4.4918 | 4.5822 | 4.6331 | 4.6644 | 0
WA | W | -84 | -54 |  | 0.98505 |  |  | 9.4191 | 6.3478 | 6.5697 | 6.6421 | 6.6716 | 6.7226 | 0
MP | S | -165 | -110 |  | 0.9621 |  | 1.15 | 10.3415 | 12.71 | 15.22 | 15.93 | 16.15 | 16.26 | 0
MP | W | -165 | -110 |  | 0.9998 |  |  | 19.8572 | 12.18 | 13.23 | 13.45 | 13.58 | 13.71 | 0
DLF 22kV
TP | S | 0 | 0 |  | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
TP | W | 0 | 0 |  | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
FBTS 66kV
AP | S | -87 | -57 |  | 0.93579 |  |  | 6.4455 | 11.8705 | 13.6988 | 14.1023 | 14.2271 | 14.2867 | 0
AP | W | -87 | -57 |  | 1 |  |  | 11.62 | 12.657 | 13.827 | 14.1116 | 14.2867 | 14.5344 | 0
E | S | -13.5 | 0 |  | 0.01309 |  |  | -0.21293 | -0.67007 | -0.74404 | -0.78816 | -0.81025 | -0.81841 | 0.53
E | W | -13.5 | 0 |  | 0.22567 |  |  | 0.21417 | -0.48104 | -0.51662 | -0.52402 | -0.53814 | -0.53814 | 0.35
FB | S | -90 | -60 |  | 0.99211 |  |  | 7.8419 | 16.9024 | 23.8933 | 24.431 | 24.4522 | 24.4026 | 0
FB | W | -90 | -60 |  | 0.99859 |  |  | 9.4199 | 19.8752 | 23.0703 | 23.1684 | 23.1546 | 23.2037 | 0
MG | S | -87 | -57 |  | 0.97022 |  |  | 6.3841 | 6.81 | 7.67 | 7.95 | 7.39 | 6.74 | 0
MG | W | -87 | -57 |  | 1 |  |  | 9.2167 | 8.52 | 8.99 | 8.63 | 7.99 | 7.93 | 0
PM | S | -27 | -13.5 |  | 0.80725 |  |  | 1.8036 | 3.8015 | 6.084 | 7.1955 | 6.9367 | 6.5976 | 0
PM | W | -27 | -13.5 |  | 0.99889 |  |  | 4.0979 | 6.28 | 8.7566 | 8.9842 | 8.7273 | 8.4899 | 0
SB | S | -110 | -55 |  | 0.99988 |  | 6 | 13.1683 | 20.0247 | 20.7901 | 23.1664 | 24.5816 | 24.2091 | 0
SB | W | -110 | -55 |  | 0.99998 |  |  | 14.877 | 18.0724 | 19.954 | 21.6479 | 21.7185 | 21.1935 | 0
SO | S | -87 | -57 |  | 0.97775 |  |  | 6.1166 | 5.62 | 7.1 | 8.21 | 8.3569 | 8.462 | 0
SO | W | -87 | -57 |  | 0.99995 |  |  | 8.357 | 5.86 | 7.67 | 7.89 | 8 | 8.12 | 0
WG | S | -81 | -54 |  | 0.99695 |  |  | 15.213 | 17.1566 | 19.3731 | 31.3393 | 31.7533 | 31.8834 | 0
WG | W | -81 | -54 |  | 0.99974 |  |  | 15.204 | 18.1309 | 24.8412 | 31.917 | 32.1773 | 32.2978 | 0
RTS 66kV
AR | S | -60 | -30 |  | 0.59107 |  |  | 3.2374 | 5.367 | 5.4464 | 6.0747 | 5.9594 | 5.6713 | 0
AR | W | -60 | -30 |  | 0.99259 |  |  | 7.2336 | 6.6367 | 7.1843 | 7.3419 | 7.1752 | 7.1077 | 0
B | S | -54 | -27 |  | 0.99131 |  | 6.2 | 4.4759 | 9.1277 | 10.4315 | 15.6917 | 15.9527 | 15.5622 | 0
B | W | -54 | -27 |  | 0.98505 |  | 6.2 | 3.6953 | 10.6306 | 15.0441 | 16.823 | 16.4721 | 16.2741 | 0
BC | S | -87 | -57 |  | 0.92461 |  |  | 5.5449 | 7.6054 | 8.8622 | 9.6473 | 9.6672 | 9.6573 | 0
BC | W | -87 | -57 |  | 0.99937 |  |  | 11.8241 | 10.4104 | 11.6572 | 11.8184 | 11.8483 | 12.0294 | 0
CL | S | -87 | -57 |  | 0.62298 |  |  | 5.4218 | 8.6201 | 9.7539 | 10.6561 | 10.4567 | 9.9335 | 0
CL | W | -87 | -57 |  | 0.99207 |  |  | 11.2432 | 11.7098 | 12.7736 | 12.8047 | 12.4426 | 12.3322 | 0
CW | S | -54 | -27 |  | 0.99622 |  |  | 6.0596 | 0 | 0 | 0 | 0 | 0 | 0
CW | W | -54 | -27 |  | 0.99611 |  |  | 6.3915 | 0 | 0 | 0 | 0 | 0 | 0
FR | S | -90 | -60 |  | 0.98433 |  |  | 6.7586 | 5.92 | 6.2 | 7.35 | 7.7 | 7.74 | 0
FR | W | -90 | -60 |  | 0.99946 |  |  | 11.2599 | 7.61 | 8.5213 | 9.3041 | 9.3982 | 9.4602 | 0
NR | S | -83 | -55 |  | 1 |  | 2.6 | 0 | -0.75802 | 0.40447 | 2.2657 | 1.9418 | 1.608 | 0
NR | W | -83 | -55 |  | 1 |  | 2.6 | 0 | -0.31401 | 2.0323 | 2.2246 | 1.8612 | 1.5373 | 0
SK | S | -87 | -57 |  | 0.97069 |  | 6.2 | 10.1173 | 11.5773 | 11.832 | 11.9953 | 12.0162 | 11.9346 | 0
SK | W | -87 | -57 |  | 0.99946 |  | 6.2 | 9.3117 | 12.2204 | 12.4556 | 12.5881 | 12.6091 | 12.7008 | 0
TK | S | -87 | -57 |  | 0.989 |  |  | 6.0344 | 9.8886 | 10.7647 | 13.7597 | 15.415 | 16.6628 | 0
TK | W | -87 | -57 |  | 0.96991 |  |  | 8.4455 | 11.4285 | 13.5471 | 15.9977 | 17.7624 | 18.5581 | 0
WP | S | -110 | -55 |  | 0.86083 |  |  | 2.6972 | 2.2614 | 3.1684 | 3.2289 | 2.9062 | 2.5738 | 0
WP | W | -110 | -55 |  | 0.99995 |  |  | 6.5668 | 4.9713 | 5.2131 | 4.9215 | 4.5784 | 4.3674 | 0
RTS 22kV
R | S | -40 | -26.5 |  | 0.71347 |  |  | 3.3462 | 9.4952 | 16.4895 | 20.6956 | 20.6546 | 20.3251 | 0
R | W | -40 | -26.5 |  | 0.97901 |  |  | 4.9233 | 12.8216 | 19.8259 | 20.8653 | 20.6956 | 20.5853 | 0
WMTS 66kV
JA | S | -165 | -110 |  | 0.91613 |  |  | 16.9179 | 25.1173 | 38.4157 | 44.0106 | 42.4655 | 40.5052 | 0
JA | W | -165 | -110 |  | 0.99922 |  |  | 29.8833 | 32.237 | 42.4068 | 41.3768 | 39.4563 | 38.0792 | 0
LQ | S | -180 | -120 |  | 0.94612 |  |  | 8.7202 | 10.3563 | 10.5761 | 14.8707 | 14.4912 | 13.188 | 0
LQ | W | -180 | -120 |  | 0.99997 |  |  | 16.4106 | 15.2171 | 18.1011 | 19.6535 | 18.3669 | 17.4852 | 0
NC | S | -60 | -30 |  | 0.98221 |  |  | 2.0769 | 2.1767 | 0.65924 | -0.42579 | -2.6732 | -4.8795 | 0
NC | W | -60 | -30 |  | 0.99991 |  |  | 5.5172 | 4.7678 | 4.4241 | 3.1286 | 1.3267 | 0.022361 | 0
DA | S | -40.5 | -27 |  | 0.9462 |  | 2 | 6.3869 | 8.0156 | 8.549 | 9.1049 | 8.549 | 7.7977 | 0
DA | W | -40.5 | -27 |  | 0.96252 |  |  | 9.1565 | 13.3111 | 13.8967 | 13.8872 | 13.2162 | 12.6718 | 0
WB | S | -60 | -30 |  | 0.9864 |  |  | 2.9062 | 5.7147 | 5.9015 | 6.8958 | 5.9895 | 5.452 | 0
WB | W | -60 | -30 |  | 0.99899 |  |  | 5.3387 | 7.7473 | 9.3675 | 10.2535 | 9.8247 | 9.588 | 0
WMTS 22kV
LS | S | -30 | -20 |  | 0.87096 |  |  | 4.2296 | 1.8883 | 1.6595 | 1.1703 | 0.9181 | 0.61033 | 0
LS | W | -30 | -20 |  | 0.95411 |  |  | 6.7245 | 1.0161 | 0 | -1.2945 | -2.153 | -3.0479 | 0
TSTS 66kV
L | S | -60 | -30 |  | 0.71943 |  |  | 4.8285 | 8.4041 | 7.2614 | 5.5754 | -3.8741 | -6.5086 | 0
L | W | -60 | -30 |  | 0.97893 |  |  | 7.7057 | 10.1903 | 9.674 | 8.118 | 6.0332 | 4.7953 | 0
Q | S | -60 | -30 |  | 0.76527 |  |  | 4.2648 | 7.2862 | 6.9144 | 6.532 | 5.0741 | 3.8424 | 0
Q | W | -60 | -30 |  | 0.98768 |  |  | 7.1143 | 8.212 | 8.74 | 9.0781 | 8.3162 | 7.817 | 0
SVTS 66kV
RD | S | -60 | -30 |  | 0.8013 |  |  | 3.0573 | 4.3618 | 3.5145 | 2.4915 | 1.0847 | -0.41183 | 0
RD | W | -60 | -30 |  | 0.98025 |  |  | 5.8149 | 5.5619 | 5.5109 | 4.8696 | 3.6284 | 2.8028 | 0

## Sub-t lines minimum demand
Subtransmission line Minimum Demand |  | Line Export Rating (MVA) | Hours 95% of Minimum Demand | Power Factor at Minimum Demand | Generation Capacity <=1MW (MW) | Generation Capacity >1MW (MW) | Historical Minimum Demand Worst case N-1 Scenario (MVA) | 50% PoE Forecast Minimum Demand Worst case N-1 Scenario (MVA) |  |  |  |  | MW Above N-1 Export Rating (2023) | Energy at Risk (MWh) (N-1 50% PoE) |  |  |  |  | Hours at Risk (N-1 50% PoE)
[7 empty] | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2023 | 2024 | 2025 | 2026 | 2027
BTS 22kV
BTS-BK185 | S | 10.5 |  | 0.66667 |  |  | 1.8 | 1.9 | 1.9 | 1.8 | 1.7 | 1.5 | 0
| W | 10.5 |  | 0.8 |  |  | 2.5 | 2.4 | 2.6 | 2.8 | 2.7 | 2.6 | 0
BTS-BK187 | S | 10.3 |  | 0.10526 |  |  | 3.8 | 3.8 | 3.2 | 3.3 | 3.2 | 2.6 | 0
| W | 10.3 |  | 0.31579 |  |  | 3.8 | 4.1 | 4.2 | 4.3 | 4.2 | 3.7 | 0
BTS-BK194 | S | 10.3 |  | 0.39474 |  |  | 3.8 | 3.8 | 3.2 | 3.3 | 3.2 | 2.5 | 0
| W | 10.3 |  | 0.57895 |  |  | 3.8 | 4.1 | 4.3 | 4.3 | 4.3 | 3.7 | 0
BTS-C186 | S | 9.9 |  | 1 |  |  | 1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0
| W | 11.2 |  | 1 |  |  | 1.1 | 0 | 0.1 | 0.1 | 0 | 0 | 0
BTS-C191 | S | 9.9 |  | 1 |  |  | 1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0
| W | 11.2 |  | 1 |  |  | 1.1 | 0 | 0.1 | 0.1 | 0 | 0 | 0
BTS-C196 | S | 9.9 |  | 1 |  |  | 1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0
| W | 11.2 |  | 1 |  |  | 1.1 | 0 | 0.1 | 0.1 | 0 | 0 | 0
BTS-F179 | S | 12 |  | 0.45455 |  |  | 3.3 | 3.4 | 3.3 | 3.2 | 3.2 | 3.2 | 0
| W | 12.6 |  | 0.48571 |  |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 0
BTS-F182 | S | 12 |  | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| W | 12.6 |  | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
BTS-F189 | S | 14.1 |  | 0.1875 |  |  | 3.2 | 3.2 | 3.2 | 3.1 | 3.1 | 3.1 | 0
| W | 14.8 |  | 0.24242 |  |  | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.4 | 0
BTS 66kV
BTS-BQ1 | S | 159.9 |  | 0.98 |  |  | 15 | 18.3 | 23.8 | 26 | 25.9 | 25.9 | 0
| W | 170.6 |  | 0.9875 |  |  | 16 | 22.5 | 25.4 | 26.2 | 26 | 26 | 0
BTS-BQ3 | S | 139.7 |  | 0.97163 |  |  | 14.1 | 17.3 | 22.5 | 24.6 | 24.4 | 24.5 | 0
| W | 149.2 |  | 0.98013 |  |  | 15.1 | 21.2 | 24 | 24.7 | 24.6 | 24.6 | 0
BTS-VM1 | S | 159.9 |  | 0.96032 |  |  | 12.6 | 15.7 | 21.3 | 23.2 | 23 | 23.1 | 0
| W | 170.6 |  | 0.97826 |  |  | 13.8 | 20.1 | 22.9 | 23.5 | 23.3 | 23.3 | 0
BQ-WP2 | S | 84 |  | 0.97647 |  |  | 8.5 | 8.5 | 8.5 | 8.5 | 8.4 | 8.5 | 0
| W | 91.5 |  | 0.97647 |  |  | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 0
BQ-WP3 | S | 84 |  | 0.97647 |  |  | 8.5 | 8.5 | 8.5 | 8.5 | 8.4 | 8.5 | 0
| W | 91.5 |  | 0.97647 |  |  | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 0
BTS-WP | S | 125.7 |  | 0.97902 |  |  | 14.3 | 17 | 21.6 | 23.4 | 23.2 | 23.3 | 0
| W | 137.2 |  | 0.99338 |  |  | 15.1 | 20.5 | 22.9 | 23.5 | 23.4 | 23.3 | 0
VM-BQ1 | S | 162.3 |  | 1 |  |  | 5.1 | 7.9 | 15.3 | 16.8 | 16.5 | 16.3 | 0
| W | 173.8 |  | 0.98684 |  |  | 7.6 | 14.6 | 17.5 | 17.5 | 17.2 | 16.9 | 0
VM-BQ3 | S | 125.7 |  | 1 |  |  | 5.1 | 7.9 | 15.3 | 16.8 | 16.5 | 16.3 | 0
| W | 128 |  | 0.98684 |  |  | 7.6 | 14.6 | 17.5 | 17.5 | 17.2 | 16.9 | 0
WP-MP1 | S | 78.3 |  | 0.92135 |  |  | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 9 | 0
| W | 84.6 |  | 0.93258 |  |  | 8.9 | 8.9 | 8.9 | 9 | 9 | 8.9 | 0
WP-MP2 | S | 80 |  | 0.91111 |  |  | 9 | 9 | 9 | 9 | 9 | 9.1 | 0
| W | 85.7 |  | 0.92222 |  |  | 9 | 9 | 9 | 9.1 | 9 | 9 | 0
WP-MP3 | S | 83.9 |  | 0.92135 |  |  | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 9 | 0
| W | 91.5 |  | 0.93258 |  |  | 8.9 | 8.9 | 8.9 | 9 | 8.9 | 8.9 | 0
VM-WA1 | S | 37.7 |  | 0.65 |  |  | 2 | 2.2 | 2.5 | 2.6 | 2.6 | 2.6 | 0
| W | 40 |  | 0.88889 |  |  | 2.7 | 3.3 | 3.4 | 3.4 | 3.4 | 3.4 | 0
VM-WA2 | S | 37.7 |  | 0.65 |  |  | 2 | 2.2 | 2.6 | 2.6 | 2.6 | 2.6 | 0
| W | 40 |  | 0.85714 |  |  | 2.8 | 3.3 | 3.4 | 3.5 | 3.5 | 3.5 | 0
VM-WA3 | S | 37.7 |  | 0.92857 |  |  | 1.4 | 1.8 | 2.3 | 2.4 | 2.4 | 2.4 | 0
| W | 40 |  | 0.96154 |  |  | 2.6 | 3.2 | 3.3 | 3.4 | 3.4 | 3.4 | 0
FBTS 66kV
FBTS-AP | S | 101.7 |  | 0.97059 |  |  | 17 | 18.2 | 20.9 | 21.5 | 21.3 | 20.7 | 0
| W | 109.7 |  | 0.97814 |  |  | 18.3 | 20.6 | 22.2 | 22.3 | 21.8 | 22 | 0
FBTS-MG | S | 100.6 |  | 0.97059 |  |  | 17 | 18.2 | 20.9 | 21.5 | 21.2 | 20.6 | 0
| W | 115.5 |  | 0.97283 |  |  | 18.4 | 20.7 | 22.3 | 22.3 | 21.8 | 22 | 0
MG-AP | S | 91.5 |  | 0.9292 |  |  | 11.3 | 11.8 | 13.5 | 13.9 | 14.1 | 14.1 | 0
| W | 91.5 |  | 0.9292 |  |  | 11.3 | 12.5 | 13.7 | 14 | 14.1 | 14.4 | 0
FBTS-E | S | 66.3 |  | 1 |  |  | 2 | 3.2 | 5.3 | 6.3 | 6.1 | 5.7 | 0
| W | 86.3 |  | 1 |  |  | 4.3 | 5.8 | 8.2 | 8.4 | 8.1 | 7.9 | 0
FBTS-PM | S | 66.3 |  | 1 |  |  | 2.4 | 3.7 | 5.9 | 7 | 6.8 | 6.4 | 0
| W | 86.3 |  | 1 |  |  | 4.6 | 6.2 | 8.6 | 8.8 | 8.5 | 8.3 | 0
E-PM | S | 74.3 |  | 1 |  |  | 2.4 | 3.7 | 5.9 | 7 | 6.8 | 6.4 | 0
| W | 91.5 |  | 1 |  |  | 4.6 | 6.2 | 8.6 | 8.8 | 8.5 | 8.3 | 0
FBTS-FB | S | 88 |  | 0.70758 |  |  | 27.7 | 29.3 | 37.3 | 38.1 | 38.1 | 38 | 0
| W | 112 |  | 0.7033 |  |  | 27.3 | 32.7 | 36.5 | 36.6 | 36.6 | 36.6 | 0
FBTS-WG | S | 88 |  | 0.70251 |  |  | 27.9 | 29.5 | 37.9 | 38.5 | 38.4 | 38.6 | 0
| W | 112 |  | 0.69818 |  |  | 27.5 | 33.2 | 36.8 | 36.9 | 37.1 | 37.1 | 0
FB-WG | S | 89.7 |  | 0.5125 |  |  | 16 | 17.4 | 25 | 25.5 | 25.5 | 25.7 | 0
| W | 94.3 |  | 0.49359 |  |  | 15.6 | 20.7 | 24.1 | 24.1 | 24.3 | 24.3 | 0
FBTS-SB | S | 117.7 |  | 0.96377 |  |  | 13.8 | 14.2 | 15.6 | 16.7 | 16.8 | 16.9 | 0
| W | 130.3 |  | 0.96324 |  |  | 13.6 | 14.4 | 16.2 | 16.4 | 16.5 | 16.6 | 0
FBTS-SO | S | 109.2 |  | 0.96377 |  |  | 13.8 | 14.2 | 15.6 | 16.7 | 16.8 | 16.9 | 0
| W | 125.7 |  | 0.96324 |  |  | 13.6 | 14.4 | 16.2 | 16.4 | 16.5 | 16.6 | 0
SB-SO | S | 109.7 |  | 0.90909 |  |  | 8.8 | 8.8 | 8.8 | 8.9 | 8.9 | 8.8 | 0
| W | 121.7 |  | 0.90909 |  |  | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 0
DLF 22kV
DLF64-TP278 | S | 12.6 |  | 0.8 |  |  | 2 | 2 | 2 | 2 | 2 | 1.9 | 0
| W | 13.1 |  | 0.72222 |  |  | 1.8 | 1.8 | 1.7 | 1.7 | 1.7 | 1.6 | 0
DLF5-TP53 | S | 12.6 |  | 0.25 |  |  | 2 | 2 | 2 | 2 | 2.2 | 2.2 | 0
| W | 13.1 |  | 0.72222 |  |  | 1.8 | 1.8 | 2.1 | 1.8 | 1.8 | 1.7 | 0
RTS 22kV
RTS-R134 | S | 19.1 |  | 1 |  |  | 2 | 3.6 | 5.9 | 7.2 | 7.2 | 7 | 0
| W | 20.7 |  | 1 |  |  | 2.8 | 4.7 | 6.9 | 7.3 | 7.2 | 7.1 | 0
RTS-R135 | S | 21.5 |  | 1 |  |  | 3.4 | 6.2 | 10 | 12.3 | 12.2 | 12 | 0
| W | 24.7 |  | 0.97917 |  |  | 4.8 | 8 | 11.8 | 12.3 | 12.2 | 12.2 | 0
RTS-R136 | S | 21.5 |  | 0.97059 |  |  | 3.4 | 6.1 | 9.9 | 12.2 | 12.1 | 11.9 | 0
| W | 24.7 |  | 0.97917 |  |  | 4.8 | 7.9 | 11.7 | 12.3 | 12.1 | 12.1 | 0
RTS 66kV
RTS-AR | S | 94.3 |  | 0.96748 |  |  | 12.3 | 12.5 | 13.7 | 15.1 | 15 | 14.8 | 0
| W | 123.5 |  | 0.97403 |  |  | 15.4 | 16.4 | 18.1 | 18.5 | 18.3 | 18.4 | 0
RTS-TK | S | 116.6 |  | 0.88462 |  |  | 7.8 | 9.5 | 10.3 | 13.1 | 14.8 | 16 | 0
| W | 122.3 |  | 0.91919 |  |  | 9.9 | 11 | 12.9 | 15.3 | 16.9 | 17.7 | 0
RTS-TK/BC | S | 135.5 |  | 0.90667 |  |  | 15 | 17.6 | 19.2 | 22.7 | 24.3 | 25.3 | 0
| W | 137.2 |  | 0.93264 |  |  | 19.3 | 21.6 | 24.6 | 27.1 | 28.5 | 29.3 | 0
BC-AR | S | 84.6 |  | 1 |  |  | 7.4 | 7.5 | 8.7 | 9.4 | 9.4 | 9.5 | 0
| W | 91.4 |  | 1 |  |  | 9.3 | 10.1 | 11.3 | 11.6 | 11.6 | 11.8 | 0
TK-BC | S | 91.5 |  | 0.96748 |  |  | 12.3 | 12.5 | 13.7 | 15.1 | 15 | 14.7 | 0
| W | 91.5 |  | 0.97403 |  |  | 15.4 | 16.4 | 18.1 | 18.5 | 18.3 | 18.4 | 0
RTS-CL | S | 135.5 |  | 1 |  |  | 14.1 | 15.3 | 16.4 | 17.3 | 17.1 | 16.5 | 0
| W | 142.3 |  | 1 |  |  | 17.1 | 18.3 | 19.3 | 19.5 | 19.1 | 19 | 0
K-CL | S | 91.4 |  | 1 |  |  | 7.4 | 8.6 | 9.7 | 10.6 | 10.4 | 9.9 | 0
| W | 91.4 |  | 0.99038 |  |  | 10.4 | 11.6 | 12.6 | 12.8 | 12.4 | 12.3 | 0
RTS-CW | S | 135.5 |  | 1 |  |  | 11.7 | 14.6 | 16.2 | 23.3 | 23.2 | 22.6 | 0
| W | 142.3 |  | 0.99315 |  |  | 14.6 | 16.4 | 22.7 | 24.6 | 24 | 23.5 | 0
RTS-NR | S | 135.5 |  | 0.99083 |  |  | 10.9 | 14.1 | 16.4 | 23.5 | 23.5 | 22.8 | 0
| W | 137.2 |  | 0.97857 |  |  | 14 | 16.4 | 23 | 24.9 | 24.3 | 23.8 | 0
B-CW | S | 85.7 |  | 0.93548 |  |  | 6.2 | 9.1 | 10.7 | 17.7 | 17.6 | 16.9 | 0
| W | 91.4 |  | 0.95402 |  |  | 8.7 | 10.6 | 16.8 | 18.7 | 18.1 | 17.6 | 0
B-NR | S | 85.7 |  | 0.99153 |  |  | 11.8 | 14.8 | 16 | 21.3 | 21.6 | 21.2 | 0
| W | 91.4 |  | 0.98639 |  |  | 14.7 | 16.6 | 21 | 22.7 | 22.5 | 22.3 | 0
RTS-SK | S | 102.9 |  | 0.93827 |  |  | 16.2 | 16.6 | 16.8 | 17 | 17 | 16.7 | 0
| W | 108 |  | 0.93567 |  |  | 17.1 | 17.4 | 17.8 | 17.9 | 18 | 18.1 | 0
RTS-FR1 | S | 82.3 |  | 0.93846 |  |  | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0
| W | 87.4 |  | 0.93846 |  |  | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0
RTS-FR2 | S | 82.3 |  | 0.93846 |  |  | 6.5 | 6.6 | 6.5 | 6.5 | 6.5 | 6.5 | 0
| W | 87.4 |  | 0.92424 |  |  | 6.6 | 6.5 | 6.5 | 6.6 | 6.5 | 6.5 | 0
RTS-FR3 | S | 82.3 |  | 0.93846 |  |  | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0
| W | 87.4 |  | 0.93846 |  |  | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0
FR-WP1 | S | 78.3 |  | 1 |  |  | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 0
| W | 84.6 |  | 1 |  |  | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 0
FR-WP2 | S | 80 |  | 1 |  |  | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 0
| W | 85.7 |  | 1 |  |  | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 0
FR-WP3 | S | 81.7 |  | 1 |  |  | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 0
| W | 88 |  | 0.95455 |  |  | 2.2 | 2.1 | 2.2 | 2.1 | 2.1 | 2.1 | 0
SVTS 66kV
SVTS-RD | S | 116.6 |  | 0.99301 |  |  | 14.3 | 12.8 | 10.2 | 6.9 | 2.4 | 3.7 | 0
| W | 122.3 |  | 0.99479 |  |  | 19.2 | 18.3 | 17.1 | 14.7 | 10.6 | 7.1 | 0
TSTS 66kV
TSTS-L | S | 106.9 |  | 0.84127 |  |  | 18.9 | 19.4 | 17.2 | 14.3 | 10 | 9.5 | 0
| W | 108.6 |  | 0.86607 |  |  | 22.4 | 22.6 | 22.5 | 20.6 | 17 | 14.5 | 0
HB-Q | S | 95.5 |  | 0.7351 |  |  | 15.1 | 15.1 | 13.6 | 11.5 | 8.1 | 8.5 | 0
| W | 108.6 |  | 0.78857 |  |  | 17.5 | 17.6 | 17.6 | 16.5 | 13.5 | 11.7 | 0
L-Q | S | 95.4 |  | 0.93805 |  |  | 11.3 | 11.8 | 10.6 | 9.5 | 7.2 | 6.3 | 0
| W | 108.6 |  | 0.94615 |  |  | 13 | 13.2 | 13.6 | 13.4 | 11.9 | 10.8 | 0
WMTS 22kV
WMTS-DA213 | S | 23.8 |  | 0.92727 |  |  | 5.5 | 8 | 8.5 | 9.1 | 8.5 | 7.8 | 0
| W | 29.1 |  | 0.94737 |  |  | 11.4 | 13.3 | 13.9 | 14 | 13.2 | 12.7 | 0
WMTS-DA222 | S | 23.8 |  | 0.92727 |  |  | 5.5 | 8 | 8.5 | 9.1 | 8.5 | 7.8 | 0
| W | 29.1 |  | 0.93043 |  |  | 11.5 | 13.4 | 14 | 14 | 13.3 | 12.7 | 0
WMTS-LS214 | S | 19.1 |  | 0.91176 |  |  | 3.4 | 3.3 | 3.3 | 3.2 | 2.9 | 2.6 | 0
| W | 19.1 |  | 0.92593 |  |  | 5.4 | 4.3 | 4.1 | 3.8 | 3.8 | 4.1 | 0
WMTS-LS226 | S | 19.1 |  | 0.90323 |  |  | 3.1 | 2.6 | 2.6 | 2.5 | 2.3 | 2.3 | 0
| W | 19.1 |  | 0.93478 |  |  | 4.6 | 3.5 | 4 | 4.3 | 4.5 | 4.8 | 0
WMTS 66kV
WMTS-JA1 | S | 145.2 |  | 0.98571 |  |  | 7 | 7.1 | 7.2 | 8.6 | 8.5 | 8.1 | 0
| W | 153.2 |  | 0.98837 |  |  | 8.6 | 8.8 | 9.8 | 10.3 | 9.8 | 9.5 | 0
WMTS-JA3 | S | 114.9 |  | 0.98485 |  |  | 6.6 | 6.7 | 6.7 | 8.1 | 8 | 7.6 | 0
| W | 121.2 |  | 0.98765 |  |  | 8.1 | 8.2 | 9.1 | 9.6 | 9.2 | 8.9 | 0
WMTS-VM1 | S | 130.3 |  | 0.88636 |  |  | 4.4 | 4.5 | 4.6 | 5.9 | 5.8 | 5.4 | 0
| W | 164.6 |  | 0.89831 |  |  | 5.9 | 6 | 6.9 | 7.4 | 7 | 6.7 | 0
WMTS-VM2 | S | 144 |  | 0.83333 |  |  | 3.6 | 3.7 | 3.7 | 4.7 | 4.6 | 4.3 | 0
| W | 155.5 |  | 0.87234 |  |  | 4.7 | 4.8 | 5.5 | 5.8 | 5.5 | 5.3 | 0
WMTS-VM3 | S | 120 |  | 0.90385 |  |  | 5.2 | 5.3 | 5.4 | 7 | 6.8 | 6.3 | 0
| W | 129.7 |  | 0.91429 |  |  | 7 | 7.1 | 8.2 | 8.7 | 8.2 | 7.9 | 0
VM-LQ1 | S | 76.6 |  | 0.55102 |  |  | 4.9 | 5.1 | 5.2 | 7.3 | 7.1 | 6.4 | 0
| W | 86.9 |  | 0.72603 |  |  | 7.3 | 7.5 | 8.9 | 9.7 | 9 | 8.6 | 0
VM-LQ3 | S | 76.6 |  | 0.56 |  |  | 5 | 5.1 | 5.2 | 7.3 | 7.2 | 6.5 | 0
| W | 86.9 |  | 0.72603 |  |  | 7.3 | 7.6 | 9 | 9.7 | 9.1 | 8.6 | 0
VM-JA | S | 91.5 |  | 0.98824 |  |  | 8.5 | 8.6 | 8.7 | 9.6 | 9.5 | 9.3 | 0
| W | 98.3 |  | 0.98958 |  |  | 9.6 | 9.6 | 10.3 | 10.6 | 10.3 | 10.2 | 0
JA-LQ2 | S | 76.6 |  | 0.54 |  |  | 5 | 5.1 | 5.2 | 7.3 | 7.1 | 6.5 | 0
| W | 86.9 |  | 0.71233 |  |  | 7.3 | 7.5 | 8.9 | 9.7 | 9 | 8.6 | 0
JA-WP | S | 47.4 |  | 0 |  |  | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0
| W | 57.2 |  | 0 |  |  | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0
WMTS-NC | S | 54.9 |  | 0.93827 |  |  | 8.1 | 7.9 | 6.7 | 5.8 | 3.9 | 4.8 | 0
| W | 70.3 |  | 0.97321 |  |  | 11.2 | 10.2 | 9.9 | 8.7 | 7.3 | 6.2 | 0
WMTS-WB | S | 54.9 |  | 0.93827 |  |  | 8.1 | 8 | 6.7 | 6.3 | 6.3 | 6.3 | 0
| W | 70.3 |  | 0.97345 |  |  | 11.3 | 10.3 | 10 | 8.8 | 7.2 | 6.2 | 0
WB-NC | S | 74.3 |  | 0.82812 |  |  | 6.4 | 6.2 | 6.3 | 6.3 | 6.3 | 6.3 | 0
| W | 97.2 |  | 0.84127 |  |  | 6.3 | 6.3 | 6.3 | 6.3 | 6.4 | 6.4 | 0

## Zone substations maximum demand
Zone Substation Maximum Demand |  | On-load Capacity - N Import Rating (MVA) | Hot or Cold Spare Capacity - N Import Rating (MVA) | Total Capacity - N Import Rating (MVA) | Cyclic N-1 Import Rating (MVA) | Hours 95% of Maximum Demand | Station Power Factor at Maximum Demand | Load Transfer Capacity (MVA) | Generation Capacity <1MW (MW) | Generation Capacity >1MW (1MW) | Actual Maximum Demand (MVA) | 50% PoE Forecast Maximum Demand (MVA) |  |  |  |  | % Load Above N-1 Rating (2023) | Energy at Risk (MWh) (N-1 50% PoE) |  |  |  |  | Hours at Risk (N-1 50% PoE)
[11 empty] | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2023 | 2024 | 2025 | 2026 | 2027
BTS 22kV
BK | S | 23 | 10 | 33 | 27.2 |  | 0.98 |  |  |  | 13.805 | 14.0284 | 14.7423 | 15.7817 | 16.0366 | 16.4229
BK | W | 23 | 10 | 33 | 28.6 |  | 0.98 |  |  |  | 14.837 | 14.9756 | 16.0464 | 16.5151 | 16.7093 | 17.1564
C | S | 22.5 |  | 22.5 | 17 |  | 0.99 |  |  |  | 11.3161 | 1.5403 | 1.5014 | 1.601 | 1.601 | 1.2104
C | W | 22.5 |  | 22.5 | 17 |  | 0.99 |  |  |  | 11.3835 | 0.88888 | 0.82861 | 0.81908 | 0.81908 | 0.76844
F | S | 20 |  | 20 | 13 | 177 | 0.99 |  |  |  | 13.1505 | 13.9388 | 14.3628 | 14.9094 | 15.3135 | 15.9519 | 7.221% | 0.86 | 3.17 | 10.32 | 17.36 | 34.38 | 3.5 | 8 | 17 | 26.5 | 39
F | W | 20 |  | 20 | 15.3 |  | 0.99 |  |  |  | 15.2269 | 15.8403 | 16.366 | 16.8211 | 17.2563 | 17.9854
BTS 66kV
BQ | S | 55 | 55 | 110 | 64.9 | 1067 | 1 |  |  | 12.4 | 58.0737 | 79.6174 | 82.6867 | 86.1971 | 86.2676 | 85.5651 | 22.68% | 651.33 | 1160.03 | 2260.9399 | 2480.1699 | 2531.25 | 133 | 201 | 372 | 409 | 422
BQ | W | 55 | 55 | 110 | 72.3 |  | 1 |  |  |  | 44.8381 | 66.9987 | 70.7299 | 72.6657 | 72.7263 | 73.418
VM | S | 57 | 27 | 84 | 62.8 |  | 0.98 |  |  |  | 36.4403 | 45.3419 | 57.3038 | 59.0738 | 58.4675 | 57.6725
VM | W | 57 | 27 | 84 | 69.2 |  | 0.98 |  |  |  | 33.1592 | 54.0893 | 59.9197 | 60.2082 | 59.5802 | 59.2191
WA | S | 57 | 27 | 84 | 67.1 |  | 0.98 |  |  |  | 33.1529 | 41.3119 | 43.0181 | 43.8144 | 43.9261 | 43.732
WA | W | 57 | 27 | 84 | 73.7 |  | 0.98 |  |  |  | 28.1756 | 35.2833 | 36.458 | 36.9993 | 37.0208 | 36.9287
MP | S | 165 |  | 165 | 124 |  | 0.97 |  |  | 1.15 | 77.0278 | 99.1342 | 105.2476 | 107.9239 | 108.7319 | 108.7416
MP | W | 165 |  | 165 | 123.4 |  | 0.97 |  |  |  | 55.0887 | 79.6674 | 83.5682 | 85.2356 | 85.7615 | 85.6985
DLF 22kV
TP | S
TP | W
FBTS 66kV
AP | S | 60 | 27 | 87 | 70 |  | 0.99 |  |  |  | 43.8187 | 49.9265 | 52.7738 | 53.6549 | 53.7469 | 53.7963
AP | W | 60 | 27 | 87 | 71.3 |  | 0.99 |  |  |  | 37.0763 | 43.4232 | 45.1049 | 45.815 | 46.2605 | 47.1812
E | S | 13.5 |  | 13.5 | 0 |  | 0.87 |  |  |  | 1.4449 | 3.2723 | 3.3441 | 3.3888 | 3.3752 | 3.3529
E | W | 13.5 |  | 13.5 | 0 |  | 0.87 |  |  |  | 1.7893 | 3.178 | 3.2363 | 3.2587 | 3.2499 | 3.2723
FB | S | 90 |  | 90 | 63.7 |  | 0.78 |  |  |  | 26.7557 | 36.1368 | 38.999 | 39.4864 | 39.503 | 39.3866
FB | W | 90 |  | 90 | 62 |  | 0.78 |  |  |  | 22.0245 | 33.99 | 36.2739 | 36.5182 | 36.4716 | 36.5647
MG | S | 60 | 27 | 87 | 64.3 |  | 0.94 |  |  |  | 30.6953 | 37.476 | 39.4782 | 40.3402 | 39.9156 | 39.4338
MG | W | 60 | 27 | 87 | 75 |  | 0.94 |  |  |  | 23.1555 | 29.656 | 30.9279 | 30.9184 | 30.4058 | 30.4501
PM | S | 27 |  | 27 | 17.4 |  | 0.96 |  |  |  | 13.4746 | 18.051 | 21.1242 | 22.112 | 21.7889 | 21.3679
PM | W | 27 |  | 27 | 19.7 |  | 0.96 |  |  |  | 12.8703 | 16.7392 | 19.3255 | 19.3476 | 19.0256 | 18.7921
SB | S | 110 |  | 110 | 59.7 |  | 0.98 |  |  | 6 | 40.4362 | 51.0754 | 53.5555 | 57.3041 | 58.9262 | 58.5236
SB | W | 110 |  | 110 | 63.6 |  | 0.98 |  |  |  | 28.3865 | 40.9326 | 43.7615 | 46.251 | 46.8933 | 46.4181
SO | S | 60 | 27 | 87 | 63.7 |  | 0.96 |  |  |  | 31.7404 | 40.9164 | 44.2979 | 45.995 | 46.4623 | 46.6108
SO | W | 60 | 27 | 87 | 71.7 |  | 0.96 |  |  |  | 23.2327 | 33.9583 | 36.9694 | 37.8637 | 38.1673 | 38.3376
WG | S | 81 |  | 81 | 67.6 |  | 0.96 |  |  |  | 46.9067 | 55.9106 | 61.3736 | 73.9715 | 74.8014 | 75.0866
WG | W | 81 |  | 81 | 71.9 |  | 0.96 |  |  |  | 37.2698 | 45.946 | 57.927 | 61.905 | 62.3732 | 62.6263
RTS 66kV
AR | S | 60 |  | 60 | 32.9 |  | 0.99 |  |  |  | 32.6843 | 34.379 | 34.7319 | 35.3408 | 34.7518 | 34.2607
AR | W | 60 |  | 60 | 35.8 |  | 0.99 |  |  |  | 27.5651 | 29.3012 | 30.1366 | 30.6668 | 30.6271 | 30.9617
B | S | 54 |  | 54 | 29 | 1707 | 0.97 |  |  | 6.2 | 30.2377 | 36.0087 | 38.7754 | 43.1597 | 42.859 | 42.1339 | 24.17% | 351.39 | 1103.98 | 11997.3496 | 12670.2998 | 10715.0996 | 168.5 | 454.5 | 3843 | 3977.5 | 3661
B | W | 54 |  | 54 | 32.2 |  | 0.97 |  |  | 6.2 | 24.0591 | 30.3186 | 35.3444 | 37.1483 | 36.61 | 36.256
BC | S | 57 | 30 | 87 | 71.6 |  | 0.98 |  |  |  | 41.2053 | 45.9582 | 48.1679 | 48.8148 | 48.5886 | 48.6319
BC | W | 57 | 30 | 87 | 70.6 |  | 0.98 |  |  |  | 39.4775 | 44.4713 | 46.454 | 46.8738 | 46.9935 | 47.6826
CL | S | 60 | 27 | 87 | 71.7 |  | 0.98 |  |  |  | 47.7201 | 54.2717 | 55.7147 | 55.9762 | 54.6807 | 53.1436
CL | W | 60 | 27 | 87 | 70.7 |  | 0.98 |  |  |  | 33.7395 | 40.5112 | 42.0887 | 42.3612 | 42.0789 | 42.3612
CW | S | 54 |  | 54 | 34.4 |  | 0 |  |  |  | 23.889 | 0 | 0 | 0 | 0 | 0
CW | W | 54 |  | 54 | 38.2 |  | 0 |  |  |  | 22.4629 | 0 | 0 | 0 | 0 | 0
FR | S | 90 |  | 90 | 61.3 |  | 0.97 |  |  |  | 39.5687 | 48.6076 | 50.5879 | 52.8401 | 53.2988 | 53.248
FR | W | 90 |  | 90 | 72.1 |  | 0.97 |  |  |  | 29.5088 | 42.1742 | 44.1956 | 45.5715 | 45.7706 | 45.6759
NR | S | 83 |  | 83 | 65.2 |  | 0.99 |  |  | 2.6 | 49.9949 | 56.3283 | 59.4737 | 61.1623 | 60.5046 | 59.8173
NR | W | 83 |  | 83 | 71.7 |  | 0.99 |  |  | 2.6 | 40.946 | 44.426 | 47.7325 | 48.2275 | 48.0153 | 48.2883
SK | S | 60 | 27 | 87 | 63.2 |  | 0.97 |  |  | 6.2 | 43.6597 | 48.5812 | 49.3701 | 49.5821 | 48.9147 | 48.0679
SK | W | 60 | 27 | 87 | 72.9 |  | 0.97 |  |  | 6.2 | 32.1794 | 38.1187 | 38.7225 | 38.8852 | 38.7323 | 39.0069
TK | S | 60 | 27 | 87 | 52.5 |  | 0.97 |  |  |  | 34.3647 | 50.2226 | 51.817 | 54.8321 | 56.153 | 57.3625
TK | W | 60 | 27 | 87 | 54.7 |  | 0.97 |  |  |  | 33.4426 | 44.3435 | 47.2071 | 49.7082 | 51.5938 | 52.8656
WP | S | 110 |  | 110 | 71.6525 |  | 0.97 |  |  |  | 26.1974 | 28.4422 | 30.3075 | 30.6133 | 30.3172 | 29.8126
WP | W | 110 |  | 110 | 71.6525 |  | 0.97 |  |  |  | 17.955 | 21.7528 | 22.7854 | 22.7224 | 22.3547 | 21.9653
RTS 22kV
R | S | 40 |  | 40 | 30.1 | 2227 | 0.99 |  |  |  | 23.953 | 31.8265 | 39.6715 | 42.3274 | 41.9254 | 41.3412 | 5.736% | 11.1 | 4500.9902 | 20344.9199 | 19820.5293 | 18665.7891 | 18.5 | 2095.5 | 4379 | 4378 | 4369.5
R | W | 40 |  | 40 | 36 |  | 0.99 |  |  |  | 20.5597 | 31.0723 | 36.7042 | 37.3083 | 36.8555 | 36.5441
WMTS 66kV
JA | S | 165 |  | 165 | 127.8 |  | 0.98 |  |  |  | 93.0387 | 119.1287 | 138.9321 | 142.8632 | 141.3774 | 138.9537
JA | W | 165 |  | 165 | 127.4 |  | 0.98 |  |  |  | 72.6741 | 99.0537 | 111.8054 | 112.4711 | 110.5995 | 108.6346
LQ | S | 120 | 60 | 180 | 131.8 |  | 0.97 |  |  |  | 64.6125 | 91.4764 | 94.5682 | 100.9461 | 100.2452 | 98.3513
LQ | W | 120 | 60 | 180 | 142.2 |  | 0.97 |  |  |  | 55.1033 | 78.45 | 82.9067 | 86.236 | 84.8394 | 83.2583
NC | S | 60 |  | 60 | 31.9 |  | 0.99 |  |  |  | 29.0736 | 33.0033 | 34.0259 | 35.6141 | 36.1714 | 37.2138
NC | W | 60 |  | 60 | 40.2 |  | 0.99 |  |  |  | 30.3387 | 30.7871 | 32.1434 | 32.8323 | 33.2976 | 34.3399
DA | S | 40.5 |  | 40.5 | 29.2 |  | 0.96 |  |  | 2 | 19.8923 | 26.2524 | 27.4254 | 28.3856 | 28.034 | 27.5202
DA | W | 40.5 |  | 40.5 | 32.6 |  | 0.96 |  |  | 2 | 19.0307 | 25.6342 | 26.7977 | 27.0545 | 26.7056 | 26.5916
WB | S | 60 |  | 60 | 34.2 |  | 0.93 |  |  |  | 20.5567 | 37.1107 | 38.7043 | 41.0356 | 41.331 | 41.864 | 8.511% | 22179.0098 | 30083.9297 | 41019.4102 | 35006.8906 | 34116.75 | 5354 | 6930 | 7751.5 | 7414 | 7394.5
WB | W | 60 |  | 60 | 36.8 |  | 0.93 |  |  |  | 22.3114 | 37.1961 | 39.8319 | 40.7848 | 41.0225 | 41.9086
WMTS 22kV
LS | S | 30 |  | 30 | 24.2 |  | 0.99 |  |  |  | 15.3531
LS | W | 30 |  | 30 | 27 |  | 0.99 |  |  |  | 13.6917
TSTS 66kV
L | S | 60 |  | 60 | 32.1 | 40 | 0.99 |  |  |  | 39.7712 | 44.0657 | 44.5856 | 45.0708 | 45.0144 | 45.2667 | 37.28% | 400.05 | 384.29 | 371.59 | 310.75 | 336.86 | 116.5 | 103.5 | 95.5 | 76 | 76.5
L | W | 60 |  | 60 | 36.4 |  | 0.99 |  |  |  | 30.9748 | 31.2888 | 31.6796 | 31.9119 | 32.1923 | 32.9655
Q | S | 60 |  | 60 | 27.2 | 34 | 0.99 |  |  |  | 33.6259 | 38.2462 | 38.9434 | 39.9631 | 39.9942 | 40.3265 | 40.61% | 732.8 | 690.96 | 788.05 | 627.43 | 677.49 | 265.5 | 241 | 257 | 184.5 | 201
Q | W | 60 |  | 60 | 31.5 |  | 0.99 |  |  |  | 28.515 | 29.3403 | 30.3027 | 30.7159 | 30.9474 | 31.7112
SVTS 66kV
RD | S | 60 |  | 60 | 24.9 | 177 | 0.98 |  |  |  | 32.0665 | 37.7922 | 38.2707 | 38.6178 | 38.4962 | 38.6277 | 51.78% | 622.32 | 593.5 | 595.89 | 495.55 | 512.3 | 198 | 173.5 | 167.5 | 138.5 | 139.5
RD | W | 60 |  | 60 | 28.7 |  | 0.98 |  |  |  | 24.9882 | 25.868 | 26.1838 | 26.2544 | 26.2661 | 26.7035

## Sub-t lines maximum demand
Subtransmission line Maximum Demand |  | Line Import Rating (MVA) | Hours 95% of Maximum Demand | Power Factor at Maximum Demand | Load Transfer Capacity (MVA) | Generation Capacity (MW) | Historical Maximum Demand Worst case N-1 Scenario (MVA) | 50% PoE Forecast Maximum Demand Worst case N-1 Scenario (MVA) |  |  |  |  | % Load Above N-1 Import Rating (2023) | Energy at Risk (MWh) (N-1 50% PoE) |  |  |  |  | Hours at Risk (N-1 50% PoE)
[7 empty] | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2023 | 2024 | 2025 | 2026 | 2027
BTS 22kV
BTS-BK185 | S | 10.5 |  | 1 |  |  | 6.6 | 6.6 | 7 | 7.6 | 7.8 | 8
| W | 10.5 |  | 1 |  |  | 6.9 | 7.1 | 7.7 | 7.9 | 8 | 8.2
BTS-BK187 | S | 10.3 |  | 0.86905 |  |  | 8.4 | 8.4 | 8.7 | 9.6 | 9.8 | 10
| W | 10.3 |  | 0.89412 |  |  | 8.5 | 8.7 | 9.5 | 9.7 | 9.8 | 10.1
BTS-BK194 | S | 10.3 |  | 0.91026 |  |  | 7.8 | 7.9 | 8.3 | 8.6 | 8.7 | 8.9
| W | 10.3 |  | 0.89412 |  |  | 8.5 | 8.7 | 9 | 9.2 | 9.3 | 9.5
BTS-C186 | S | 9.9 |  | 0.98276 |  |  | 5.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6
| W | 11.2 |  | 0.96721 |  |  | 6.1 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4
BTS-C191 | S | 9.9 |  | 0.98276 |  |  | 5.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6
| W | 11.2 |  | 0.96721 |  |  | 6.1 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4
BTS-C196 | S | 9.9 |  | 0.98276 |  |  | 5.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6
| W | 11.2 |  | 0.96721 |  |  | 6.1 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4
BTS-F179 | S | 12 | 3 | 0.97872 |  |  | 14.1 | 14.6 | 14.9 | 15.6 | 16 | 16.7 | 21.67% | 159 | 223 | 335 | 437 | 688 | 195 | 245 | 319 | 379 | 513
| W | 12.6 | 3 | 0.97531 |  |  | 16.2 | 16.8 | 17.2 | 17.7 | 18.1 | 18.9 | 33.33%
BTS-F182 | S | 12 |  | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| W | 12.6 |  | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0
BTS-F189 | S | 14.1 | 3 | 0.97842 |  |  | 13.9 | 14.4 | 14.8 | 15.5 | 15.9 | 16.6 |  | 6 | 12 | 21 | 32 | 61 | 11 | 17 | 23 | 32 | 62
| W | 14.8 | 3 | 0.97484 |  |  | 15.9 | 16.5 | 17 | 17.5 | 18 | 18.8 | 11.49%
BTS 66kV
BTS-BQ1 | S | 159.9 |  | 0.99746 |  |  | 39.3 | 38.9 | 39.1 | 39.2 | 38.9 | 38.9
| W | 170.6 |  | 0.99744 |  |  | 39.1 | 39.3 | 39.3 | 39.1 | 39.1 | 39.1
BTS-BQ3 | S | 139.7 |  | 0.99746 |  |  | 39.3 | 38.9 | 39.1 | 39.2 | 38.9 | 38.9
| W | 149.2 |  | 0.99744 |  |  | 39.1 | 39.3 | 39.3 | 39.1 | 39.1 | 39.1
BTS-VM1 | S | 159.9 |  | 0.98079 |  |  | 78.1 | 90.6 | 97.3 | 100.4 | 99.8 | 99.2
| W | 170.6 |  | 0.98497 |  |  | 73.2 | 86.3 | 90.8 | 91.8 | 91.6 | 91.7
BQ-WP2 | S | 84 |  | 0.98095 |  |  | 73.5 | 85.5 | 91.8 | 94.8 | 94.4 | 93.6
| W | 91.5 |  | 0.98542 |  |  | 68.6 | 81.4 | 85.7 | 86.6 | 86.5 | 86.5
BQ-WP3 | S | 84 |  | 0.98054 |  |  | 66.8 | 77.9 | 84.5 | 87.2 | 86.8 | 86.1
| W | 91.5 |  | 0.9856 |  |  | 62.5 | 74.9 | 79.2 | 80 | 79.8 | 79.8
BTS-WP | S | 125.7 |  | 0.98372 |  |  | 73.7 | 83.8 | 89.2 | 91.8 | 91.4 | 90.8
| W | 137.2 |  | 0.98847 |  |  | 69.4 | 80.4 | 84.1 | 84.8 | 84.7 | 84.8
VM-BQ1 | S | 162.3 |  | 0.95979 |  |  | 37.3 | 44 | 51.2 | 52.7 | 52.4 | 52
| W | 173.8 |  | 0.96056 |  |  | 35.5 | 45.5 | 49.6 | 49.9 | 49.6 | 49.3
VM-BQ3 | S | 125.7 |  | 0.95979 |  |  | 37.3 | 44 | 51.2 | 52.7 | 52.4 | 52
| W | 128 |  | 0.96056 |  |  | 35.5 | 45.5 | 49.6 | 49.9 | 49.6 | 49.3
WP-MP1 | S | 78.3 |  | 0.89524 |  |  | 21 | 24.5 | 26.4 | 26.5 | 26.6 | 26.5
| W | 84.6 |  | 0.95732 |  |  | 16.4 | 19.1 | 21 | 21.2 | 21.2 | 21.1
WP-MP2 | S | 80 |  | 0.8972 |  |  | 21.4 | 25 | 26.9 | 27 | 27.1 | 27
| W | 85.7 |  | 0.95238 |  |  | 16.8 | 19.5 | 21.4 | 21.6 | 21.6 | 21.5
WP-MP3 | S | 83.9 |  | 0.99432 |  |  | 17.6 | 18.8 | 19.4 | 19.6 | 19.7 | 19.6
| W | 91.5 |  | 0.98089 |  |  | 15.7 | 16.6 | 16.7 | 16.9 | 16.9 | 16.8
VM-WA1 | S | 37.7 |  | 0.98228 |  |  | 39.5 | 39.5 | 39.8 | 39.9 | 39.5 | 39.5
| W | 40 |  | 0.98232 |  |  | 39.6 | 39.5 | 39.5 | 39.7 | 39.8 | 39.7
VM-WA2 | S | 37.7 |  | 0.9798 |  |  | 39.6 | 39.6 | 39.8 | 39.9 | 39.6 | 39.6
| W | 40 |  | 0.98237 |  |  | 39.7 | 39.6 | 39.6 | 39.8 | 39.8 | 39.7
VM-WA3 | S | 37.7 |  | 0.97975 |  |  | 39.5 | 39.4 | 39.7 | 39.8 | 39.5 | 39.5
| W | 40 |  | 0.98232 |  |  | 39.6 | 39.5 | 39.5 | 39.7 | 39.7 | 39.6
FBTS 66kV
FBTS-AP | S | 101.7 |  | 0.92915 |  |  | 86.1 | 90.9 | 96.7 | 98.7 | 98.3 | 97.7
| W | 109.7 |  | 0.93983 |  |  | 69.8 | 75.3 | 78.5 | 79.4 | 79.2 | 80.2
FBTS-MG | S | 100.6 |  | 0.92899 |  |  | 85.9 | 90.7 | 95.9 | 98.6 | 98.3 | 97.9
| W | 115.5 |  | 0.94134 |  |  | 69.9 | 75.1 | 78 | 79 | 78.9 | 79.9
MG-AP | S | 91.5 |  | 0.95152 |  |  | 49.5 | 51.7 | 54.7 | 56.1 | 56.2 | 56.3
| W | 91.5 |  | 0.95704 |  |  | 41.9 | 44.6 | 46.3 | 47.2 | 47.6 | 48.6
FBTS-E | S | 66.3 |  | 0.90404 |  |  | 19.8 | 22.3 | 26.1 | 27.3 | 26.9 | 26.3
| W | 86.3 |  | 0.92222 |  |  | 18 | 20.7 | 23.8 | 23.9 | 23.4 | 23.2
FBTS-PM | S | 66.3 |  | 0.92708 |  |  | 19.2 | 21.6 | 25 | 26.1 | 25.7 | 25.3
| W | 86.3 |  | 0.9375 |  |  | 17.6 | 20.1 | 23 | 23 | 22.6 | 22.4
E-PM | S | 74.3 |  | 0.91667 |  |  | 16.8 | 19 | 22.7 | 23.9 | 23.5 | 22.9
| W | 91.5 |  | 0.92715 |  |  | 15.1 | 17.5 | 20.5 | 20.6 | 20.2 | 19.9
FBTS-FB | S | 88 |  | 0.78209 |  |  | 100.5 | 106.7 | 110 | 110.7 | 110.7 | 110.4
| W | 112 |  | 0.7816 |  |  | 98.9 | 104.2 | 106.9 | 107.1 | 106.6 | 107.2
FBTS-WG | S | 88 |  | 0.77767 |  |  | 101.2 | 107 | 110.5 | 110.9 | 110.9 | 110.9
| W | 112 |  | 0.77744 |  |  | 99.3 | 104.5 | 107 | 107.5 | 107.5 | 107.5
FB-WG | S | 89.7 |  | 0.85692 |  |  | 62.9 | 63.3 | 63.2 | 63.4 | 63.4 | 63.2
| W | 94.3 |  | 0.85714 |  |  | 63 | 63.3 | 63.3 | 63.3 | 62.8 | 63.2
FBTS-SB | S | 117.7 |  | 0.89298 |  |  | 84.1 | 87.4 | 91.4 | 93.1 | 93.7 | 93.9
| W | 130.3 |  | 0.89777 |  |  | 76.3 | 79.4 | 82.5 | 83.7 | 84 | 84.2
FBTS-SO | S | 109.2 |  | 0.89298 |  |  | 84.1 | 87.4 | 91.4 | 93.2 | 93.7 | 93.9
| W | 125.7 |  | 0.89583 |  |  | 76.8 | 79.4 | 82.5 | 83.7 | 84 | 84.2
SB-SO | S | 109.7 |  | 0.88345 |  |  | 42.9 | 43 | 46.6 | 48.4 | 48.9 | 49.1
| W | 121.7 |  | 0.88372 |  |  | 43 | 43 | 42.9 | 43 | 43 | 42.9
DLF 22kV
DLF64-TP278 | S | 12.6 |  | 0.825 |  |  | 4 | 4 | 4 | 3.9 | 3.8 | 3.7
| W | 13.1 |  | 0.82353 |  |  | 3.4 | 3.4 | 3.4 | 3.4 | 3.3 | 3.2
DLF5-TP53 | S | 12.6 |  | 0.825 |  |  | 4 | 4 | 4 | 3.9 | 3.8 | 3.7
| W | 13.1 |  | 0.82353 |  |  | 3.4 | 3.4 | 3.4 | 3.4 | 3.3 | 3.2
RTS 22kV
RTS-R134 | S | 19.1 |  | 0.99115 |  |  | 11.3 | 13.4 | 16 | 17 | 16.9 | 16.7
| W | 20.7 |  | 0.99074 |  |  | 10.8 | 13.2 | 15 | 15.2 | 15.1 | 15
RTS-R135 | S | 21.5 |  | 0.98446 |  |  | 19.3 | 22.9 | 27.3 | 29 | 28.8 | 28.5
| W | 24.7 |  | 0.98378 |  |  | 18.5 | 22.4 | 25.6 | 25.9 | 25.7 | 25.5
RTS-R136 | S | 21.5 |  | 0.98438 |  |  | 19.2 | 22.7 | 27.1 | 28.8 | 28.6 | 28.3
| W | 24.7 |  | 0.98361 |  |  | 18.3 | 22.3 | 25.5 | 25.7 | 25.5 | 25.3
RTS 66kV
RTS-AR | S | 94.3 |  | 0.91727 |  |  | 83.4 | 83.4 | 86.6 | 87.9 | 87.2 | 86.9
| W | 123.5 |  | 0.92622 |  |  | 75.9 | 78.5 | 81.2 | 81.9 | 82 | 82.9
RTS-TK | S | 116.6 |  | 0.96219 |  |  | 52.9 | 54.9 | 56.9 | 59.8 | 61.3 | 62.8
| W | 122.3 |  | 0.96639 |  |  | 47.6 | 49.4 | 52.1 | 53.4 | 55.1 | 57
RTS-TK/BC | S | 135.5 |  | 0.94821 |  |  | 100.4 | 104.6 | 108.6 | 113 | 114 | 115.2
| W | 137.2 |  | 0.95082 |  |  | 91.5 | 95 | 100.2 | 103.3 | 105.2 | 107.6
BC-AR | S | 84.6 |  | 0.89552 |  |  | 46.9 | 46.9 | 49.2 | 49.8 | 49.7 | 49.8
| W | 91.4 |  | 0.9141 |  |  | 45.4 | 47.1 | 48.7 | 48.9 | 49 | 49.7
TK-BC | S | 91.5 |  | 0.94608 |  |  | 81.6 | 82.7 | 85.9 | 87.2 | 86.5 | 85.1
| W | 91.5 |  | 0.95089 |  |  | 73.3 | 75.8 | 78.8 | 79.5 | 79.6 | 80.4
RTS-CL | S | 135.5 |  | 0.93617 |  |  | 89.3 | 92.4 | 94.3 | 94.6 | 93.3 | 90.6
| W | 142.3 |  | 0.95405 |  |  | 74 | 75.8 | 77.7 | 77.9 | 77.6 | 78.6
K-CL | S | 91.4 |  | 0.93199 |  |  | 54.4 | 58 | 59.7 | 60 | 58.7 | 56.3
| W | 91.4 |  | 0.955 |  |  | 40 | 42.3 | 44.1 | 44.2 | 43.9 | 44.1
RTS-CW | S | 135.5 |  | 0.91828 |  |  | 123.6 | 131.3 | 139.6 | 145.4 | 144.7 | 144.6
| W | 142.3 |  | 0.93744 |  |  | 102.3 | 108.7 | 117.9 | 120.7 | 120.3 | 121.7
RTS-NR | S | 135.5 |  | 0.91118 |  |  | 121.6 | 130.1 | 137.6 | 143.2 | 142.5 | 142.5
| W | 137.2 |  | 0.92444 |  |  | 101.9 | 108.2 | 117.5 | 119.1 | 119.2 | 120.2
B-CW | S | 85.7 |  | 0.94533 |  |  | 87.8 | 92 | 98.3 | 104 | 103.2 | 102
| W | 91.4 |  | 0.95448 |  |  | 70.3 | 74.2 | 82.8 | 85.8 | 85 | 85
B-NR | S | 85.7 |  | 0.92913 |  |  | 63.5 | 69.4 | 72.3 | 75.6 | 75.7 | 76.3
| W | 91.4 |  | 0.93253 |  |  | 57.8 | 61.7 | 66.8 | 67.9 | 68.3 | 69
RTS-SK | S | 102.9 |  | 0.94313 |  |  | 72.1 | 76.8 | 78.5 | 78.5 | 78.2 | 77
| W | 108 |  | 0.98131 |  |  | 64.2 | 66.7 | 67.5 | 68.1 | 68 | 68.1
RTS-FR1 | S | 82.3 |  | 1 |  |  | 28.8 | 28.7 | 28.7 | 28.7 | 28.9 | 28.9
| W | 87.4 |  | 1 |  |  | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.9
RTS-FR2 | S | 82.3 |  | 0.99654 |  |  | 28.9 | 28.9 | 28.9 | 28.9 | 28.9 | 28.9
| W | 87.4 |  | 1 |  |  | 28.8 | 28.9 | 28.9 | 28.8 | 29 | 28.9
RTS-FR3 | S | 82.3 |  | 1 |  |  | 28.7 | 28.6 | 28.6 | 28.6 | 28.7 | 28.8
| W | 87.4 |  | 0.99652 |  |  | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7
FR-WP1 | S | 78.3 |  | 0.7874 |  |  | 12.7 | 12.6 | 12.5 | 12.6 | 12.5 | 12.5
| W | 84.6 |  | 0.7874 |  |  | 12.7 | 12.7 | 12.6 | 12.7 | 12.7 | 12.6
FR-WP2 | S | 80 |  | 0.91818 |  |  | 11 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9
| W | 85.7 |  | 0.92727 |  |  | 11 | 11 | 11 | 11 | 11 | 11
FR-WP3 | S | 81.7 |  | 0.92523 |  |  | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7
| W | 88 |  | 0.92523 |  |  | 10.7 | 10.8 | 10.7 | 10.7 | 10.7 | 10.7
SVTS 66kV
SVTS-RD | S | 116.6 |  | 0.95344 |  |  | 94.5 | 100.1 | 102.2 | 102.4 | 103 | 103.4
| W | 122.3 |  | 0.97013 |  |  | 70.3 | 71.9 | 73.3 | 73.6 | 73.5 | 73.9
TSTS 66kV
TSTS-L | S | 106.9 | 2 | 0.91297 |  |  | 117.2 | 120.2 | 121.7 | 123.2 | 123.1 | 123.7 | 12.44% | 23 | 30 | 39 | 38 | 42 | 5 | 6 | 7 | 7 | 7
| W | 108.6 | 3 | 0.92695 |  |  | 83.5 | 84.1 | 85.9 | 86.6 | 87.1 | 89.1
HB-Q | S | 95.5 |  | 0.92623 |  |  | 85.4 | 86.6 | 87.5 | 89 | 89.1 | 89.7
| W | 108.6 |  | 0.91987 |  |  | 62.4 | 63.2 | 64.6 | 65.2 | 65.7 | 67.3
L-Q | S | 95.4 |  | 0.95801 |  |  | 64.3 | 66.4 | 66.8 | 67.7 | 67.7 | 67.9
| W | 108.6 |  | 0.97308 |  |  | 48.3 | 48.4 | 49.6 | 50.1 | 50.2 | 51.3
WMTS 22kV
WMTS-DA213 | S | 23.8 |  | 0.95726 |  |  | 23.4 | 27 | 28.3 | 29.1 | 28.8 | 28.3
| W | 29.1 |  | 0.93776 |  |  | 24.1 | 26.4 | 27.4 | 27.8 | 27.5 | 27.4
WMTS-DA222 | S | 23.8 |  | 0.93249 |  |  | 23.7 | 27.5 | 28.7 | 29.8 | 29.4 | 28.7
| W | 29.1 |  | 0.93061 |  |  | 24.5 | 26.8 | 28.1 | 28.3 | 28 | 27.8
WMTS-LS214 | S | 19.1 |  | 0.97717 |  |  | 21.9 | 11.1 | 11.4 | 11.8 | 11.8 | 11.8
| W | 19.1 |  | 0.97861 |  |  | 18.7 | 11.3 | 11.3 | 11.1 | 10.7 | 10.3
WMTS-LS226 | S | 19.1 |  | 0.97717 |  |  | 21.9 | 7.5 | 7.7 | 8.1 | 8.1 | 8.2
| W | 19.1 |  | 0.97861 |  |  | 18.7 | 7.7 | 7.6 | 7.5 | 7.5 | 7.9
WMTS 66kV
WMTS-JA1 | S | 145.2 |  | 0.96762 |  |  | 52.5 | 54.2 | 55.2 | 57.8 | 57.6 | 56.7
| W | 153.2 |  | 0.97521 |  |  | 48.4 | 49.6 | 51.2 | 52.5 | 52 | 51.5
WMTS-JA3 | S | 114.9 |  | 0.97556 |  |  | 49.1 | 50.8 | 51.7 | 54.1 | 53.6 | 53.1
| W | 121.2 |  | 0.98234 |  |  | 45.3 | 46.5 | 48 | 49.1 | 48.7 | 48.3
WMTS-VM1 | S | 130.3 |  | 0.97574 |  |  | 37.1 | 38.7 | 39.7 | 41.8 | 41.6 | 41.1
| W | 164.6 |  | 0.98498 |  |  | 33.3 | 34.5 | 35.9 | 37.1 | 36.7 | 36.2
WMTS-VM2 | S | 144 |  | 0.95307 |  |  | 27.7 | 28.9 | 29.6 | 31.2 | 31 | 30.6
| W | 155.5 |  | 0.96774 |  |  | 24.8 | 25.7 | 26.8 | 27.6 | 27.3 | 27
WMTS-VM3 | S | 120 |  | 0.959 |  |  | 43.9 | 45.8 | 47 | 49.5 | 49.2 | 48.6
| W | 129.7 |  | 0.96954 |  |  | 39.4 | 40.8 | 42.5 | 43.9 | 43.4 | 42.8
VM-LQ1 | S | 76.6 |  | 0.95183 |  |  | 43.6 | 45.4 | 46.6 | 50.1 | 48.7 | 47.8
| W | 86.9 |  | 0.94723 |  |  | 37.9 | 40.3 | 41.9 | 43.1 | 42.3 | 41.5
VM-LQ3 | S | 76.6 |  | 0.84091 |  |  | 52.8 | 56.9 | 60.6 | 64.8 | 65.4 | 64.3
| W | 86.9 |  | 0.87588 |  |  | 42.7 | 45.3 | 48.9 | 52.1 | 51.3 | 50.4
VM-JA | S | 91.5 |  | 0.99252 |  |  | 53.5 | 54.7 | 55.3 | 57.1 | 56.7 | 56.3
| W | 98.3 |  | 0.99606 |  |  | 50.7 | 51.6 | 52.7 | 53.5 | 53.2 | 52.9
JA-LQ2 | S | 76.6 |  | 0.8416 |  |  | 52.4 | 57.1 | 60.2 | 66.2 | 65.8 | 64.7
| W | 86.9 |  | 0.87822 |  |  | 42.7 | 44.9 | 49 | 52.3 | 51.5 | 50.5
JA-WP | S | 47.4 |  | 0 |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
| W | 57.2 |  | 0 |  |  | 0.5 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5
WMTS-NC | S | 54.9 | 3 | 0.91693 |  |  | 62.6 | 62.9 | 64.5 | 65.9 | 66.5 | 67.7 | 14.57% | 849 | 1370 | 2820 | 3171 | 4124 | 167 | 265 | 483 | 537 | 693
| W | 70.3 | 5 | 0.91639 |  |  | 59.8 | 60.5 | 62.5 | 63 | 63.5 | 64.6
WMTS-WB | S | 54.9 | 3 | 0.91242 |  |  | 62.8 | 63.5 | 64.4 | 66.7 | 67.3 | 68.6 | 15.66% | 627 | 1143 | 2130 | 2388 | 3180 | 133 | 217 | 367 | 401 | 548
| W | 70.3 | 5 | 0.91376 |  |  | 60.3 | 60.3 | 62.1 | 63.2 | 63.7 | 64.9
WB-NC | S | 74.3 |  | 0.93824 |  |  | 34 | 34.6 | 35.5 | 37.7 | 38.3 | 39.4
| W | 97.2 |  | 0.93987 |  |  | 31.6 | 31.8 | 33.4 | 34.4 | 34.9 | 36