## Intro
CitiPower 2024 Distribution System Limitation Template
This Distribution Systems Limitations template is intended to make the Distribution Annual Planning Report (DAPR) limitation data more accessible and usable. Any information provided in this System Limitations template should be read in conjunction with the CitiPower 2024 DAPR. It should also be noted that the information in this template and the DAPR are based on high-level risk assessments produced for the DAPR. As such the numbers are indicative and subject to change. Therefore the information in this template should not be used to make investment decisions, and should only be used to assist in discussions with CitiPower. Finalised data will be produced in a detailed risk assessment conducted at the RIT-D or business case stage. However CitiPower invites interested parties to submit their proposals or to engage in joint planning with CitiPower as early as possible in order to defer or avoid the proposed augmentation. CitiPower also publishes its own Network Limitation maps in order to assist with the visualisation of the limitation data presented within this template and the DAPR. The data in this template will be updated annually and will be published along with the DAPR. We welcome any feedback to improve the content or usability of this template.

## Citipower Limitations
Owner | Asset Name | Asset Code | Network Element | Voltage level (kV) | Rating |  |  |  | Nameplate Rating | Location |  |  |  | Residential customers affected |  | Business Case | [7 empty] | Demand Reduction required to defer investment by 1 year |  | Emergency Generation |  | Load Transfer capability (MVA) | Power Factor | Summer 10% POE | [14 empty] | Summer 50% POE | [14 empty] | Weighted Energy at Risk (MWh)
[5 empty] | Summer |  | Winter |  |  | Start |  | End |  |  |  | Constraint Primary Driver | Investment Description | Preferred network investment |  |  |  | Proposed Timing | Annual Deferral Value | [6 empty] | Forecast Maximum Demand (MVA) |  |  |  |  | Maximum Load at risk (MVA) (N-1) |  |  |  |  | Hours at Risk (Hrs) |  |  |  |  | Forecast Maximum Demand (MVA) |  |  |  |  | Maximum Load at risk (MVA) (N-1) |  |  |  |  | Hours at Risk (Hrs)
[5 empty] | N Rating (MVA) | N-1 Rating (MVA) | N Rating (MVA) | N-1 Rating (MVA) |  | Longitude | Latitude | Longitude | Latitude | Count | Percent |  |  | capital cost ($) | cost accuracy plus | cost accuracy minus | Operating cost ($) |  |  | (MW) | (MVA) | (MW) | (MVA) |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029
Citipower | Collingwood | B | zss | 66/11 | 69.4 | 29 | 75.7 | 32.2 | 54 | 144.9913 | -37.8068 | 144.9913 | -37.8068 | 5158 | 75.38% | capacity | Citipower's preferred network option is to establish a third transformer at B. See the DAPR report for more details. | 7356836 | 30% | 30% | 73568.36 | 2029 | 313649.2094 | 19.4872 | 19.6841 | 0 | 0 | 6.4588 | 0.99 | 47.7334 | 49.4612 | 50.4782 | 51.6811 | 52.6653 | 18.7334 | 20.4612 | 21.4782 | 22.6811 | 23.6653 | 494.25 | 724.5 | 897.5 | 1106.5 | 1307.25 | 44.125 | 45.7222 | 46.6623 | 47.7743 | 48.6841 | 15.125 | 16.7222 | 17.6623 | 18.7743 | 19.6841 | 249.25 | 359 | 450 | 582.5 | 715.25 | 1149.196 | 1631.3278 | 2008.5787 | 2549.2338 | 3103.5624
Citipower | Brunswick | BK | zss | 22/6.6 | 27.2 | 27.2 | 28.6 | 28.6 | 33 | 144.9724 | -37.7569 | 144.9724 | -37.7569 | 7305 | 89.18% | reliability | Citipower's preferred network option is to offload to WB and convert 6.6kV feeders to 11kV. See the DAPR report for more details. | 30380536.7231 | 30% | 30% | 303805.3672 | 2028 | 1295234.9791 | 0 | 0 | 0 | 0 | 0 | 0.99 | 18.3921 | 19.9846 | 20.5474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.4697 | 16.8092 | 17.2825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Citipower | Bouveries/ Queens | BQ | zss | 66/11 | 132.3 | 64.9 | 147.3 | 72.3 | 110 | 144.9613 | -37.8052 | 144.9613 | -37.8052 | 17217 | 87.1% | capacity | Citipower's preferred network option is to establish a third transformer at BQ. See the DAPR report for more details. | 18102588 | 30% | 30% | 181025.88 | 2028 | 771780.4792 | 20.9176 | 21.1289 | 0 | 0 | 10.4408 | 0.99 | 91.9614 | 97.5425 | 98.0384 | 98.073 | 138.4553 | 27.0614 | 32.6425 | 33.1384 | 33.173 | 73.5553 | 525 | 1032.5 | 1187 | 1239 | 6677 | 80.6679 | 85.5636 | 85.9986 | 86.0289 | 121.452 | 15.7679 | 20.6636 | 21.0986 | 21.1289 | 56.552 | 44.25 | 99.5 | 107.75 | 109 | 4067 | 796.088 | 1879.1121 | 2219.6063 | 2335.1497 | 64706.7849
Citipower | Bouveries/ Queens feeder 17 | BQ017 | feeder | 11 | 10.6 | 10.6 | 10.6 | 10.6 | - | 144.9432 | -37.7924 | 144.9432 | -37.7924 | 4386 | 92.12% | capacity | Citipower's preferred network option is to construct a new feeder from BQ. See the DAPR report for more details. | 4000000 | 30% | 30% | 40000 | 2026 | 189790.3782 | 4.693 | 4.693 | 0 | 0 | 0 | 1 | 15.938 | 17.4564 | 17.6962 | 18.0158 | 18.1985 | 5.338 | 6.8564 | 7.0962 | 7.4158 | 7.5985 | 490.75 | 905.25 | 1115 | 1232.75 | 1331 | 13.9628 | 15.293 | 15.5031 | 15.7831 | 15.9431 | 3.3628 | 4.693 | 4.9031 | 5.1831 | 5.3431 | 122.5 | 335 | 454.5 | 533.25 | 600.5 | 119.3767 | 332.4071 | 455.3351 | 551.7453 | 634.6816
Citipower | Fishermans Bend | E | zss | 66/6.6 | 10.9 | 0 | 12.1 | 0 | 46 | 144.9226 | -37.8243 | 144.9226 | -37.8243 | 0 | 0% | capacity | Citipower's preferred network option is to offload to WG and convert 6.6kV feeders to 11kV. See the DAPR report for more details. | 4472699 | 30% | 30% | 44727.001 | 2029 | 190687.7501 | 2.08 | 2.08 | 0 | 0 | 3.178 | 1 | 1.6983 | 1.887 | 2.0202 | 2.1645 | 2.3088 | 1.6983 | 1.887 | 2.0202 | 2.1645 | 2.3088 | 8760 | 8760 | 8760 | 8760 | 8760 | 1.53 | 1.7 | 1.82 | 1.95 | 2.08 | 1.53 | 1.7 | 1.82 | 1.95 | 2.08 | 8760 | 8760 | 8760 | 8760 | 8760 | 6179.5553 | 6877.3841 | 7414.815 | 7948.4487 | 8459.6595
Citipower | Fitzroy | F | zss | 22/6.6 | 30.2 | 13.5 | 35.2 | 15.3 | 23 | 144.9896 | -37.7873 | 144.9896 | -37.7873 | 7852 | 91.37% | capacity | Citipower's preferred network option is to offload to CW and convert 6.6kV feeders to 11kV. See the DAPR report for more details. | 45172423.6556 | 30% | 30% | 451724.2366 | 2027 | 1925867.9906 | 0 | 0 | 0 | 0 | 1.6118 | 1 | 16.0398 | 16.5325 | 0 | 0 | 0 | 2.5398 | 3.0325 | 0 | 0 | 0 | 25.5 | 19.75 | 0 | 0 | 0 | 14.07 | 14.5022 | 0 | 0 | 0 | 0.57003 | 1.0022 | 0 | 0 | 0 | 3.75 | 2.5 | 0 | 0 | 0 | 6.0749 | 6.8098 | 0 | 0 | 0
Citipower | West Brunswick | WB011 | feeder | 6.6 | 0 | 0 | 0 | 0 | - | 144.9446 | -37.7611 | 144.9446 | -37.7611 | 1654 | 96.5% | capacity | Citipower's preferred network option is to uprate feeder WB011 and offload WB002. See the DAPR report for more details. | 260000 | 30% | 30% | 2600 | 2027 | 11084.7645 | 4.5459 | 4.5918 | 0 | 0 | 0 | 0.99 | 2.9006 | 4.8269 | 5.1181 | 5.1741 | 5.2301 | 2.9006 | 4.8269 | 5.1181 | 5.1741 | 5.2301 | 0 | 12.75 | 27.25 | 31.25 | 36.25 | 2.6023 | 4.3305 | 4.5918 | 4.642 | 4.6922 | 2.6023 | 4.3305 | 4.5918 | 4.642 | 4.6922 | 0 | 1.5 | 5.25 | 7 | 8.5 | 0 | 1.7366 | 4.1402 | 5.0501 | 5.9651
Citipower | Armadale 11kV Switchboard Replacement | AR | zss | 11 | 0 | 0 | 0 | 0 | 60 | 145.0192 | -37.8555 | 145.0192 | -37.8555 | 11972 | 90.24% | asset condition | Citipower’s preferred network option is to replace the 11kV switchboard at AR. See the DAPR report for more details. | 7775638 | 30% | 30% | 77756.38 | 2027 | 331504.2922 | - | - | 0 | 0 | 5.8301 | 0.98 | 37.64 | 38.42 | 38.75 | 39.16 | 39.66 | 37.64 | 38.42 | 38.75 | 39.16 | 39.66 | - | - | - | - | - | 34.12 | 34.83 | 35.03 | 35.33 | 35.75 | 34.12 | 34.83 | 35.03 | 35.33 | 35.75 | - | - | - | - | - | - | - | - | - | -
Citipower | Armadale #2 Transformer Replacement | AR | zss | 66/11 | 32.9 | 0 | 35.8 | 0 | 60 | 145.0192 | -37.8555 | 145.0192 | -37.8555 | 11972 | 90.24% | asset condition | Citipower’s preferred network option is to replace the #2 transformer AR. See the DAPR report for more details. | 6426019 | 30% | 30% | 64260.19 | 2029 | 273965.0277 | 35.035 | 35.75 | 0 | 0 | 5.8301 | 0.98 | 37.64 | 38.42 | 38.75 | 39.16 | 39.66 | 37.64 | 38.42 | 38.75 | 39.16 | 39.66 | 8760 | 8760 | 8760 | 8760 | 8760 | 34.12 | 34.83 | 35.03 | 35.33 | 35.75 | 34.12 | 34.83 | 35.03 | 35.33 | 35.75 | 8760 | 8760 | 8760 | 8760 | 8760 | 114640 | 116924 | 117915 | 119173 | 120674
Citipower | Collingwood (B) 11kV Switchboard Replacement | B | zss | 11 | 0 | 0 | 0 | 0 | 54 | 144.9913 | -37.8068 | 144.9913 | -37.8068 | 5158 | 75.38% | asset condition | Citipower’s preferred network option is to replace the 11kV switchboard at B. See the DAPR report for more details. | 15800000 | 30% | 30% | 158000 | 2028 | 673612.6112 | - | - | 0 | 0 | 6.4588 | 0.99 | 47.7334 | 49.4612 | 50.4782 | 51.6811 | 52.6653 | 47.7334 | 49.4612 | 50.4782 | 51.6811 | 52.6653 | - | - | - | - | - | 44.125 | 45.7222 | 46.6623 | 47.7743 | 48.6841 | 44.125 | 45.7222 | 46.6623 | 47.7743 | 48.6841 | - | - | - | - | - | - | - | - | - | -
Citipower | Collingwood (CW) 11kV Switchboard Replacement | CW | zss | 11 | 0 | 0 | 0 | 0 | 54 | 144.9872 | -37.7981 | 144.9872 | -37.7981 | 7666 | 78.28% | asset condition | Citipower’s preferred network option is to replace the 11kV switchboard at CW. See the DAPR report for more details. | 9000000 | 30% | 30% | 90000 | 2026 | 383703.3861 | - | - | 0 | 0 | 0.7621 | 0.99 | 29.535 | 32.2106 | 50.0557 | 51.1811 | 52.272 | 29.535 | 32.2106 | 50.0557 | 51.1811 | 52.272 | - | - | - | - | - | 25.83 | 28.19 | 43.96 | 44.95 | 45.92 | 25.83 | 28.19 | 43.96 | 44.95 | 45.92 | - | - | - | - | - | - | - | - | - | -
Citipower | Northcote 11kV Switchboard Replacement | NC | zss | 11 | 0 | 0 | 0 | 0 | 60 | 145.0033 | -37.771 | 145.0033 | -37.771 | 17685 | 92.23% | asset condition | Citipower’s preferred network option is to replace the 11kV switchboard at NC. See the DAPR report for more details. | 7239102 | 30% | 30% | 72391.02 | 2029 | 308629.7722 | - | - | 0 | 0 | 0 | 0.99 | 37.4 | 38.1 | 38.95 | 39.9 | 40.74 | 37.4 | 38.1 | 38.95 | 39.9 | 40.74 | - | - | - | - | - | 33.94 | 34.68 | 35.38 | 36.29 | 37.17 | 33.94 | 34.68 | 35.38 | 36.29 | 37.17 | - | - | - | - | - | - | - | - | - | -
Citipower | Northcote #1 Transformer Replacement | NC | zss | 66/11 | 31.9 | 0 | 40.2 | 0 | 60 | 145.0033 | -37.771 | 145.0033 | -37.771 | 17685 | 92.23% | asset condition | Citipower’s preferred network option is to replace the #1 transformer NC. See the DAPR report for more details. | 7599585 | 30% | 30% | 75995.85 | 2027 | 323998.4997 | 35.0262 | 35.38 | 0 | 0 | 0 | 0.99 | 37.4 | 38.1 | 38.95 | 39.9 | 40.74 | 37.4 | 38.1 | 38.95 | 39.9 | 40.74 | 8760 | 8760 | 8760 | 8760 | 8760 | 33.94 | 34.68 | 35.38 | 36.29 | 37.17 | 33.94 | 34.68 | 35.38 | 36.29 | 37.17 | 8760 | 8760 | 8760 | 8760 | 8760 | 110676 | 112813 | 115305 | 118191 | 120795
Citipower | Richmond 22kV Switchboard Retirement | R | zss | 22 | 0 | 0 | 0 | 0 | 39 | 144.994 | -37.8325 | 144.994 | -37.8325 | 4789 | 72.65% | asset condition | Citipower’s preferred network option is to retire the 22kV switchboard at R. See the DAPR report for more details. | 2700000 | 30% | 30% | 27000 | 2026 | 115111.0158 | - | - | 0 | 0 | 7.259 | 1 | 35.97 | 41.8 | 45.59 | 46.3 | 46.64 | 35.97 | 41.8 | 45.59 | 46.3 | 46.64 | - | - | - | - | - | 31.9 | 37.55 | 41.1 | 41.68 | 41.81 | 31.9 | 37.55 | 41.1 | 41.68 | 41.81 | - | - | - | - | - | - | - | - | - | -
Citipower | Riversdale 11kV Switchboard Replacement | RD | zss | 11 | 0 | 0 | 0 | 0 | 60 | 145.0869 | -37.8426 | 145.0869 | -37.8426 | 10885 | 92.16% | asset condition | Citipower’s preferred network option is to replace the 11kV switchboard at RD. See the DAPR report for more details. | 7242171 | 30% | 30% | 72421.71 | 2028 | 308760.615 | - | - | 0 | 0 | 8.4403 | 0.99 | 39.92 | 40 | 40.38 | 40.99 | 41.31 | 39.92 | 40 | 40.38 | 40.99 | 41.31 | - | - | - | - | - | 36.08 | 36.22 | 36.38 | 36.85 | 37.28 | 36.08 | 36.22 | 36.38 | 36.85 | 37.28 | - | - | - | - | - | - | - | - | - | -
Citipower | Victoria Market 11kV Switchboard Replacement | VM | zss | 11 | 0 | 0 | 0 | 0 | 84 | 144.9536 | -37.8085 | 144.9536 | -37.8085 | 7926 | 81.78% | asset condition | Citipower’s preferred network option is to replace the 11kV switchboard at VM. See the DAPR report for more details. | 13766800 | 30% | 30% | 137668 | 2028 | 586929.7529 | - | - | 0 | 0 | 12.2698 | 0.99 | 67.45 | 71.11 | 72.28 | 73.62 | 74.97 | 67.45 | 71.11 | 72.28 | 73.62 | 74.97 | - | - | - | - | - | 60.46 | 64.03 | 65.21 | 66.52 | 67.7 | 60.46 | 64.03 | 65.21 | 66.52 | 67.7 | - | - | - | - | - | - | - | - | - | -
Citipower | Victoria Market #1 Transformer Replacement | VM | zss | 66/11 | 57.88 | 28.94 | 70.22 | 35.11 | 84 | 144.9536 | -37.8085 | 144.9536 | -37.8085 | 7926 | 81.78% | asset condition | Citipower’s preferred network option is to replace the #1 transformer VM. See the DAPR report for more details. | 5575079 | 30% | 30% | 55750.79 | 2030 | 237686.2989 | 67.023 | 67.7 | 0 | 0 | 12.2698 | 0.99 | 67.45 | 71.11 | 72.28 | 73.62 | 74.97 | 38.51 | 42.17 | 43.34 | 44.68 | 46.03 | 7011 | 7676 | 7893 | 8136 | 8348 | 60.46 | 64.03 | 65.21 | 66.52 | 67.7 | 31.52 | 35.09 | 36.27 | 37.58 | 38.76 | 5360 | 6338 | 6602 | 6848 | 7051 | 51892.2985 | 66234.4063 | 71030.7387 | 76653.2808 | 82445.8999

## Sub-T Aug Sum
Sub transmission line | Season | Line N Import Rating (MVA) | Line Power Factor at Maximum Demand | Embedded Generation Capacity (MVA) | Load Transfer Capability (MVA) | Hours load is > 95% of Maximum Demand (Hrs) | Actual Maximum Demand (MVA) | 50% POE |  |  |  |  | 50% POE load above N Import Rating (%) | 50% POE load above N Import Rating (MVA) | 50% POE
[8 empty] | Forecast Maximum Demand (MVA) | [6 empty] | Energy at Risk (MWh) |  |  |  |  | Hours at Risk (Hrs)
|  |  | 2024 | 2024 | 2025 | 2024 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2025 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029
RTS-RP124 | S | 7.6 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-RP124 | W | 7.6 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF1 | S | 87.5 | 0.9749 | 0 | - | - | 23.9 | 26.1 | 27.4 | 28.5 | 29.4 | 30.2 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF1 | W | 87.5 | 0.9751 | 0 | - | - | 24.1 | 22.8 | 23.7 | 24.4 | 25.1 | 25.7 | - | - | - | - | - | - | - | - | - | - | - | -
VM-LQ3 | S | 76.6 | 0.90814 | 26.1277 | - | - | 38.1 | 42.6 | 47.6 | 51 | 52.3 | 54.3 | - | - | - | - | - | - | - | - | - | - | - | -
VM-LQ3 | W | 86.9 | 0.90789 | 26.1277 | - | - | 38 | 31 | 33.5 | 35.5 | 36.6 | 37.6 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-WG | S | 88 | 0.94777 | 12.9152 | - | - | 65.1 | 78.6 | 89.2 | 94.5 | 100.8 | 106.3 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-WG | W | 112 | 0.94486 | 12.9152 | - | - | 67.1 | 78.6 | 85.5 | 90.6 | 96.3 | 101.4 | - | - | - | - | - | - | - | - | - | - | - | -
VM-WA2 | S | 37.7 | 0.95294 | 31.5038 | - | - | 17 | 20.9 | 22.2 | 23.2 | 23.9 | 25 | - | - | - | - | - | - | - | - | - | - | - | -
VM-WA2 | W | 40 | 0.94937 | 31.5038 | - | - | 15.8 | 15.4 | 16.1 | 16.3 | 16.7 | 16.9 | - | - | - | - | - | - | - | - | - | - | - | -
FB-WG | S | 89.7 | 0.96692 | 25.6631 | - | - | 39.3 | 52.5 | 59.5 | 62.6 | 65.8 | 68.7 | - | - | - | - | - | - | - | - | - | - | - | -
FB-WG | W | 94.3 | 0.96825 | 25.6631 | - | - | 37.8 | 46.5 | 50.2 | 52.8 | 55.5 | 57.6 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-FR3 | S | 82.3 | 0.98452 | 18.4119 | - | - | 32.3 | 33.5 | 34.4 | 34.6 | 34.8 | 35.1 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-FR3 | W | 87.4 | 0.98452 | 18.4119 | - | - | 32.3 | 29.7 | 30.1 | 30.3 | 30.5 | 30.9 | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-HB | S | 117.2 | 0.8928 | 0 | - | - | 116.6 | 120.4 | 121.2 | 121.6 | 123.4 | 124.7 | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-HB | W | 126.3 | 0.9 | 0 | - | - | 112 | 85 | 86.5 | 88.2 | 90 | 91 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BQ3 | S | 139.7 | 0.9682 | 1.0402 | - | - | 91.2 | 95.5 | 98.9 | 99.5 | 100.5 | 101.1 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BQ3 | W | 149.2 | 0.96909 | 1.0402 | - | - | 90.6 | 81.7 | 83.2 | 83.9 | 84.6 | 85 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-ARD1 | S | 21.9 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-ARD1 | W | 26.5 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
B-NR | S | 85.7 | 0.95857 | 34.0652 | - | - | 70 | 73.3 | 77.7 | 97.8 | 100.4 | 102.8 | - | - | - | - | - | - | - | - | - | - | - | -
B-NR | W | 91.4 | 0.9584 | 34.0652 | - | - | 67.3 | 60.5 | 82.4 | 84.1 | 86.6 | 88.4 | - | - | - | - | - | - | - | - | - | - | - | -
B-CW | S | 85.7 | 0.94929 | 29.046 | - | 3.75 | 98.6 | 103.9 | 107.7 | 109.5 | 112.1 | 114.6 | 21.24% | 18.2 | 140.9738 | 190.6639 | 216.7085 | 256.8564 | 295.0519 | 13.5 | 16.5 | 17.25 | 17.75 | 18.5
B-CW | W | 91.4 | 0.95016 | 29.046 | - | 0.5 | 96.3 | 84.7 | 88.1 | 89.2 | 93.1 | 94.5 | - | - | - | - | - | - | - | - | - | - | - | -
BQ-WP3 | S | 84 | 0.96806 | 65.4648 | - | - | 40.7 | 41.4 | 43.1 | 43 | 43.3 | 43.2 | - | - | - | - | - | - | - | - | - | - | - | -
BQ-WP3 | W | 91.5 | 0.9679 | 65.4648 | - | - | 40.5 | 31.2 | 31.8 | 31.9 | 32 | 32 | - | - | - | - | - | - | - | - | - | - | - | -
BQ-WP2 | S | 84 | 0.96806 | 65.4648 | - | - | 40.7 | 41.4 | 43.1 | 43 | 43.3 | 43.2 | - | - | - | - | - | - | - | - | - | - | - | -
BQ-WP2 | W | 91.5 | 0.9679 | 65.4648 | - | - | 40.5 | 31.2 | 31.8 | 31.9 | 32 | 32 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-FR1 | S | 82.3 | 0.9816 | 18.4119 | - | - | 32.6 | 33.8 | 34.5 | 34.9 | 35.1 | 35.4 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-FR1 | W | 87.4 | 0.9816 | 18.4119 | - | - | 32.6 | 30 | 30.4 | 30.6 | 30.8 | 31.2 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BK194 | S | 10.3 | 0.94118 | 54.4501 | - | - | 8.5 | 8.6 | 9.1 | 9.3 | 2.4 | 2.4 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BK194 | W | 10.3 | 0.94118 | 54.4501 | - | - | 8.5 | 9 | 9.2 | 9.6 | 2.8 | 3.1 | - | - | - | - | - | - | - | - | - | - | - | -
TK-BC | S | 91.5 | 0.94314 | 62.5322 | - | - | 80.9 | 83.1 | 84.9 | 89.9 | 91.1 | 92.1 | - | - | - | - | - | - | - | - | - | - | - | -
TK-BC | W | 91.5 | 0.94444 | 62.5322 | - | - | 81 | 71.9 | 75.2 | 78.8 | 79.6 | 80.4 | - | - | - | - | - | - | - | - | - | - | - | -
SB-SO | S | 109.7 | 0.98504 | 42.6797 | - | - | 40.1 | 44.1 | 46.5 | 48 | 49.5 | 50.8 | - | - | - | - | - | - | - | - | - | - | - | -
SB-SO | W | 121.7 | 0.98701 | 42.6797 | - | - | 38.5 | 32.5 | 34 | 34.9 | 36.1 | 36.9 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BK187 | S | 10.3 | 0.98718 | 54.4501 | - | - | 7.8 | 8.1 | 8.8 | 9.2 | 2.3 | 2.3 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BK187 | W | 10.3 | 0.98718 | 54.4501 | - | - | 7.8 | 8.2 | 8.7 | 8.8 | 2.6 | 3 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-FR2 | S | 82.3 | 0.98466 | 18.4119 | - | - | 32.6 | 33.8 | 34.7 | 34.9 | 35 | 35.4 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-FR2 | W | 87.4 | 0.98466 | 18.4119 | - | - | 32.6 | 30 | 30.4 | 30.6 | 30.8 | 31.1 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-SB | S | 117.7 | 0.97091 | 18.9423 | - | - | 72.2 | 79.3 | 83.8 | 86.5 | 89.4 | 92 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-SB | W | 130.3 | 0.97118 | 18.9423 | - | - | 69.4 | 58 | 60.7 | 62.4 | 64.5 | 66 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-RP123 | S | 11.4 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-RP123 | W | 11.4 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
FR-WP3 | S | 81.7 | 0.92053 | 82.8365 | - | - | 15.1 | 16.3 | 17 | 17.3 | 17.1 | 17.8 | - | - | - | - | - | - | - | - | - | - | - | -
FR-WP3 | W | 88 | 0.91391 | 82.8365 | - | - | 15.1 | 12.4 | 12.8 | 13 | 13.2 | 13 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BQ1 | S | 159.9 | 0.96691 | 1.0402 | - | - | 96.7 | 101.3 | 104.9 | 105.5 | 106.5 | 107.2 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BQ1 | W | 170.6 | 0.96875 | 1.0402 | - | - | 96 | 86.6 | 88.1 | 88.9 | 89.7 | 90.1 | - | - | - | - | - | - | - | - | - | - | - | -
VM-BQ1 | S | 162.3 | 0.95565 | 21.7111 | - | - | 45.1 | 50.8 | 54.3 | 55.3 | 56.2 | 57.6 | - | - | - | - | - | - | - | - | - | - | - | -
VM-BQ1 | W | 173.8 | 0.95711 | 21.7111 | - | - | 44.3 | 40.4 | 41.6 | 42.8 | 43.7 | 44.3 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-VM1 | S | 159.9 | 0.96856 | 20.6709 | - | - | 82.7 | 87.4 | 90.8 | 91.5 | 92.5 | 93.2 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-VM1 | W | 170.6 | 0.96833 | 20.6709 | - | - | 82.1 | 74.1 | 75.5 | 76.4 | 77.1 | 77.6 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-R136 | S | 21.5 | 0.98462 | 1.9222 | 8.0021 | - | 19.5 | 21.7 | 25.5 | 27.8 | 28.1 | 28.2 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-R136 | W | 24.7 | 0.98515 | 1.9222 | 8.0021 | - | 20.2 | 21.1 | 23.6 | 24.5 | 24.8 | 24.8 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-SO | S | 109.2 | 0.97091 | 23.7374 | - | - | 72.2 | 79.8 | 83.8 | 86.8 | 89.4 | 92 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-SO | W | 125.7 | 0.97118 | 23.7374 | - | - | 69.4 | 58 | 60.7 | 62.4 | 64.5 | 66 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-K | S | 90.3 | 0.96692 | 0 | - | - | 90.7 | 91 | 92.3 | 93.3 | 93.4 | 94.6 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-K | W | 104.6 | 0.967 | 0 | - | - | 90.9 | 66.5 | 67.9 | 68.1 | 69.5 | 70.1 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-EW | S | 85.7 | 0.9709 | 0 | - | - | 65.3 | 68.9 | 71.9 | 73.6 | 75.6 | 77.9 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-EW | W | 101.7 | 0.97024 | 0 | - | - | 67.2 | 63.3 | 65.3 | 67.4 | 69.3 | 71.4 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-F179 | S | 12 | 0.98734 | 1.3729 | 1.6 | 1.5 | 15.8 | 14.6 | 14.9 | 3.1 | 3.1 | 3.1 | 21.67% | 2.6 | 6.9594 | 1.0173 | 0 | 0 | 0 | 7.5 | 2 | 0 | 0 | 0
BTS-F179 | W | 12.6 | 0.98734 | 1.3729 | 1.6 | 3.5 | 15.8 | 17.1 | 3.3 | 3.2 | 3.2 | 3.2 | 35.71% | 4.5 | 6.9594 | 1.0173 | 0 | 0 | 0 | 7.5 | 2 | 0 | 0 | 0
FR-WP1 | S | 78.3 | 1 | 82.8365 | - | - | 13.3 | 14.5 | 15.2 | 15.5 | 15.8 | 16 | - | - | - | - | - | - | - | - | - | - | - | -
FR-WP1 | W | 84.6 | 1 | 82.8365 | - | - | 13.3 | 11 | 11.4 | 11.5 | 11.7 | 11.9 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-TK/BC | S | 135.5 | 0.95305 | 62.5322 | - | - | 100.1 | 104.1 | 107 | 111 | 112.9 | 114.5 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-TK/BC | W | 137.2 | 0.95272 | 62.5322 | - | - | 99.4 | 89.3 | 92.5 | 96.2 | 98 | 98.9 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-CW | S | 135.5 | 0.93282 | 14.8598 | - | - | 131 | 137.3 | 144.9 | 166.8 | 171.2 | 176.3 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-CW | W | 142.3 | 0.93381 | 14.8598 | - | - | 125.4 | 111.2 | 136.5 | 138.6 | 145 | 147.3 | - | - | - | - | - | - | - | - | - | - | - | -
VM-WA3 | S | 37.7 | 0.97484 | 31.5038 | - | - | 15.9 | 18.6 | 19.8 | 19.8 | 20.3 | 20.3 | - | - | - | - | - | - | - | - | - | - | - | -
VM-WA3 | W | 40 | 0.97959 | 31.5038 | - | - | 14.7 | 14.3 | 14.9 | 15.2 | 15.5 | 15.7 | - | - | - | - | - | - | - | - | - | - | - | -
DLF5-TP53 | S | 12.6 | 0.95652 | 0 | - | - | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | - | - | - | - | - | - | - | - | - | - | - | -
DLF5-TP53 | W | 13.1 | 0.95652 | 0 | - | - | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-ARD2 | S | 21.9 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-ARD2 | W | 26.5 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-PM | S | 66.3 | 0.95425 | 23.4658 | - | - | 15.3 | 16.6 | 17.8 | 17.9 | 18.1 | 18.2 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-PM | W | 86.3 | 0.95425 | 23.4658 | - | - | 15.3 | 16.4 | 16.9 | 17.1 | 17.5 | 17.7 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-WP | S | 125.7 | 0.96753 | 64.4246 | - | - | 89.3 | 93.2 | 96.6 | 97.1 | 98 | 98.5 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-WP | W | 137.2 | 0.96956 | 64.4246 | - | - | 88.7 | 78.5 | 80 | 80.7 | 81.3 | 81.7 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-C186 | S | 9.9 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-C186 | W | 11.2 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
VM-WA1 | S | 37.7 | 0.94611 | 31.5038 | - | - | 16.7 | 20.5 | 21.8 | 22.8 | 23.4 | 24.5 | - | - | - | - | - | - | - | - | - | - | - | -
VM-WA1 | W | 40 | 0.94839 | 31.5038 | - | - | 15.5 | 15.1 | 15.8 | 16 | 16.3 | 16.6 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-C196 | S | 9.9 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-C196 | W | 11.2 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
FR-WP2 | S | 80 | 0.92105 | 82.8365 | - | - | 15.2 | 16.4 | 17.2 | 17.4 | 17.2 | 17.9 | - | - | - | - | - | - | - | - | - | - | - | -
FR-WP2 | W | 85.7 | 0.92105 | 82.8365 | - | - | 15.2 | 12.5 | 12.9 | 13.1 | 13.3 | 13.2 | - | - | - | - | - | - | - | - | - | - | - | -
HB-Q | S | 95.5 | 0.90588 | 15.1917 | - | - | 85 | 88.6 | 89 | 89.3 | 90.4 | 91.3 | - | - | - | - | - | - | - | - | - | - | - | -
HB-Q | W | 108.6 | 0.9057 | 15.1917 | - | - | 85.9 | 63.5 | 64.2 | 65.1 | 66.2 | 66.5 | - | - | - | - | - | - | - | - | - | - | - | -
MG-AP | S | 91.5 | 0.9428 | 17.7017 | - | - | 50.7 | 55.1 | 57.6 | 58.2 | 59.4 | 60.7 | - | - | - | - | - | - | - | - | - | - | - | -
MG-AP | W | 91.5 | 0.94466 | 17.7017 | - | - | 50.6 | 43.6 | 44.6 | 45.7 | 47.1 | 48.4 | - | - | - | - | - | - | - | - | - | - | - | -
JA-WP | S | 47.4 | 0 | 93.4642 | - | - | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | - | - | - | - | - | - | - | - | - | - | - | -
JA-WP | W | 57.2 | 0 | 93.4642 | - | - | 0.5 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | - | - | - | - | - | - | - | - | - | - | - | -
SK-EW | S | 86.3 | 0.95444 | 18.5026 | - | - | 41.7 | 45.9 | 48.3 | 49.4 | 50.9 | 52.4 | - | - | - | - | - | - | - | - | - | - | - | -
SK-EW | W | 91.5 | 0.95402 | 18.5026 | - | - | 43.5 | 38.6 | 40 | 41.4 | 42.6 | 44 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-VM3 | S | 120 | 0.94149 | 20.6709 | - | - | 37.6 | 40.2 | 45.7 | 47.3 | 48.8 | 50.6 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-VM3 | W | 129.7 | 0.97849 | 20.6709 | - | - | 37.2 | 33.2 | 34.6 | 35.5 | 36.2 | 36.8 | - | - | - | - | - | - | - | - | - | - | - | -
VM-LQ1 | S | 76.6 | 0.95184 | 26.1277 | - | - | 35.3 | 36.5 | 39.4 | 40.6 | 41.9 | 43.5 | - | - | - | - | - | - | - | - | - | - | - | -
VM-LQ1 | W | 86.9 | 0.95455 | 26.1277 | - | - | 35.2 | 29.8 | 32.2 | 32.8 | 33.9 | 34.8 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF3 | S | 87.5 | 0.97083 | 0 | - | - | 24 | 26.2 | 27.4 | 28.5 | 29.4 | 30.2 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF3 | W | 87.5 | 0.97107 | 0 | - | - | 24.2 | 22.8 | 23.8 | 24.4 | 25.2 | 25.8 | - | - | - | - | - | - | - | - | - | - | - | -
K-CL | S | 91.5 | 0.94499 | 17.7292 | - | - | 50.9 | 49.5 | 50.3 | 50.7 | 50.3 | 51 | - | - | - | - | - | - | - | - | - | - | - | -
K-CL | W | 105.7 | 0.9451 | 17.7292 | - | - | 51 | 37.7 | 38.7 | 38.5 | 39.3 | 39.6 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-R134 | S | 19.1 | 0.9913 | 1.9222 | - | - | 11.5 | 12.8 | 15 | 16.4 | 16.6 | 16.7 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-R134 | W | 20.7 | 0.98333 | 1.9222 | - | - | 12 | 12.5 | 14 | 14.5 | 14.6 | 14.7 | - | - | - | - | - | - | - | - | - | - | - | -
WP-MP3 | S | 83.9 | 0.93824 | 104.7639 | - | - | 42.1 | 42.7 | 44.5 | 44.6 | 44.8 | 45.2 | - | - | - | - | - | - | - | - | - | - | - | -
WP-MP3 | W | 91.5 | 0.9378 | 104.7639 | - | - | 41.8 | 31.8 | 32.5 | 32.5 | 32.7 | 33 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-F182 | S | 12 | 1 | 1.3729 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-F182 | W | 12.6 | 1 | 1.3729 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-JA1 | S | 145.2 | 0.94949 | 29.0396 | - | - | 49.5 | 53.2 | 60.7 | 62.8 | 64.7 | 67.1 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-JA1 | W | 153.2 | 0.9828 | 29.0396 | - | - | 46.5 | 42.8 | 44.1 | 44.9 | 45.9 | 47.6 | - | - | - | - | - | - | - | - | - | - | - | -
E-PM | S | 74.3 | 0.93103 | 31.6462 | - | - | 14.5 | 15.7 | 16.8 | 16.8 | 16.9 | 16.9 | - | - | - | - | - | - | - | - | - | - | - | -
E-PM | W | 91.5 | 0.92466 | 31.6462 | - | - | 14.6 | 15.4 | 15.8 | 16 | 16.2 | 16.3 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-AP | S | 101.7 | 0.95377 | 0.481 | - | - | 82.2 | 89.7 | 95 | 96.5 | 98 | 99.6 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-AP | W | 109.7 | 0.95411 | 0.481 | - | - | 82.8 | 70.6 | 73.1 | 74.3 | 75.8 | 76.8 | - | - | - | - | - | - | - | - | - | - | - | -
L-Q | S | 95.4 | 0.95342 | 16.3039 | - | - | 64.4 | 67.7 | 67.8 | 67.9 | 68.3 | 68.9 | - | - | - | - | - | - | - | - | - | - | - | -
L-Q | W | 108.6 | 0.96327 | 16.3039 | - | - | 59.9 | 49.5 | 50.6 | 51.6 | 52.5 | 53.3 | - | - | - | - | - | - | - | - | - | - | - | -
DLF64-TP278 | S | 12.6 | 0.97059 | 0 | - | - | 6.8 | 6.9 | 6.9 | 6.9 | 6.8 | 6.8 | - | - | - | - | - | - | - | - | - | - | - | -
DLF64-TP278 | W | 13.1 | 0.95652 | 0 | - | - | 6.9 | 6.8 | 6.9 | 6.8 | 6.8 | 6.9 | - | - | - | - | - | - | - | - | - | - | - | -
WP-MP2 | S | 80 | 0.93602 | 104.7639 | - | - | 42.2 | 42.8 | 44.7 | 44.8 | 44.9 | 45.2 | - | - | - | - | - | - | - | - | - | - | - | -
WP-MP2 | W | 85.7 | 0.93795 | 104.7639 | - | - | 41.9 | 31.9 | 32.6 | 32.6 | 32.8 | 33.1 | - | - | - | - | - | - | - | - | - | - | - | -
VM-BQ3 | S | 125.7 | 0.95565 | 21.7111 | - | - | 45.1 | 50.8 | 54.3 | 55.3 | 56.2 | 57.6 | - | - | - | - | - | - | - | - | - | - | - | -
VM-BQ3 | W | 128 | 0.95711 | 21.7111 | - | - | 44.3 | 40.4 | 41.6 | 42.8 | 43.7 | 44.3 | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-L | S | 106.9 | 0.89941 | 1.1122 | 12.9938 | 1.5 | 119.3 | 122.6 | 123.2 | 123.7 | 124.9 | 126.2 | 14.69% | 15.7 | 216.0679 | 230.3714 | 242.7194 | 273.3929 | 309.0444 | 25 | 26 | 26.5 | 28 | 29.5
TSTS-L | W | 108.6 | 0.91045 | 1.1122 | 12.9938 | 2.5 | 113.9 | 85.4 | 87 | 88.7 | 90.5 | 91.7 | - | - | - | - | - | - | - | - | - | - | - | -
WP-MP1 | S | 78.3 | 0.93824 | 104.7639 | - | - | 42.1 | 42.7 | 44.6 | 44.7 | 44.8 | 45.3 | - | - | - | - | - | - | - | - | - | - | - | -
WP-MP1 | W | 84.6 | 0.94019 | 104.7639 | - | - | 41.8 | 31.9 | 32.5 | 32.6 | 32.7 | 33.1 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-JA3 | S | 114.9 | 0.95506 | 29.0396 | - | - | 44.5 | 47.9 | 54.6 | 56.5 | 58.2 | 60.4 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-JA3 | W | 121.2 | 0.98853 | 29.0396 | - | - | 43.6 | 40.1 | 41.4 | 42.1 | 42.7 | 43.1 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-R135 | S | 21.5 | 0.98477 | 1.9222 | 8.0021 | - | 19.7 | 21.8 | 25.6 | 27.9 | 28.3 | 28.4 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-R135 | W | 24.7 | 0.98529 | 1.9222 | 8.0021 | - | 20.4 | 21.2 | 23.8 | 24.7 | 24.9 | 25 | - | - | - | - | - | - | - | - | - | - | - | -
JA-LQ2 | S | 76.6 | 0.90814 | 34.4965 | - | - | 38.1 | 42.2 | 47.7 | 50.6 | 52.5 | 54.6 | - | - | - | - | - | - | - | - | - | - | - | -
JA-LQ2 | W | 86.9 | 0.91053 | 34.4965 | - | - | 38 | 31 | 33.4 | 35.4 | 36.6 | 37.6 | - | - | - | - | - | - | - | - | - | - | - | -
RD-EB | S | 65.2 | 0.99031 | 11.3272 | - | - | 51.6 | 53.8 | 53.7 | 53.8 | 54.6 | 54.7 | - | - | - | - | - | - | - | - | - | - | - | -
RD-EB | W | 77.2 | 0.98986 | 11.3272 | - | - | 49.3 | 39.4 | 39.7 | 40.2 | 40.8 | 41.1 | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-RD | S | 80 | 0.95991 | 11.3272 | 22.6 | 0.5 | 92.3 | 94.7 | 95.1 | 95.3 | 96.7 | 97.6 | 18.38% | 14.7 | 26.6317 | 27.8801 | 28.583 | 33.5168 | 36.6865 | 3.5 | 3.5 | 3.5 | 4 | 4
SVTS-RD | W | 97.2 | 0.95916 | 11.3272 | 22.6 | 2 | 90.6 | 67.1 | 68 | 68.9 | 70.2 | 70.7 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-AR | S | 94.3 | 0.92262 | 12.6295 | - | - | 84 | 86.4 | 88.9 | 92.8 | 95.1 | 95.7 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-AR | W | 123.5 | 0.92133 | 12.6295 | - | - | 83.9 | 74.4 | 78 | 82.3 | 83.1 | 84.3 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-VM2 | S | 144 | 0.97447 | 20.6709 | - | - | 23.5 | 24.4 | 26 | 26.8 | 27.5 | 28.4 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-VM2 | W | 155.5 | 0.97863 | 20.6709 | - | - | 23.4 | 21 | 21.9 | 22.4 | 22.8 | 23.2 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-FB | S | 88 | 0.95062 | 12.7479 | - | - | 64.8 | 78.7 | 89.2 | 95 | 100.7 | 106 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-FB | W | 112 | 0.94784 | 12.7479 | - | - | 67.1 | 78.5 | 85.3 | 90.9 | 96.4 | 100.9 | - | - | - | - | - | - | - | - | - | - | - | -
BC-AR | S | 84.6 | 0.91974 | 57.0044 | - | - | 46.1 | 48.7 | 50.4 | 53.9 | 55.5 | 55.3 | - | - | - | - | - | - | - | - | - | - | - | -
BC-AR | W | 91.4 | 0.91991 | 57.0044 | - | - | 46.2 | 43.4 | 46 | 49.7 | 50.1 | 50.6 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-RP125 | S | 9 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-RP125 | W | 9.7 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-MG | S | 100.6 | 0.95278 | 17.2207 | - | - | 82.6 | 89.4 | 95.2 | 96 | 97.5 | 99.1 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-MG | W | 115.5 | 0.95411 | 17.2207 | - | - | 82.8 | 70.6 | 72.8 | 73.9 | 75.5 | 76.7 | - | - | - | - | - | - | - | - | - | - | - | -
VM-JA | S | 91.5 | 0.96825 | 49.7105 | - | - | 50.4 | 54.5 | 62.6 | 64.7 | 66.4 | 68.9 | - | - | - | - | - | - | - | - | - | - | - | -
VM-JA | W | 98.3 | 0.99798 | 49.7105 | - | - | 49.5 | 46.7 | 47.8 | 48.2 | 48.7 | 49.7 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BK185 | S | 10.5 | 1 | 54.4501 | - | - | 7.6 | 7.6 | 8.3 | 8.6 | 1.3 | 1.7 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BK185 | W | 10.5 | 1 | 54.4501 | - | - | 7.6 | 7.9 | 8.4 | 8.6 | 1.4 | 1.4 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-SK | S | 83.5 | 0.98134 | 18.5026 | - | - | 64.3 | 68.6 | 71 | 73.2 | 74.7 | 76.9 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-SK | W | 93.2 | 0.97885 | 18.5026 | - | - | 66.2 | 62.8 | 64.8 | 66.5 | 68.8 | 70.3 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-C191 | S | 9.9 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-C191 | W | 11.2 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-VM1 | S | 130.3 | 0.99363 | 20.6709 | - | - | 31.4 | 32.8 | 34.9 | 35.9 | 36.9 | 38.2 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-VM1 | W | 164.6 | 0.99363 | 20.6709 | - | - | 31.4 | 28.1 | 29.3 | 30 | 30.6 | 31.1 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-NR | S | 135.5 | 0.92829 | 19.879 | 4.001 | - | 128.3 | 134.1 | 142 | 166.7 | 170.8 | 175.1 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-NR | W | 137.2 | 0.92938 | 19.879 | 4.001 | - | 123.2 | 109.5 | 135.4 | 139.1 | 142.7 | 146.6 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-F189 | S | 14.1 | 0.98701 | 1.3729 | 1.6 | 2.5 | 15.4 | 14.2 | 14.7 | 3 | 3 | 3 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-F189 | W | 14.8 | 0.98701 | 1.3729 | 1.6 | 2 | 15.4 | 16.7 | 3 | 3.1 | 3.1 | 3.1 | 12.84% | 1.9 | 6.9594 | 1.0173 | 0 | 0 | 0 | 7.5 | 2 | 0 | 0 | 0
RTS-TK | S | 116.6 | 0.96388 | 18.1573 | - | - | 52.6 | 54.5 | 56 | 58.1 | 59 | 59.8 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-TK | W | 122.3 | 0.96381 | 18.1573 | - | - | 52.5 | 46.7 | 48.5 | 50.4 | 51.1 | 51.6 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-E | S | 66.3 | 0.94231 | 8.1803 | - | - | 15.6 | 17 | 18.3 | 18.4 | 18.6 | 18.7 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-E | W | 86.3 | 0.93631 | 8.1803 | - | - | 15.7 | 16.8 | 17.3 | 17.6 | 17.9 | 18.2 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-CL | S | 117.2 | 0.96806 | 17.7292 | - | - | 90.8 | 91 | 92.6 | 92.5 | 93.5 | 93.9 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-CL | W | 126.3 | 0.9692 | 17.7292 | - | - | 90.9 | 66.7 | 67.4 | 68.2 | 69 | 70.2 | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-EB | S | 94.9 | 0.95243 | 0 | - | - | 92.5 | 94.6 | 95.1 | 95.3 | 96.6 | 97.7 | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-EB | W | 101.7 | 0.95264 | 0 | - | - | 90.8 | 67 | 67.6 | 68.7 | 70.1 | 70.6 | - | - | - | - | - | - | - | - | - | - | - | -

## ZSS Aug Sum
Zone Substation | Season | Station N Import Rating (MVA) | Station N-1 Import Rating (MVA) | Station Nameplate Rating (MVA) | Station Power Factor at Maximum Demand | Embedded Generation Capacity (MVA) | Load Transfer Capability (MVA) | Hours load is > 95% of Maximum Demand (Hrs) | Actual Maximum Demand (MVA) | 10% POE |  |  |  |  | 50% POE |  |  |  |  | 50% POE load above N-1 Import Rating (%) | 50% POE load above N-1 Import Rating (MVA) | 10% POE | [14 empty] | 50% POE | [14 empty] | Weighted POE
[10 empty] | Forecast Maximum Demand (MVA) |  |  |  |  | Forecast Maximum Demand (MVA) | [6 empty] | Energy at Risk (MWh) |  |  |  |  | Expected Energy at Risk (MWh) |  |  |  |  | Hours at Risk (Hrs) |  |  |  |  | Energy at Risk (MWh) |  |  |  |  | Expected Energy at Risk (MWh) |  |  |  |  | Hours at Risk (Hrs) |  |  |  |  | Energy at Risk (MWh) |  |  |  |  | Expected Energy at Risk (MWh)
[5 empty] | 2024 | 2024 | 2024 | 2024 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2025 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029
AP | S | 70 | 70 | 87 | 0.98 | 3.952 | 23.2441 | 14.16 | 47.75 | 60.45 | 62.88 | 63.88 | 65.38 | 66.69 | 51.9 | 53.95 | 54.62 | 55.81 | 56.94 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AP | W | 71.3 | 71.3 | 87 | 1 | 3.952 | 23.2441 | 14.16 | 36.36 | 43.67 | 44.71 | 46.04 | 47.36 | 48.46 | 41.73 | 42.71 | 43.92 | 45.15 | 46.18 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AR | S | 61.8 | 32.9 | 60 | 0.98 | 3.0682 | 5.8301 | 3.39 | 34.39 | 37.64 | 38.42 | 38.75 | 39.16 | 39.66 | 34.12 | 34.83 | 35.03 | 35.33 | 35.75 | 3.708% | 1.22 | 31.35 | 43.59 | 47.15 | 55.3 | 68.53 | 0.03 | 0.04 | 0.04 | 0.05 | 0.06 | 24 | 27.5 | 29.5 | 30.5 | 33 | 0.98 | 2.32 | 2.54 | 3.4 | 5.24 | 0 | 0 | 0 | 0 | 0 | 2 | 2.5 | 2.5 | 4 | 5.5 | 10.091 | 14.701 | 15.923 | 18.97 | 24.227 | 0.009 | 0.012 | 0.012 | 0.015 | 0.018
AR | W | 67.4 | 35.8 | 60 | 1 | 3.0682 | 5.8301 | 3.39 | 27.07 | 30.37 | 30.92 | 31.22 | 31.79 | 32.18 | 28.83 | 29.29 | 29.59 | 30.06 | 30.47 | - | - | 31.35 | 43.59 | 47.15 | 55.3 | 68.53 | 0.03 | 0.04 | 0.04 | 0.05 | 0.06 | 24 | 27.5 | 29.5 | 30.5 | 33 | 0.98 | 2.32 | 2.54 | 3.4 | 5.24 | 0 | 0 | 0 | 0 | 0 | 2 | 2.5 | 2.5 | 4 | 5.5 | 10.091 | 14.701 | 15.923 | 18.97 | 24.227 | 0.009 | 0.012 | 0.012 | 0.015 | 0.018
B | S | 69.4 | 29 | 54 | 0.99 | 2.2857 | 6.4588 | 9.12 | 41.51 | 47.7334 | 49.4612 | 50.4782 | 51.6811 | 52.6653 | 44.125 | 45.7222 | 46.6623 | 47.7743 | 48.6841 | 52.16% | 15.125 | 1809.5654 | 2565.4179 | 3156.878 | 3983.9893 | 4806.7646 | 7.8414 | 11.1168 | 13.6798 | 17.264 | 20.8293 | 494.25 | 724.5 | 897.5 | 1106.5 | 1307.25 | 866.1806 | 1231.0034 | 1516.4504 | 1934.3386 | 2373.6185 | 3.7534 | 5.3343 | 6.5713 | 8.3821 | 10.2857 | 249.25 | 359 | 450 | 582.5 | 715.25 | 1149.196 | 1631.3278 | 2008.5787 | 2549.2338 | 3103.5624 | 4.9798 | 7.0691 | 8.7038 | 11.0467 | 13.4488
B | W | 75.7 | 32.2 | 54 | 0.99 | 2.2857 | 6.4588 | 9.12 | 25.88 | 36.4082 | 38.1116 | 39.1118 | 40.1433 | 41.1018 | 35.081 | 36.7224 | 37.6861 | 38.68 | 39.6035 | 8.947% | 2.881 | 1809.5654 | 2565.4179 | 3156.878 | 3983.9893 | 4806.7646 | 7.8414 | 11.1168 | 13.6798 | 17.264 | 20.8293 | 494.25 | 724.5 | 897.5 | 1106.5 | 1307.25 | 866.1806 | 1231.0034 | 1516.4504 | 1934.3386 | 2373.6185 | 3.7534 | 5.3343 | 6.5713 | 8.3821 | 10.2857 | 249.25 | 359 | 450 | 582.5 | 715.25 | 1149.196 | 1631.3278 | 2008.5787 | 2549.2338 | 3103.5624 | 4.9798 | 7.0691 | 8.7038 | 11.0467 | 13.4488
BC | S | 109.6 | 71.6 | 87 | 0.99 | 2.9594 | 12.3651 | 4.08 | 42.55 | 55.33 | 56.86 | 60.4 | 61.63 | 61.7 | 45.06 | 46.16 | 49.5 | 50.82 | 50.9 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BC | W | 123.8 | 70.6 | 87 | 1 | 2.9594 | 12.3651 | 4.08 | 38.06 | 43.98 | 46.27 | 49.24 | 49.99 | 50.16 | 40.4 | 42.84 | 45.63 | 46.18 | 46.36 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BK | S | 27.2 | 27.2 | 33 | 0.99 | 3.3666 | 0 | 2.66 | 14.43 | 18.3921 | 19.9846 | 20.5474 | 0 | 0 | 15.4697 | 16.8092 | 17.2825 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BK | W | 28.6 | 28.6 | 33 | 1 | 3.3666 | 0 | 2.66 | 15.19 | 16.3719 | 17.4365 | 18.1086 | 9.3393 | 0.2527 | 15.2512 | 16.2429 | 16.869 | 8.7 | 0.2354 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BQ | S | 132.3 | 64.9 | 110 | 0.99 | 4.2415 | 10.4408 | 25.87 | 79.42 | 91.9614 | 97.5425 | 98.0384 | 98.073 | 138.4553 | 80.6679 | 85.5636 | 85.9986 | 86.0289 | 121.452 | 24.3% | 15.7679 | 2233.1153 | 5180.0094 | 6223.7673 | 6598.6337 | 122598.187 | 9.6768 | 22.4467 | 26.9697 | 28.5941 | 531.2588 | 525 | 1032.5 | 1187 | 1239 | 6677 | 180.2191 | 464.4418 | 503.5373 | 507.9423 | 39896.184 | 0.78095 | 2.0126 | 2.182 | 2.2011 | 172.8835 | 44.25 | 99.5 | 107.75 | 109 | 4067 | 796.088 | 1879.1121 | 2219.6063 | 2335.1497 | 64706.7849 | 3.4497 | 8.1428 | 9.6183 | 10.119 | 280.3961
BQ | W | 147.3 | 72.3 | 110 | 1 | 4.2415 | 10.4408 | 25.87 | 63.68 | 91.5697 | 95.9863 | 97.4943 | 98.0369 | 142.5504 | 72.6743 | 76.1796 | 77.3764 | 77.8071 | 113.1352 | 0.5178% | 0.37434 | 2233.1153 | 5180.0094 | 6223.7673 | 6598.6337 | 122598.187 | 9.6768 | 22.4467 | 26.9697 | 28.5941 | 531.2588 | 525 | 1032.5 | 1187 | 1239 | 6677 | 180.2191 | 464.4418 | 503.5373 | 507.9423 | 39896.184 | 0.78095 | 2.0126 | 2.182 | 2.2011 | 172.8835 | 44.25 | 99.5 | 107.75 | 109 | 4067 | 796.088 | 1879.1121 | 2219.6063 | 2335.1497 | 64706.7849 | 3.4497 | 8.1428 | 9.6183 | 10.119 | 280.3961
CL | S | 106.5 | 71.7 | 87 | 0.98 | 5.5805 | 0.85737 | 6.24 | 49.03 | 54.32 | 54.94 | 55.14 | 55.14 | 55.6 | 47.81 | 48.65 | 48.6 | 48.57 | 48.95 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CL | W | 120.2 | 70.7 | 87 | 1 | 5.5805 | 0.85737 | 6.24 | 34.74 | 39.65 | 40.35 | 40.54 | 41.04 | 41.49 | 37.03 | 37.72 | 37.93 | 38.3 | 38.77 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CW | S | 65.3 | 34.4 | 54 | 0.99 | 2.6188 | 0.7621 | 10.06 | 25.09 | 29.535 | 32.2106 | 50.0557 | 51.1811 | 52.272 | 25.83 | 28.19 | 43.96 | 44.95 | 45.92 | - | - | 0 | 0 | 1030.3101 | 1364.3582 | 1734.4436 | 0 | 0 | 4.4647 | 5.9122 | 7.5159 | 0 | 0 | 344.25 | 424.5 | 501 | 0 | 0 | 173.248 | 255.1531 | 362.7165 | 0 | 0 | 0.75074 | 1.1057 | 1.5718 | 0 | 0 | 79.75 | 118.5 | 160 | 0 | 0 | 430.3666 | 587.9146 | 774.2347 | 0 | 0 | 1.8649 | 2.5476 | 3.355
CW | W | 73.4 | 38.2 | 54 | 1 | 2.6188 | 0.7621 | 10.06 | 22.47 | 25.5118 | 37.3712 | 48.4558 | 49.4796 | 50.4259 | 24.29 | 43.7 | 44.61 | 45.57 | 46.34 | - | - | 0 | 0 | 1030.3101 | 1364.3582 | 1734.4436 | 0 | 0 | 4.4647 | 5.9122 | 7.5159 | 0 | 0 | 344.25 | 424.5 | 501 | 0 | 0 | 173.248 | 255.1531 | 362.7165 | 0 | 0 | 0.75074 | 1.1057 | 1.5718 | 0 | 0 | 79.75 | 118.5 | 160 | 0 | 0 | 430.3666 | 587.9146 | 774.2347 | 0 | 0 | 1.8649 | 2.5476 | 3.355
DA | S | 43.8 | 29.2 | 37 | 0.98 | 0.8564 | 9.3637 | 4.53 | 31.23 | 37.53 | 40.31 | 41.41 | 42.68 | 43.93 | 33.83 | 36.06 | 37.07 | 38.23 | 39.26 | 15.86% | 4.63 | 323.59 | 804.36 | 1081.08 | 1490.98 | 1984.89 | 0.44 | 1.08 | 1.46 | 2.01 | 2.67 | 152 | 277.5 | 351 | 451.5 | 585.5 | 45.43 | 186.58 | 295.53 | 466.6 | 661.77 | 0.06 | 0.25 | 0.4 | 0.63 | 0.89 | 39 | 107.5 | 149 | 199.5 | 252 | 128.878 | 371.914 | 531.195 | 773.914 | 1058.706 | 0.174 | 0.499 | 0.718 | 1.044 | 1.424
DA | W | 48.9 | 32.6 | 37 | 0.98 | 0.8564 | 9.3637 | 4.53 | 23.2 | 32.47 | 33.52 | 34.58 | 35.69 | 36.69 | 27.65 | 28.83 | 29.73 | 30.7 | 31.54 | - | - | 323.59 | 804.36 | 1081.08 | 1490.98 | 1984.89 | 0.44 | 1.08 | 1.46 | 2.01 | 2.67 | 152 | 277.5 | 351 | 451.5 | 585.5 | 45.43 | 186.58 | 295.53 | 466.6 | 661.77 | 0.06 | 0.25 | 0.4 | 0.63 | 0.89 | 39 | 107.5 | 149 | 199.5 | 252 | 128.878 | 371.914 | 531.195 | 773.914 | 1058.706 | 0.174 | 0.499 | 0.718 | 1.044 | 1.424
E | S | 10.9 | 0 | 46 | 1 | 0.208 | 3.178 | 2.2 | 1.27 | 1.6983 | 1.887 | 2.0202 | 2.1645 | 2.3088 | 1.53 | 1.7 | 1.82 | 1.95 | 2.08 | 100% | 1.53 | 6618.2736 | 7365.6108 | 7941.0366 | 8512.5297 | 9060.076 | 59.9153 | 66.6814 | 71.8929 | 77.067 | 82.0234 | 8760 | 8760 | 8760 | 8760 | 8760 | 5991.5332 | 6668.1441 | 7189.2914 | 7706.6997 | 8202.3382 | 66.1827 | 73.6561 | 79.4104 | 85.1253 | 90.6008 | 8760 | 8760 | 8760 | 8760 | 8760 | 6179.5553 | 6877.3841 | 7414.815 | 7948.4487 | 8459.6595 | 64.3025 | 71.5637 | 77.1551 | 82.7078 | 88.0275
E | W | 12.1 | 0 | 46 | 1 | 0.208 | 3.178 | 2.2 | 0.94 | 1.6335 | 1.8205 | 1.9745 | 2.1175 | 2.2495 | 1.485 | 1.655 | 1.795 | 1.925 | 2.045 | 100% | 1.485 | 6618.2736 | 7365.6108 | 7941.0366 | 8512.5297 | 9060.076 | 59.9153 | 66.6814 | 71.8929 | 77.067 | 82.0234 | 8760 | 8760 | 8760 | 8760 | 8760 | 5991.5332 | 6668.1441 | 7189.2914 | 7706.6997 | 8202.3382 | 66.1827 | 73.6561 | 79.4104 | 85.1253 | 90.6008 | 8760 | 8760 | 8760 | 8760 | 8760 | 6179.5553 | 6877.3841 | 7414.815 | 7948.4487 | 8459.6595 | 64.3025 | 71.5637 | 77.1551 | 82.7078 | 88.0275
F | S | 30.2 | 13.5 | 23 | 1 | 3.5254 | 1.6118 | 1.37 | 13.94 | 16.0398 | 16.5325 | 0 | 0 | 0 | 14.07 | 14.5022 | 0 | 0 | 0 | 4.222% | 0.57003 | 17.9403 | 20.1946 | 0 | 0 | 0 | 0.11661 | 0.13126 | 0 | 0 | 0 | 25.5 | 19.75 | 0 | 0 | 0 | 0.98972 | 1.0735 | 0 | 0 | 0 | 0.0064332 | 0.0069778 | 0 | 0 | 0 | 3.75 | 2.5 | 0 | 0 | 0 | 6.0749 | 6.8098 | 0 | 0 | 0 | 0.039487 | 0.044264 | 0 | 0 | 0
F | W | 35.2 | 15.3 | 23 | 1 | 3.5254 | 1.6118 | 1.37 | 15.13 | 16.7145 | 9.0248 | 0.83573 | 0.64125 | 0.47831 | 15.9186 | 8.595 | 0.79593 | 0.61071 | 0.45553 | 4.043% | 0.6186 | 17.9403 | 20.1946 | 0 | 0 | 0 | 0.11661 | 0.13126 | 0 | 0 | 0 | 25.5 | 19.75 | 0 | 0 | 0 | 0.98972 | 1.0735 | 0 | 0 | 0 | 0.0064332 | 0.0069778 | 0 | 0 | 0 | 3.75 | 2.5 | 0 | 0 | 0 | 6.0749 | 6.8098 | 0 | 0 | 0 | 0.039487 | 0.044264 | 0 | 0 | 0
FB | S | 113.7 | 63.7 | 90 | 0.98 | 0.65312 | 5.1251 | 5.36 | 27.94 | 32.21 | 36.19 | 39.22 | 42.03 | 44.77 | 28.14 | 31.42 | 33.83 | 36.22 | 38.52 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FB | W | 125.4 | 62 | 90 | 0.99 | 0.65312 | 5.1251 | 5.36 | 24.74 | 34.35 | 37.36 | 40.07 | 42.76 | 45.23 | 30.35 | 33.02 | 35.41 | 37.78 | 39.97 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FR | S | 109.6 | 61.3 | 90 | 0.97 | 0.30334 | 0 | 6.94 | 40.22 | 43.76 | 47.65 | 48.78 | 48.84 | 48.78 | 38.93 | 43.12 | 44.04 | 44.04 | 43.95 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FR | W | 122.2 | 72.1 | 90 | 0.99 | 0.30334 | 0 | 6.94 | 27.77 | 34.54 | 36.32 | 36.55 | 36.51 | 36.36 | 30.93 | 33.55 | 33.92 | 33.83 | 33.7 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JA | S | 203.5 | 127.8 | 165 | 0.99 | 0.7355 | 61.5588 | 6.77 | 103.7 | 126.98 | 141.73 | 146.89 | 151.99 | 156.88 | 106.69 | 119.88 | 124.27 | 128.68 | 132.72 | - | - | 0 | 90.1 | 262.53 | 521.89 | 868.34 | 0 | 0.11 | 0.33 | 0.66 | 1.1 | 0 | 25 | 47.5 | 72 | 95.5 | 0 | 0 | 0 | 0 | 7.21 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0 | 4 | 0 | 27.03 | 78.759 | 156.567 | 265.549 | 0 | 0.033 | 0.099 | 0.198 | 0.337
JA | W | 202.7 | 127.4 | 165 | 1 | 0.7355 | 61.5588 | 6.77 | 73.78 | 118.03 | 130.85 | 135.52 | 140.31 | 144.59 | 89.12 | 97.42 | 100.89 | 104.35 | 107.51 | - | - | 0 | 90.1 | 262.53 | 521.89 | 868.34 | 0 | 0.11 | 0.33 | 0.66 | 1.1 | 0 | 25 | 47.5 | 72 | 95.5 | 0 | 0 | 0 | 0 | 7.21 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0 | 4 | 0 | 27.03 | 78.759 | 156.567 | 265.549 | 0 | 0.033 | 0.099 | 0.198 | 0.337
L | S | 76.6 | 32.1 | 60 | 0.98 | 10.1513 | 12.2317 | 1.58 | 43.95 | 47.37 | 47.86 | 48.31 | 48.89 | 49.36 | 43.46 | 43.86 | 44.24 | 44.78 | 45.17 | 35.39% | 11.36 | 432.34 | 479.12 | 586.08 | 807.18 | 1083.19 | 0.42 | 0.47 | 0.57 | 0.79 | 1.05 | 100.5 | 105.5 | 127.5 | 180 | 250 | 189.57 | 215.13 | 264.71 | 364.92 | 472.61 | 0.18 | 0.21 | 0.26 | 0.35 | 0.46 | 57 | 62.5 | 71 | 93 | 119 | 262.401 | 294.327 | 361.121 | 497.598 | 655.784 | 0.252 | 0.288 | 0.353 | 0.482 | 0.637
L | W | 87.6 | 36.4 | 60 | 1 | 10.1513 | 12.2317 | 1.58 | 30.59 | 33.46 | 33.77 | 34.32 | 35.01 | 35.32 | 31.47 | 31.73 | 32.23 | 32.84 | 33.19 | - | - | 432.34 | 479.12 | 586.08 | 807.18 | 1083.19 | 0.42 | 0.47 | 0.57 | 0.79 | 1.05 | 100.5 | 105.5 | 127.5 | 180 | 250 | 189.57 | 215.13 | 264.71 | 364.92 | 472.61 | 0.18 | 0.21 | 0.26 | 0.35 | 0.46 | 57 | 62.5 | 71 | 93 | 119 | 262.401 | 294.327 | 361.121 | 497.598 | 655.784 | 0.252 | 0.288 | 0.353 | 0.482 | 0.637
LQ | S | 131.8 | 131.8 | 180 | 0.98 | 0.10104 | 21.5294 | 5.56 | 68.77 | 83.65 | 90.45 | 93.5 | 96.65 | 99.54 | 72.59 | 79.52 | 82.2 | 85 | 87.58 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LQ | W | 142.2 | 142.2 | 180 | 0.99 | 0.10104 | 21.5294 | 5.56 | 46.89 | 65.12 | 69.24 | 71.5 | 73.93 | 76.13 | 57.77 | 61.84 | 63.9 | 66.06 | 67.94 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MG | S | 64.3 | 64.3 | 87 | 0.99 | 1.0185 | 9.6787 | 10.86 | 31.99 | 37.15 | 40.04 | 40.25 | 40.43 | 40.56 | 34.14 | 37.26 | 37.49 | 37.71 | 37.95 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MG | W | 75 | 75 | 87 | 1 | 1.0185 | 9.6787 | 10.86 | 22.37 | 28.77 | 29.62 | 29.71 | 29.7 | 29.62 | 26.99 | 28.09 | 28.15 | 28.24 | 28.24 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MP | S | 202.3 | 124 | 165 | 0.98 | 1.0931 | 4.001 | 7.18 | 80.45 | 92.12 | 96.01 | 96.24 | 96.55 | 96.85 | 84.29 | 88.02 | 88.13 | 88.48 | 88.7 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MP | W | 201.5 | 123.4 | 165 | 1 | 1.0931 | 4.001 | 7.18 | 54.44 | 74.65 | 76.27 | 76.49 | 76.95 | 77.11 | 63.18 | 64.77 | 64.98 | 65.32 | 65.43 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NC | S | 72.8 | 31.9 | 60 | 0.99 | 11.5341 | 0 | 2.74 | 31.75 | 37.4 | 38.1 | 38.95 | 39.9 | 40.74 | 33.94 | 34.68 | 35.38 | 36.29 | 37.17 | 6.395% | 2.04 | 46.51 | 77.97 | 133.25 | 210.32 | 299.67 | 0.04 | 0.06 | 0.11 | 0.17 | 0.25 | 25.5 | 38.5 | 54 | 76 | 101 | 3.44 | 8.16 | 19.35 | 40.02 | 72.63 | 0 | 0.01 | 0.02 | 0.03 | 0.06 | 3 | 8.5 | 16 | 26 | 42 | 16.361 | 29.103 | 53.52 | 91.11 | 140.742 | 0.012 | 0.025 | 0.047 | 0.072 | 0.117
NC | W | 83.7 | 40.2 | 60 | 1 | 11.5341 | 0 | 2.74 | 31.24 | 32.56 | 33.25 | 34.12 | 35.07 | 35.76 | 30.86 | 31.51 | 32.3 | 33.19 | 33.83 | - | - | 46.51 | 77.97 | 133.25 | 210.32 | 299.67 | 0.04 | 0.06 | 0.11 | 0.17 | 0.25 | 25.5 | 38.5 | 54 | 76 | 101 | 3.44 | 8.16 | 19.35 | 40.02 | 72.63 | 0 | 0.01 | 0.02 | 0.03 | 0.06 | 3 | 8.5 | 16 | 26 | 42 | 16.361 | 29.103 | 53.52 | 91.11 | 140.742 | 0.012 | 0.025 | 0.047 | 0.072 | 0.117
NR | S | 97.1 | 65.2 | 83 | 0.99 | 4.7334 | 4.6679 | 6.68 | 52.02 | 59.29 | 61.43 | 62.57 | 63.85 | 64.87 | 53.92 | 55.88 | 56.66 | 57.77 | 58.79 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NR | W | 106.6 | 71.7 | 83 | 1 | 4.7334 | 4.6679 | 6.68 | 41.98 | 49.06 | 50.37 | 51.51 | 52.78 | 53.78 | 46.51 | 47.81 | 48.95 | 50.19 | 51.21 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PM | S | 34.8 | 17.4 | 26 | 0.97 | 1.6196 | 4.6298 | 14.29 | 13.87 | 18.41 | 19.57 | 19.73 | 19.93 | 20.13 | 14.88 | 15.9 | 15.87 | 15.92 | 15.95 | - | - | 0.8 | 10.52 | 13.4 | 18.23 | 25.36 | 0 | 0.03 | 0.03 | 0.05 | 0.06 | 7 | 21 | 25.5 | 31.5 | 43.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24 | 3.156 | 4.02 | 5.469 | 7.608 | 0 | 0.009 | 0.009 | 0.015 | 0.018
PM | W | 39.4 | 19.7 | 26 | 0.98 | 1.6196 | 4.6298 | 14.29 | 11.39 | 15.75 | 16.18 | 16.34 | 16.61 | 16.72 | 14.63 | 14.99 | 15.14 | 15.36 | 15.46 | - | - | 0.8 | 10.52 | 13.4 | 18.23 | 25.36 | 0 | 0.03 | 0.03 | 0.05 | 0.06 | 7 | 21 | 25.5 | 31.5 | 43.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24 | 3.156 | 4.02 | 5.469 | 7.608 | 0 | 0.009 | 0.009 | 0.015 | 0.018
Q | S | 54.4 | 27.2 | 60 | 0.98 | 6.8341 | 6.8018 | 2.82 | 36.1 | 44.19 | 44.66 | 44.81 | 45.22 | 45.48 | 39.75 | 40.1 | 40.18 | 40.48 | 40.71 | 46.14% | 12.55 | 1398.91 | 1358.51 | 1186.68 | 1265.54 | 1450.67 | 1.43 | 1.39 | 1.21 | 1.29 | 1.48 | 370.5 | 354 | 279.5 | 291 | 339 | 555.61 | 520.02 | 475.28 | 504.74 | 563.88 | 0.57 | 0.53 | 0.49 | 0.52 | 0.58 | 173.5 | 139.5 | 121 | 123.5 | 139.5 | 808.6 | 771.567 | 688.7 | 732.98 | 829.917 | 0.828 | 0.788 | 0.706 | 0.751 | 0.85
Q | W | 54.4 | 31.5 | 60 | 1 | 6.8341 | 6.8018 | 2.82 | 29.25 | 30.75 | 30.99 | 31.23 | 31.58 | 31.65 | 29.22 | 29.46 | 29.7 | 29.99 | 30.1 | - | - | 1398.91 | 1358.51 | 1186.68 | 1265.54 | 1450.67 | 1.43 | 1.39 | 1.21 | 1.29 | 1.48 | 370.5 | 354 | 279.5 | 291 | 339 | 555.61 | 520.02 | 475.28 | 504.74 | 563.88 | 0.57 | 0.53 | 0.49 | 0.52 | 0.58 | 173.5 | 139.5 | 121 | 123.5 | 139.5 | 808.6 | 771.567 | 688.7 | 732.98 | 829.917 | 0.828 | 0.788 | 0.706 | 0.751 | 0.85
R | S | 49.9 | 30.1 | 39 | 1 | 1.5673 | 7.259 | 5.98 | 29.02 | 35.97 | 41.8 | 45.59 | 46.3 | 46.64 | 31.9 | 37.55 | 41.1 | 41.68 | 41.81 | 5.98% | 1.8 | 125.36 | 750.63 | 1794.54 | 2039.68 | 2124.23 | 0.13 | 0.81 | 1.93 | 2.19 | 2.29 | 63 | 203.5 | 459 | 510.5 | 522.5 | 7.52 | 240.25 | 718.51 | 822.6 | 838.97 | 0.01 | 0.26 | 0.77 | 0.89 | 0.9 | 7 | 102.5 | 219 | 250.5 | 253.5 | 42.872 | 393.364 | 1041.319 | 1187.724 | 1224.548 | 0.046 | 0.425 | 1.118 | 1.28 | 1.317
R | W | 58.9 | 36 | 39 | 1 | 1.5673 | 7.259 | 5.98 | 23.2 | 32.69 | 37.22 | 38.65 | 38.99 | 39.16 | 28.54 | 32.56 | 34.06 | 34.42 | 34.63 | - | - | 125.36 | 750.63 | 1794.54 | 2039.68 | 2124.23 | 0.13 | 0.81 | 1.93 | 2.19 | 2.29 | 63 | 203.5 | 459 | 510.5 | 522.5 | 7.52 | 240.25 | 718.51 | 822.6 | 838.97 | 0.01 | 0.26 | 0.77 | 0.89 | 0.9 | 7 | 102.5 | 219 | 250.5 | 253.5 | 42.872 | 393.364 | 1041.319 | 1187.724 | 1224.548 | 0.046 | 0.425 | 1.118 | 1.28 | 1.317
RD | S | 54.4 | 24.9 | 60 | 0.99 | 7.3274 | 8.4403 | 1.77 | 35.97 | 39.92 | 40 | 40.38 | 40.99 | 41.31 | 36.08 | 36.22 | 36.38 | 36.85 | 37.28 | 44.9% | 11.18 | 578.05 | 654.03 | 821.05 | 1138.28 | 1438.58 | 0.46 | 0.52 | 0.65 | 0.9 | 1.14 | 140.5 | 159 | 202.5 | 295.5 | 389 | 259.55 | 298.36 | 356.05 | 467.85 | 586.19 | 0.2 | 0.24 | 0.28 | 0.37 | 0.46 | 75.5 | 86 | 100.5 | 131.5 | 171 | 355.1 | 405.061 | 495.55 | 668.979 | 841.907 | 0.278 | 0.324 | 0.391 | 0.529 | 0.664
RD | W | 54.4 | 28.7 | 60 | 1 | 7.3274 | 8.4403 | 1.77 | 26.19 | 27.42 | 27.73 | 28.15 | 28.67 | 28.9 | 25.61 | 25.89 | 26.28 | 26.76 | 27 | - | - | 578.05 | 654.03 | 821.05 | 1138.28 | 1438.58 | 0.46 | 0.52 | 0.65 | 0.9 | 1.14 | 140.5 | 159 | 202.5 | 295.5 | 389 | 259.55 | 298.36 | 356.05 | 467.85 | 586.19 | 0.2 | 0.24 | 0.28 | 0.37 | 0.46 | 75.5 | 86 | 100.5 | 131.5 | 171 | 355.1 | 405.061 | 495.55 | 668.979 | 841.907 | 0.278 | 0.324 | 0.391 | 0.529 | 0.664
SB | S | 137.8 | 59.7 | 110 | 0.99 | 0.44308 | 0 | 9.51 | 40.15 | 49.2 | 52 | 53.56 | 55.27 | 56.81 | 43.19 | 45.82 | 47.21 | 48.68 | 50.07 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SB | W | 151 | 63.6 | 110 | 1 | 0.44308 | 0 | 9.51 | 26.77 | 35.26 | 37.15 | 38.33 | 39.53 | 40.64 | 32.27 | 33.76 | 34.84 | 35.96 | 36.96 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SK | S | 105.4 | 63.2 | 87 | 0.98 | 1.3123 | 0 | 12.8 | 41.71 | 54.62 | 56.58 | 58.04 | 59.59 | 61.1 | 45.56 | 47.49 | 48.65 | 49.94 | 51.24 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SK | W | 116.6 | 72.9 | 87 | 1 | 1.3123 | 0 | 12.8 | 32.37 | 39.74 | 41.08 | 42.3 | 43.77 | 44.89 | 37.12 | 38.36 | 39.6 | 40.9 | 41.99 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SO | S | 63.7 | 63.7 | 87 | 0.98 | 0.5412 | 0 | 9.49 | 30.83 | 37.4 | 39.24 | 40.45 | 41.7 | 42.88 | 33.74 | 35.43 | 36.45 | 37.58 | 38.66 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SO | W | 71.7 | 71.7 | 87 | 0.99 | 0.5412 | 0 | 9.49 | 21.27 | 31.28 | 32.61 | 33.58 | 34.67 | 35.57 | 25.61 | 26.62 | 27.46 | 28.36 | 29.14 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TK | S | 110.2 | 52.5 | 87 | 0.98 | 2.9717 | 14.499 | 8.58 | 47.2 | 56.86 | 58.57 | 59.54 | 60.85 | 61.65 | 49.57 | 51.28 | 51.66 | 52.44 | 53.09 | - | - | 11.87 | 29.11 | 38.99 | 60.49 | 75.62 | 0.01 | 0.03 | 0.04 | 0.06 | 0.07 | 9.5 | 20.5 | 23 | 27.5 | 31.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.561 | 8.733 | 11.697 | 18.147 | 22.686 | 0.003 | 0.009 | 0.012 | 0.018 | 0.021
TK | W | 124.6 | 54.7 | 87 | 1 | 2.9717 | 14.499 | 8.58 | 37.29 | 45.74 | 46.92 | 47.85 | 49.14 | 49.82 | 42.4 | 43.4 | 44.29 | 45.34 | 46 | - | - | 11.87 | 29.11 | 38.99 | 60.49 | 75.62 | 0.01 | 0.03 | 0.04 | 0.06 | 0.07 | 9.5 | 20.5 | 23 | 27.5 | 31.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.561 | 8.733 | 11.697 | 18.147 | 22.686 | 0.003 | 0.009 | 0.012 | 0.018 | 0.021
VM | S | 90.96 | 57.88 | 84 | 0.99 | 2.0434 | 12.2698 | 11.65 | 56.7 | 67.45 | 71.11 | 72.28 | 73.62 | 74.97 | 60.46 | 64.03 | 65.21 | 66.52 | 67.7 | 4.457% | 2.58 | 249.47 | 657.83 | 849.67 | 1096.91 | 1382.7 | 38.4 | 193.63 | 283.74 | 413.59 | 579.86 | 83.5 | 160.5 | 187 | 215.5 | 253 | 7.21 | 71.36 | 123.38 | 202.29 | 298.23 | 0.01 | 3.78 | 10.54 | 24.16 | 49.1 | 6 | 39 | 52 | 77 | 98.5 | 79.888 | 247.301 | 341.267 | 470.676 | 623.571 | 11.527 | 60.735 | 92.5 | 140.989 | 208.328
VM | W | 110.1 | 70.22 | 84 | 1 | 2.0434 | 12.2698 | 11.65 | 45.52 | 62.23 | 64.18 | 65.43 | 67.08 | 68.2 | 50.35 | 51.85 | 52.9 | 54.12 | 54.99 | - | - | 249.47 | 657.83 | 849.67 | 1096.91 | 1382.7 | 38.4 | 193.63 | 283.74 | 413.59 | 579.86 | 83.5 | 160.5 | 187 | 215.5 | 253 | 7.21 | 71.36 | 123.38 | 202.29 | 298.23 | 0.01 | 3.78 | 10.54 | 24.16 | 49.1 | 6 | 39 | 52 | 77 | 98.5 | 79.888 | 247.301 | 341.267 | 470.676 | 623.571 | 11.527 | 60.735 | 92.5 | 140.989 | 208.328
WA | S | 67.1 | 67.1 | 84 | 0.98 | 0.17459 | 2.3816 | 11.96 | 32.38 | 43.63 | 46.25 | 47.1 | 47.99 | 48.85 | 38.41 | 40.53 | 41.33 | 42.14 | 42.88 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WA | W | 73.7 | 73.7 | 84 | 0.99 | 0.17459 | 2.3816 | 11.96 | 23.59 | 40.05 | 41.09 | 41.89 | 42.71 | 43.4 | 31.71 | 32.81 | 33.45 | 34.12 | 34.7 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WB | S | 52.7 | 31.8 | 90 | 0.99 | 8.1752 | 1.3375 | 3.58 | 33.31 | 39.0893 | 42.1738 | 42.8804 | 64.2702 | 64.9768 | 35.0499 | 37.8157 | 38.4493 | 57.6287 | 58.2623 | 10.22% | 3.2499 | 37.1887 | 85.9061 | 108.3969 | 2175.3528 | 4269.2919 | 0.24173 | 0.55839 | 0.70458 | 14.1398 | 27.7504 | 15.75 | 28.75 | 35 | 541.25 | 1182.75 | 5.8312 | 22.3397 | 32.5494 | 1057.8691 | 1942.4037 | 0.037903 | 0.14521 | 0.21157 | 6.8761 | 12.6256 | 4 | 12.25 | 14.75 | 214.5 | 527.25 | 15.2385 | 41.4096 | 55.3036 | 1393.1142 | 2640.4702 | 0.09905 | 0.26916 | 0.35947 | 9.0552 | 17.1631
WB | W | 52.7 | 31.8 | 90 | 1 | 8.1752 | 1.3375 | 3.58 | 32.71 | 37.6877 | 39.8389 | 41.0643 | 51.619 | 62.2446 | 34.6307 | 36.6075 | 37.7335 | 47.4321 | 57.1957 | 8.902% | 2.8307 | 37.1887 | 85.9061 | 108.3969 | 2175.3528 | 4269.2919 | 0.24173 | 0.55839 | 0.70458 | 14.1398 | 27.7504 | 15.75 | 28.75 | 35 | 541.25 | 1182.75 | 5.8312 | 22.3397 | 32.5494 | 1057.8691 | 1942.4037 | 0.037903 | 0.14521 | 0.21157 | 6.8761 | 12.6256 | 4 | 12.25 | 14.75 | 214.5 | 527.25 | 15.2385 | 41.4096 | 55.3036 | 1393.1142 | 2640.4702 | 0.09905 | 0.26916 | 0.35947 | 9.0552 | 17.1631
WG | S | 109.9 | 67.6 | 81 | 0.99 | 0.97589 | 7.4686 | 13.14 | 39.66 | 52.3073 | 59.1591 | 62.2128 | 65.2556 | 68.1561 | 47.9884 | 54.2744 | 57.076 | 59.8675 | 62.5285 | - | - | 0 | 0 | 0 | 0 | 0.13904 | 0 | 0 | 0 | 0 | 0.00061177 | 0 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.041712 | 0 | 0 | 0 | 0 | 0.00018353
WG | W | 119 | 71.9 | 81 | 0.99 | 0.97589 | 7.4686 | 13.14 | 31.87 | 47.7332 | 53.1795 | 56.5306 | 59.2537 | 61.8902 | 44.1974 | 49.2403 | 52.3432 | 54.8646 | 57.3058 | - | - | 0 | 0 | 0 | 0 | 0.13904 | 0 | 0 | 0 | 0 | 0.00061177 | 0 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.041712 | 0 | 0 | 0 | 0 | 0.00018353
WP | S | 143.3 | 71.7 | 84 | 0.98 | 0.041 | 0 | 7.47 | 27.07 | 32.71 | 34.46 | 35.08 | 35.75 | 36.39 | 29.42 | 30.93 | 31.5 | 32.1 | 32.65 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WP | W | 163.28 | 71.7 | 84 | 1 | 0.041 | 0 | 7.47 | 18.19 | 22.72 | 23.62 | 24.05 | 24.51 | 24.93 | 21.5 | 22.37 | 22.78 | 23.22 | 23.62 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0