## Intro
CitiPower 2024 Distribution System Limitation Template
This Distribution Systems Limitations template is intended to make the Distribution Annual Planning Report (DAPR) limitation data more accessible and usable. Any information provided in this System Limitations template should be read in conjunction with the CitiPower 2024 DAPR. It should also be noted that the information in this template and the DAPR are based on high-level risk assessments produced for the DAPR. As such the numbers are indicative and subject to change. Therefore the information in this template should not be used to make investment decisions, and should only be used to assist in discussions with CitiPower. Finalised data will be produced in a detailed risk assessment conducted at the RIT-D or business case stage. However CitiPower invites interested parties to submit their proposals or to engage in joint planning with CitiPower as early as possible in order to defer or avoid the proposed augmentation. CitiPower also publishes its own Network Limitation maps in order to assist with the visualisation of the limitation data presented within this template and the DAPR. The data in this template will be updated annually and will be published along with the DAPR. We welcome any feedback to improve the content or usability of this template.

## Citipower Limitations
Owner | Asset Name | Asset Code | Network Element | Voltage level (kV) | Rating |  |  |  | Nameplate Rating | Location |  |  |  | Residential customers affected |  | Business Case | [7 empty] | Demand Reduction required to defer investment by 1 year |  | Emergency Generation |  | Load Transfer capability (MVA) | Power Factor | Summer 10% POE | [14 empty] | Summer 50% POE | [14 empty] | Weighted Energy at Risk (MWh) |  |  |  |  | Weighted Expected Energy at Risk (MWh)
[5 empty] | Summer |  | Winter |  |  | Start |  | End |  |  |  | Constraint Primary Driver | Investment Description | Preferred network investment |  |  |  | Proposed Timing | Annual Deferral Value | [6 empty] | Forecast Maximum Demand (MVA) |  |  |  |  | Maximum Load at risk (MVA) (N-1) |  |  |  |  | Hours at Risk (Hrs) |  |  |  |  | Forecast Maximum Demand (MVA) |  |  |  |  | Maximum Load at risk (MVA) (N-1) |  |  |  |  | Hours at Risk (Hrs)
[5 empty] | N Rating (MVA) | N-1 Rating (MVA) | N Rating (MVA) | N-1 Rating (MVA) |  | Longitude | Latitude | Longitude | Latitude | Count | Percent |  |  | capital cost ($) | cost accuracy plus | cost accuracy minus | Operating cost ($) |  |  | (MW) | (MVA) | (MW) | (MVA) |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029

## Sub-T Aug Sum
Sub transmission line | Season | Line N Import Rating (MVA) | Line Power Factor at Minimum Demand | Embedded Generation Capacity (MVA) | Load Transfer Capability (MVA) | Hours load is > 95% of Minimum Demand (Hrs) | Actual Minimum Demand (MVA) | 50% POE |  |  |  |  | 50% POE load above N Import Rating (%) | 50% POE load above N Import Rating (MVA) | 50% POE
[8 empty] | Forecast Minimum Demand (MVA) | [6 empty] | Energy at Risk (MWh) |  |  |  |  | Expected Energy at Risk (MWh) |  |  |  |  | Hours at Risk (Hrs)
|  |  | 2024 | 2024 | 2025 | 2024 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2025 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029
RTS-RP124 | S | 7.6 | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-RP124 | W | 7.6 | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF1 | S | 87.5 | 0.9749 |  |  |  | 23.9 | 26.1 | 27.4 | 28.5 | 29.4 | 30.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF1 | W | 87.5 | 0.9751 |  |  |  | 24.1 | 22.8 | 23.7 | 24.4 | 25.1 | 25.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-LQ3 | S | 76.6 | 0.90814 |  |  |  | 38.1 | 42.6 | 47.6 | 51 | 52.3 | 54.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-LQ3 | W | 86.9 | 0.90789 |  |  |  | 38 | 31 | 33.5 | 35.5 | 36.6 | 37.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-WG | S | 88 | 0.94777 |  |  |  | 65.1 | 78.6 | 89.2 | 94.5 | 100.8 | 106.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-WG | W | 112 | 0.94486 |  |  |  | 67.1 | 78.6 | 85.5 | 90.6 | 96.3 | 101.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-WA2 | S | 37.7 | 0.95294 |  |  |  | 17 | 20.9 | 22.2 | 23.2 | 23.9 | 25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-WA2 | W | 40 | 0.94937 |  |  |  | 15.8 | 15.4 | 16.1 | 16.3 | 16.7 | 16.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FB-WG | S | 89.7 | 0.96692 |  |  |  | 39.3 | 52.5 | 59.5 | 62.6 | 65.8 | 68.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FB-WG | W | 94.3 | 0.96825 |  |  |  | 37.8 | 46.5 | 50.2 | 52.8 | 55.5 | 57.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-FR3 | S | 82.3 | 0.98452 |  |  |  | 32.3 | 33.5 | 34.4 | 34.6 | 34.8 | 35.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-FR3 | W | 87.4 | 0.98452 |  |  |  | 32.3 | 29.7 | 30.1 | 30.3 | 30.5 | 30.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-HB | S | 117.2 | 0.8928 |  |  |  | 116.6 | 120.4 | 121.2 | 121.6 | 123.4 | 124.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-HB | W | 126.3 | 0.9 |  |  |  | 112 | 85 | 86.5 | 88.2 | 90 | 91 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BQ3 | S | 139.7 | 0.9682 |  |  |  | 91.2 | 95.5 | 98.9 | 99.5 | 100.5 | 101.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BQ3 | W | 149.2 | 0.96909 |  |  |  | 90.6 | 81.7 | 83.2 | 83.9 | 84.6 | 85 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-ARD1 | S | 21.9 | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-ARD1 | W | 26.5 | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
B-NR | S | 85.7 | 0.95857 |  |  |  | 70 | 73.3 | 77.7 | 97.8 | 100.4 | 102.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
B-NR | W | 91.4 | 0.9584 |  |  |  | 67.3 | 60.5 | 82.4 | 84.1 | 86.6 | 88.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
B-CW | S | 85.7 | 0.94929 |  |  |  | 98.6 | 103.9 | 107.7 | 109.5 | 112.1 | 114.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
B-CW | W | 91.4 | 0.95016 |  |  |  | 96.3 | 84.7 | 88.1 | 89.2 | 93.1 | 94.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BQ-WP3 | S | 84 | 0.96806 |  |  |  | 40.7 | 41.4 | 43.1 | 43 | 43.3 | 43.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BQ-WP3 | W | 91.5 | 0.9679 |  |  |  | 40.5 | 31.2 | 31.8 | 31.9 | 32 | 32 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BQ-WP2 | S | 84 | 0.96806 |  |  |  | 40.7 | 41.4 | 43.1 | 43 | 43.3 | 43.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BQ-WP2 | W | 91.5 | 0.9679 |  |  |  | 40.5 | 31.2 | 31.8 | 31.9 | 32 | 32 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-FR1 | S | 82.3 | 0.9816 |  |  |  | 32.6 | 33.8 | 34.5 | 34.9 | 35.1 | 35.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-FR1 | W | 87.4 | 0.9816 |  |  |  | 32.6 | 30 | 30.4 | 30.6 | 30.8 | 31.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BK194 | S | 10.3 | 0.94118 |  |  |  | 8.5 | 8.6 | 9.1 | 9.3 | 2.4 | 2.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BK194 | W | 10.3 | 0.94118 |  |  |  | 8.5 | 9 | 9.2 | 9.6 | 2.8 | 3.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TK-BC | S | 91.5 | 0.94314 |  |  |  | 80.9 | 83.1 | 84.9 | 89.9 | 91.1 | 92.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TK-BC | W | 91.5 | 0.94444 |  |  |  | 81 | 71.9 | 75.2 | 78.8 | 79.6 | 80.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SB-SO | S | 109.7 | 0.98504 |  |  |  | 40.1 | 44.1 | 46.5 | 48 | 49.5 | 50.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SB-SO | W | 121.7 | 0.98701 |  |  |  | 38.5 | 32.5 | 34 | 34.9 | 36.1 | 36.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BK187 | S | 10.3 | 0.98718 |  |  |  | 7.8 | 8.1 | 8.8 | 9.2 | 2.3 | 2.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BK187 | W | 10.3 | 0.98718 |  |  |  | 7.8 | 8.2 | 8.7 | 8.8 | 2.6 | 3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-FR2 | S | 82.3 | 0.98466 |  |  |  | 32.6 | 33.8 | 34.7 | 34.9 | 35 | 35.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-FR2 | W | 87.4 | 0.98466 |  |  |  | 32.6 | 30 | 30.4 | 30.6 | 30.8 | 31.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-SB | S | 117.7 | 0.97091 |  |  |  | 72.2 | 79.3 | 83.8 | 86.5 | 89.4 | 92 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-SB | W | 130.3 | 0.97118 |  |  |  | 69.4 | 58 | 60.7 | 62.4 | 64.5 | 66 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-RP123 | S | 11.4 | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-RP123 | W | 11.4 | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FR-WP3 | S | 81.7 | 0.92053 |  |  |  | 15.1 | 16.3 | 17 | 17.3 | 17.1 | 17.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FR-WP3 | W | 88 | 0.91391 |  |  |  | 15.1 | 12.4 | 12.8 | 13 | 13.2 | 13 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BQ1 | S | 159.9 | 0.96691 |  |  |  | 96.7 | 101.3 | 104.9 | 105.5 | 106.5 | 107.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BQ1 | W | 170.6 | 0.96875 |  |  |  | 96 | 86.6 | 88.1 | 88.9 | 89.7 | 90.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-BQ1 | S | 162.3 | 0.95565 |  |  |  | 45.1 | 50.8 | 54.3 | 55.3 | 56.2 | 57.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-BQ1 | W | 173.8 | 0.95711 |  |  |  | 44.3 | 40.4 | 41.6 | 42.8 | 43.7 | 44.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-VM1 | S | 159.9 | 0.96856 |  |  |  | 82.7 | 87.4 | 90.8 | 91.5 | 92.5 | 93.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-VM1 | W | 170.6 | 0.96833 |  |  |  | 82.1 | 74.1 | 75.5 | 76.4 | 77.1 | 77.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-R136 | S | 21.5 | 0.98462 |  |  |  | 19.5 | 21.7 | 25.5 | 27.8 | 28.1 | 28.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-R136 | W | 24.7 | 0.98515 |  |  |  | 20.2 | 21.1 | 23.6 | 24.5 | 24.8 | 24.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-SO | S | 109.2 | 0.97091 |  |  |  | 72.2 | 79.8 | 83.8 | 86.8 | 89.4 | 92 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-SO | W | 125.7 | 0.97118 |  |  |  | 69.4 | 58 | 60.7 | 62.4 | 64.5 | 66 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-K | S | 90.3 | 0.96692 |  |  |  | 90.7 | 91 | 92.3 | 93.3 | 93.4 | 94.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-K | W | 104.6 | 0.967 |  |  |  | 90.9 | 66.5 | 67.9 | 68.1 | 69.5 | 70.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-EW | S | 85.7 | 0.9709 |  |  |  | 65.3 | 68.9 | 71.9 | 73.6 | 75.6 | 77.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-EW | W | 101.7 | 0.97024 |  |  |  | 67.2 | 63.3 | 65.3 | 67.4 | 69.3 | 71.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-F179 | S | 12 | 0.98734 |  |  |  | 15.8 | 14.6 | 14.9 | 3.1 | 3.1 | 3.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-F179 | W | 12.6 | 0.98734 |  |  |  | 15.8 | 17.1 | 3.3 | 3.2 | 3.2 | 3.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FR-WP1 | S | 78.3 | 1 |  |  |  | 13.3 | 14.5 | 15.2 | 15.5 | 15.8 | 16 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FR-WP1 | W | 84.6 | 1 |  |  |  | 13.3 | 11 | 11.4 | 11.5 | 11.7 | 11.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-TK/BC | S | 135.5 | 0.95305 |  |  |  | 100.1 | 104.1 | 107 | 111 | 112.9 | 114.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-TK/BC | W | 137.2 | 0.95272 |  |  |  | 99.4 | 89.3 | 92.5 | 96.2 | 98 | 98.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-CW | S | 135.5 | 0.93282 |  |  |  | 131 | 137.3 | 144.9 | 166.8 | 171.2 | 176.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-CW | W | 142.3 | 0.93381 |  |  |  | 125.4 | 111.2 | 136.5 | 138.6 | 145 | 147.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-WA3 | S | 37.7 | 0.97484 |  |  |  | 15.9 | 18.6 | 19.8 | 19.8 | 20.3 | 20.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-WA3 | W | 40 | 0.97959 |  |  |  | 14.7 | 14.3 | 14.9 | 15.2 | 15.5 | 15.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLF5-TP53 | S | 12.6 | 0.95652 |  |  |  | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLF5-TP53 | W | 13.1 | 0.95652 |  |  |  | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-ARD2 | S | 21.9 | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-ARD2 | W | 26.5 | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-PM | S | 66.3 | 0.95425 |  |  |  | 15.3 | 16.6 | 17.8 | 17.9 | 18.1 | 18.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-PM | W | 86.3 | 0.95425 |  |  |  | 15.3 | 16.4 | 16.9 | 17.1 | 17.5 | 17.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-WP | S | 125.7 | 0.96753 |  |  |  | 89.3 | 93.2 | 96.6 | 97.1 | 98 | 98.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-WP | W | 137.2 | 0.96956 |  |  |  | 88.7 | 78.5 | 80 | 80.7 | 81.3 | 81.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-C186 | S | 9.9 | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-C186 | W | 11.2 | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-WA1 | S | 37.7 | 0.94611 |  |  |  | 16.7 | 20.5 | 21.8 | 22.8 | 23.4 | 24.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-WA1 | W | 40 | 0.94839 |  |  |  | 15.5 | 15.1 | 15.8 | 16 | 16.3 | 16.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-C196 | S | 9.9 | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-C196 | W | 11.2 | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FR-WP2 | S | 80 | 0.92105 |  |  |  | 15.2 | 16.4 | 17.2 | 17.4 | 17.2 | 17.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FR-WP2 | W | 85.7 | 0.92105 |  |  |  | 15.2 | 12.5 | 12.9 | 13.1 | 13.3 | 13.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HB-Q | S | 95.5 | 0.90588 |  |  |  | 85 | 88.6 | 89 | 89.3 | 90.4 | 91.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HB-Q | W | 108.6 | 0.9057 |  |  |  | 85.9 | 63.5 | 64.2 | 65.1 | 66.2 | 66.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MG-AP | S | 91.5 | 0.9428 |  |  |  | 50.7 | 55.1 | 57.6 | 58.2 | 59.4 | 60.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MG-AP | W | 91.5 | 0.94466 |  |  |  | 50.6 | 43.6 | 44.6 | 45.7 | 47.1 | 48.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
JA-WP | S | 47.4 | 0 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
JA-WP | W | 57.2 | 0 |  |  |  | 0.5 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SK-EW | S | 86.3 | 0.95444 |  |  |  | 41.7 | 45.9 | 48.3 | 49.4 | 50.9 | 52.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SK-EW | W | 91.5 | 0.95402 |  |  |  | 43.5 | 38.6 | 40 | 41.4 | 42.6 | 44 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-VM3 | S | 120 | 0.94149 |  |  |  | 37.6 | 40.2 | 45.7 | 47.3 | 48.8 | 50.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-VM3 | W | 129.7 | 0.97849 |  |  |  | 37.2 | 33.2 | 34.6 | 35.5 | 36.2 | 36.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-LQ1 | S | 76.6 | 0.95184 |  |  |  | 35.3 | 36.5 | 39.4 | 40.6 | 41.9 | 43.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-LQ1 | W | 86.9 | 0.95455 |  |  |  | 35.2 | 29.8 | 32.2 | 32.8 | 33.9 | 34.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF3 | S | 87.5 | 0.97083 |  |  |  | 24 | 26.2 | 27.4 | 28.5 | 29.4 | 30.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF3 | W | 87.5 | 0.97107 |  |  |  | 24.2 | 22.8 | 23.8 | 24.4 | 25.2 | 25.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
K-CL | S | 91.5 | 0.94499 |  |  |  | 50.9 | 49.5 | 50.3 | 50.7 | 50.3 | 51 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
K-CL | W | 105.7 | 0.9451 |  |  |  | 51 | 37.7 | 38.7 | 38.5 | 39.3 | 39.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-R134 | S | 19.1 | 0.9913 |  |  |  | 11.5 | 12.8 | 15 | 16.4 | 16.6 | 16.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-R134 | W | 20.7 | 0.98333 |  |  |  | 12 | 12.5 | 14 | 14.5 | 14.6 | 14.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WP-MP3 | S | 83.9 | 0.93824 |  |  |  | 42.1 | 42.7 | 44.5 | 44.6 | 44.8 | 45.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WP-MP3 | W | 91.5 | 0.9378 |  |  |  | 41.8 | 31.8 | 32.5 | 32.5 | 32.7 | 33 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-F182 | S | 12 | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-F182 | W | 12.6 | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-JA1 | S | 145.2 | 0.94949 |  |  |  | 49.5 | 53.2 | 60.7 | 62.8 | 64.7 | 67.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-JA1 | W | 153.2 | 0.9828 |  |  |  | 46.5 | 42.8 | 44.1 | 44.9 | 45.9 | 47.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
E-PM | S | 74.3 | 0.93103 |  |  |  | 14.5 | 15.7 | 16.8 | 16.8 | 16.9 | 16.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
E-PM | W | 91.5 | 0.92466 |  |  |  | 14.6 | 15.4 | 15.8 | 16 | 16.2 | 16.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-AP | S | 101.7 | 0.95377 |  |  |  | 82.2 | 89.7 | 95 | 96.5 | 98 | 99.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-AP | W | 109.7 | 0.95411 |  |  |  | 82.8 | 70.6 | 73.1 | 74.3 | 75.8 | 76.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
L-Q | S | 95.4 | 0.95342 |  |  |  | 64.4 | 67.7 | 67.8 | 67.9 | 68.3 | 68.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
L-Q | W | 108.6 | 0.96327 |  |  |  | 59.9 | 49.5 | 50.6 | 51.6 | 52.5 | 53.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLF64-TP278 | S | 12.6 | 0.97059 |  |  |  | 6.8 | 6.9 | 6.9 | 6.9 | 6.8 | 6.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLF64-TP278 | W | 13.1 | 0.95652 |  |  |  | 6.9 | 6.8 | 6.9 | 6.8 | 6.8 | 6.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WP-MP2 | S | 80 | 0.93602 |  |  |  | 42.2 | 42.8 | 44.7 | 44.8 | 44.9 | 45.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WP-MP2 | W | 85.7 | 0.93795 |  |  |  | 41.9 | 31.9 | 32.6 | 32.6 | 32.8 | 33.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-BQ3 | S | 125.7 | 0.95565 |  |  |  | 45.1 | 50.8 | 54.3 | 55.3 | 56.2 | 57.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-BQ3 | W | 128 | 0.95711 |  |  |  | 44.3 | 40.4 | 41.6 | 42.8 | 43.7 | 44.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-L | S | 106.9 | 0.89941 |  |  |  | 119.3 | 122.6 | 123.2 | 123.7 | 124.9 | 126.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-L | W | 108.6 | 0.91045 |  |  |  | 113.9 | 85.4 | 87 | 88.7 | 90.5 | 91.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WP-MP1 | S | 78.3 | 0.93824 |  |  |  | 42.1 | 42.7 | 44.6 | 44.7 | 44.8 | 45.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WP-MP1 | W | 84.6 | 0.94019 |  |  |  | 41.8 | 31.9 | 32.5 | 32.6 | 32.7 | 33.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-JA3 | S | 114.9 | 0.95506 |  |  |  | 44.5 | 47.9 | 54.6 | 56.5 | 58.2 | 60.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-JA3 | W | 121.2 | 0.98853 |  |  |  | 43.6 | 40.1 | 41.4 | 42.1 | 42.7 | 43.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-R135 | S | 21.5 | 0.98477 |  |  |  | 19.7 | 21.8 | 25.6 | 27.9 | 28.3 | 28.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-R135 | W | 24.7 | 0.98529 |  |  |  | 20.4 | 21.2 | 23.8 | 24.7 | 24.9 | 25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
JA-LQ2 | S | 76.6 | 0.90814 |  |  |  | 38.1 | 42.2 | 47.7 | 50.6 | 52.5 | 54.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
JA-LQ2 | W | 86.9 | 0.91053 |  |  |  | 38 | 31 | 33.4 | 35.4 | 36.6 | 37.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RD-EB | S | 65.2 | 0.99031 |  |  |  | 51.6 | 53.8 | 53.7 | 53.8 | 54.6 | 54.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RD-EB | W | 77.2 | 0.98986 |  |  |  | 49.3 | 39.4 | 39.7 | 40.2 | 40.8 | 41.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-RD | S | 80 | 0.95991 |  |  |  | 92.3 | 94.7 | 95.1 | 95.3 | 96.7 | 97.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-RD | W | 97.2 | 0.95916 |  |  |  | 90.6 | 67.1 | 68 | 68.9 | 70.2 | 70.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-AR | S | 94.3 | 0.92262 |  |  |  | 84 | 86.4 | 88.9 | 92.8 | 95.1 | 95.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-AR | W | 123.5 | 0.92133 |  |  |  | 83.9 | 74.4 | 78 | 82.3 | 83.1 | 84.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-VM2 | S | 144 | 0.97447 |  |  |  | 23.5 | 24.4 | 26 | 26.8 | 27.5 | 28.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-VM2 | W | 155.5 | 0.97863 |  |  |  | 23.4 | 21 | 21.9 | 22.4 | 22.8 | 23.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-FB | S | 88 | 0.95062 |  |  |  | 64.8 | 78.7 | 89.2 | 95 | 100.7 | 106 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-FB | W | 112 | 0.94784 |  |  |  | 67.1 | 78.5 | 85.3 | 90.9 | 96.4 | 100.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BC-AR | S | 84.6 | 0.91974 |  |  |  | 46.1 | 48.7 | 50.4 | 53.9 | 55.5 | 55.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BC-AR | W | 91.4 | 0.91991 |  |  |  | 46.2 | 43.4 | 46 | 49.7 | 50.1 | 50.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-RP125 | S | 9 | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-RP125 | W | 9.7 | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-MG | S | 100.6 | 0.95278 |  |  |  | 82.6 | 89.4 | 95.2 | 96 | 97.5 | 99.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-MG | W | 115.5 | 0.95411 |  |  |  | 82.8 | 70.6 | 72.8 | 73.9 | 75.5 | 76.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-JA | S | 91.5 | 0.96825 |  |  |  | 50.4 | 54.5 | 62.6 | 64.7 | 66.4 | 68.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-JA | W | 98.3 | 0.99798 |  |  |  | 49.5 | 46.7 | 47.8 | 48.2 | 48.7 | 49.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BK185 | S | 10.5 | 1 |  |  |  | 7.6 | 7.6 | 8.3 | 8.6 | 1.3 | 1.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BK185 | W | 10.5 | 1 |  |  |  | 7.6 | 7.9 | 8.4 | 8.6 | 1.4 | 1.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-SK | S | 83.5 | 0.98134 |  |  |  | 64.3 | 68.6 | 71 | 73.2 | 74.7 | 76.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-SK | W | 93.2 | 0.97885 |  |  |  | 66.2 | 62.8 | 64.8 | 66.5 | 68.8 | 70.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-C191 | S | 9.9 | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-C191 | W | 11.2 | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-VM1 | S | 130.3 | 0.99363 |  |  |  | 31.4 | 32.8 | 34.9 | 35.9 | 36.9 | 38.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-VM1 | W | 164.6 | 0.99363 |  |  |  | 31.4 | 28.1 | 29.3 | 30 | 30.6 | 31.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-NR | S | 135.5 | 0.92829 |  |  |  | 128.3 | 134.1 | 142 | 166.7 | 170.8 | 175.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-NR | W | 137.2 | 0.92938 |  |  |  | 123.2 | 109.5 | 135.4 | 139.1 | 142.7 | 146.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-F189 | S | 14.1 | 0.98701 |  |  |  | 15.4 | 14.2 | 14.7 | 3 | 3 | 3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-F189 | W | 14.8 | 0.98701 |  |  |  | 15.4 | 16.7 | 3 | 3.1 | 3.1 | 3.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-TK | S | 116.6 | 0.96388 |  |  |  | 52.6 | 54.5 | 56 | 58.1 | 59 | 59.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-TK | W | 122.3 | 0.96381 |  |  |  | 52.5 | 46.7 | 48.5 | 50.4 | 51.1 | 51.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-E | S | 66.3 | 0.94231 |  |  |  | 15.6 | 17 | 18.3 | 18.4 | 18.6 | 18.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-E | W | 86.3 | 0.93631 |  |  |  | 15.7 | 16.8 | 17.3 | 17.6 | 17.9 | 18.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-CL | S | 117.2 | 0.96806 |  |  |  | 90.8 | 91 | 92.6 | 92.5 | 93.5 | 93.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-CL | W | 126.3 | 0.9692 |  |  |  | 90.9 | 66.7 | 67.4 | 68.2 | 69 | 70.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-EB | S | 94.9 | 0.95243 |  |  |  | 92.5 | 94.6 | 95.1 | 95.3 | 96.6 | 97.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-EB | W | 101.7 | 0.95264 |  |  |  | 90.8 | 67 | 67.6 | 68.7 | 70.1 | 70.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -

## ZSS Aug Sum
Zone Substation | Season | Station N Export Rating (MVA) | Station N-1 Export Rating (MVA) | Station Nameplate Rating (MVA) | Station Power Factor at Minimum Demand | Embedded Generation Capacity (MVA) | Load Transfer Capability (MVA) | Generation Headroom (MVA) | Hours load is > 95% of Minimum Demand (Hrs) | Actual Minimum Demand (MVA) | 50% POE |  |  |  |  | % 50% POE load below N-1 Export Rating | 50% POE
[11 empty] | Forecast Minimum Demand (MVA) | [5 empty] | Energy at Risk (MWh) |  |  |  |  | Expected Energy at Risk (MWh) |  |  |  |  | Hours at Risk (Hrs)
[5 empty] | 2024 | 2024 | 2025 | 2024 | 2024 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029
AP | S | -87 | -57 | 87 | 0.99 | 3.952 | 23.2441 | 53.048 | 0 | 11.22 | 9.9 | 10.76 | 10.93 | 11.26 | 11.54 | -
AP | W | -87 | -57 | 87 | 0.99 | 3.952 | 23.2441 | 53.048 | 0 | 11.49 | 12.36 | 12.73 | 13.05 | 13.42 | 13.72 | -
AR | S | -60 | -30 | 60 | 0.97 | 3.0682 | 5.8301 | 26.9318 | 0 | 6.98 | 7.2 | 7.55 | 7.59 | 7.63 | 7.12 | -
AR | W | -60 | -30 | 60 | 0.97 | 3.0682 | 5.8301 | 26.9318 | 0 | 7.34 | 7.64 | 7.83 | 7.86 | 7.94 | 8.03 | -
B | S | -54 | -27 | 54 | 1 | 2.2857 | 6.4588 | 24.7143 | 0 | 15.65 | 14.34 | 15.24 | 15.65 | 16.08 | 16.5 | -
B | W | -54 | -27 | 54 | 1 | 2.2857 | 6.4588 | 24.7143 | 0 | 9.2 | 10.8 | 11.15 | 11.43 | 11.77 | 12.04 | -
BC | S | -87 | -57 | 87 | 0.98 | 2.9594 | 12.3651 | 54.0406 | 0 | 11.34 | 11.24 | 11.64 | 13 | 13.56 | 13.59 | -
BC | W | -87 | -57 | 87 | 0.98 | 2.9594 | 12.3651 | 54.0406 | 0 | 11.47 | 11.89 | 12.6 | 13.81 | 14.05 | 14.05 | -
BK | S | -23 | -20 | 33 | 1 | 3.3666 | 0 | 16.6334 | 0 | 2.66 | 3.08 | 3.54 | 2.99 | -1.09 | -2.2 | -
BK | W | -23 | -20 | 33 | 1 | 3.3666 | 0 | 16.6334 | 0 | 3.72 | 3.78 | 4.19 | 3.75 | -1.15 | -1.4 | -
BQ | S | -110 | -55 | 110 | 1 | 4.2415 | 10.4408 | 50.7585 | 0 | 29.11 | 28.13 | 30.35 | 30.73 | 30.84 | 30.96 | -
BQ | W | -110 | -55 | 110 | 1 | 4.2415 | 10.4408 | 50.7585 | 0 | 31.59 | 29.41 | 30.07 | 30.16 | 30.31 | 30.26 | -
CL | S | -87 | -57 | 87 | 0.98 | 5.5805 | 0.85737 | 51.4195 | 0 | 11 | 10.67 | 11.06 | 11.16 | 11.14 | 10.5 | -
CL | W | -87 | -57 | 87 | 0.98 | 5.5805 | 0.85737 | 51.4195 | 0 | 11.41 | 11.09 | 11.38 | 11.44 | 11.51 | 11.56 | -
CW | S | -54 | -27 | 54 | 0.98 | 2.6188 | 0.7621 | 24.3812 | 0 | 6.52 | 6.26 | 7.35 | 10.06 | 10.2 | 10.29 | -
CW | W | -54 | -27 | 54 | 0.98 | 2.6188 | 0.7621 | 24.3812 | 0 | 6.65 | 6.95 | 10 | 9.74 | 9.51 | 9.25 | -
DA | S | -40.5 | -27 | 37 | 1 | 0.8564 | 9.3637 | 26.1436 | 0 | 10.39 | 11.41 | 12.42 | 12.73 | 13.15 | 13.54 | -
DA | W | -40.5 | -27 | 37 | 1 | 0.8564 | 9.3637 | 26.1436 | 0 | 10.41 | 10.59 | 11.02 | 11.37 | 11.75 | 12.09 | -
E | S | -13.5 | 0 | 46 | 1 | 0.208 | 3.178 | 0 | 0.62 | 0 | -0.12 | -0.14 | -0.15 | -0.16 | -0.17 | 100%
E | W | -13.5 | 0 | 46 | 1 | 0.208 | 3.178 | 0 | 0.62 | 0.02 | -0.01 | -0.02 | -0.02 | -0.02 | -0.01 | 100%
F | S | -20 | -10 | 23 | 1 | 3.5254 | 1.6118 | 6.4746 | 0 | 1.87 | 2.72 | 2.2 | -1.72 | -2.73 | -2.92 | -
F | W | -20 | -10 | 23 | 1 | 3.5254 | 1.6118 | 6.4746 | 0 | 3.3 | 3.47 | -1.33 | -1.36 | -1.42 | -1.46 | -
FB | S | -90 | -60 | 90 | 1 | 0.65312 | 5.1251 | 59.3469 | 0 | 9.74 | 7.9 | 8.85 | 9.58 | 10.26 | 10.92 | -
FB | W | -90 | -60 | 90 | 1 | 0.65312 | 5.1251 | 59.3469 | 0 | 9.34 | 9.98 | 10.89 | 11.69 | 12.49 | 13.24 | -
FR | S | -90 | -60 | 90 | 1 | 0.30334 | 0 | 59.6967 | 0 | 11.07 | 8.86 | 10.28 | 10.93 | 10.94 | 10.91 | -
FR | W | -90 | -60 | 90 | 1 | 0.30334 | 0 | 59.6967 | 0 | 11.5 | 9.91 | 10.68 | 10.72 | 10.69 | 10.63 | -
JA | S | -165 | -110 | 165 | 0.99 | 0.7355 | 61.5588 | 109.2645 | 0 | 32.75 | 26.53 | 32.42 | 33.86 | 34.98 | 36.08 | -
JA | W | -165 | -110 | 165 | 0.99 | 0.7355 | 61.5588 | 109.2645 | 0 | 32.45 | 29.63 | 32.21 | 33.24 | 34.3 | 35.39 | -
L | S | -60 | -30 | 60 | 0.98 | 10.1513 | 12.2317 | 19.8487 | 0 | 4.16 | 5.76 | 4.07 | 2.92 | -3.37 | -5.09 | -
L | W | -60 | -30 | 60 | 0.98 | 10.1513 | 12.2317 | 19.8487 | 0 | 8.11 | 6.56 | 4.65 | 3.18 | -2.92 | -3.51 | -
LQ | S | -180 | -120 | 180 | 1 | 0.10104 | 21.5294 | 119.899 | 0 | 16.77 | 17.53 | 20.04 | 20.9 | 21.59 | 22.25 | -
LQ | W | -180 | -120 | 180 | 1 | 0.10104 | 21.5294 | 119.899 | 0 | 16.19 | 16.49 | 17.48 | 18.06 | 18.7 | 19.23 | -
MG | S | -87 | -57 | 87 | 1 | 1.0185 | 9.6787 | 55.9815 | 0 | 8.68 | 9.3 | 10.65 | 10.73 | 10.74 | 10.72 | -
MG | W | -87 | -57 | 87 | 1 | 1.0185 | 9.6787 | 55.9815 | 0 | 9.33 | 9.87 | 10.3 | 10.28 | 10.29 | 10.25 | -
MP | S | -165 | -110 | 165 | 1 | 1.0931 | 4.001 | 108.9069 | 0 | 24.61 | 19.29 | 20.8 | 20.94 | 21.02 | 21.14 | -
MP | W | -165 | -110 | 165 | 1 | 1.0931 | 4.001 | 108.9069 | 0 | 24.8 | 20.16 | 20.68 | 20.75 | 20.87 | 20.94 | -
NC | S | -60 | -30 | 60 | 0.24 | 11.5341 | 0 | 18.4659 | 0 | 1.15 | 1.44 | -1.79 | -3.63 | -5.91 | -7.96 | -
NC | W | -60 | -30 | 60 | 0.24 | 11.5341 | 0 | 18.4659 | 0 | 4.14 | 2.78 | 1.49 | -1.78 | -3.19 | -4.84 | -
NR | S | -83 | -55 | 83 | 1 | 4.7334 | 4.6679 | 50.2666 | 0 | 12.73 | 14.39 | 15.27 | 15.62 | 16.01 | 16.37 | -
NR | W | -83 | -55 | 83 | 1 | 4.7334 | 4.6679 | 50.2666 | 0 | 14.17 | 15.01 | 15.51 | 15.87 | 16.3 | 16.61 | -
PM | S | -27 | -13.5 | 26 | 1 | 1.6196 | 4.6298 | 11.8804 | 0 | 2.54 | 2.18 | 2.73 | 2.49 | 2.27 | 2.1 | -
PM | W | -27 | -13.5 | 26 | 1 | 1.6196 | 4.6298 | 11.8804 | 0 | 3.52 | 4.29 | 4.28 | 4.12 | 4.01 | 3.89 | -
Q | S | -60 | -30 | 60 | 0.95 | 6.8341 | 6.8018 | 23.1659 | 0 | 4.35 | 6.54 | 5.76 | 4.18 | 3.01 | 2.66 | -
Q | W | -60 | -30 | 60 | 0.95 | 6.8341 | 6.8018 | 23.1659 | 0 | 7.11 | 7.41 | 6.42 | 5.06 | 3.96 | 3.1 | -
R | S | -40 | -26.5 | 39 | 0.93 | 1.5673 | 7.259 | 24.9327 | 0 | 5.5 | 5.35 | 8.09 | 9.71 | 9.9 | 9.88 | -
R | W | -40 | -26.5 | 39 | 0.93 | 1.5673 | 7.259 | 24.9327 | 0 | 5.86 | 7.11 | 9.16 | 10.07 | 10.09 | 10.05 | -
RD | S | -60 | -30 | 60 | 1 | 7.3274 | 8.4403 | 22.6726 | 0 | 0.15 | 2.8 | 2.4 | -2.63 | -3.92 | -5.49 | -
RD | W | -60 | -30 | 60 | 1 | 7.3274 | 8.4403 | 22.6726 | 0 | 4.96 | 3.49 | 2.56 | -2.4 | -2.91 | -4.03 | -
SB | S | -110 | -55 | 110 | 1 | 0.44308 | 0 | 54.5569 | 0 | 14.66 | 13.79 | 14.72 | 15.24 | 15.72 | 16.18 | -
SB | W | -110 | -55 | 110 | 1 | 0.44308 | 0 | 54.5569 | 0 | 13.31 | 14.79 | 15.36 | 15.84 | 16.33 | 16.76 | -
SK | S | -87 | -57 | 87 | 1 | 1.3123 | 0 | 55.6877 | 0 | 13.9 | 14 | 14.97 | 15.37 | 15.8 | 16.24 | -
SK | W | -87 | -57 | 87 | 1 | 1.3123 | 0 | 55.6877 | 0 | 13.39 | 14.66 | 15.14 | 15.56 | 16.02 | 16.4 | -
SO | S | -87 | -57 | 87 | 1 | 0.5412 | 0 | 56.4588 | 0 | 8.66 | 8.63 | 9.12 | 9.42 | 9.71 | 10.01 | -
SO | W | -87 | -57 | 87 | 1 | 0.5412 | 0 | 56.4588 | 0 | 9.29 | 8.85 | 9.16 | 9.44 | 9.73 | 10 | -
TK | S | -87 | -57 | 87 | 0.98 | 2.9717 | 14.499 | 54.0283 | 0 | 11.39 | 11.98 | 12.69 | 12.91 | 13.18 | 13.41 | -
TK | W | -87 | -57 | 87 | 0.98 | 2.9717 | 14.499 | 54.0283 | 0 | 11.76 | 12.8 | 13.18 | 13.41 | 13.69 | 13.89 | -
VM | S | -57 | -54 | 84 | 1 | 2.0434 | 12.2698 | 51.9566 | 0 | 21.52 | 17.57 | 18.76 | 19.12 | 19.54 | 19.93 | -
VM | W | -57 | -54 | 84 | 1 | 2.0434 | 12.2698 | 51.9566 | 0 | 22.69 | 16.39 | 16.95 | 17.29 | 17.69 | 17.99 | -
WA | S | -84 | -54 | 84 | 1 | 0.17459 | 2.3816 | 53.8254 | 0 | 9.3 | 9.48 | 10.49 | 10.74 | 10.95 | 11.17 | -
WA | W | -84 | -54 | 84 | 1 | 0.17459 | 2.3816 | 53.8254 | 0 | 10.22 | 10.18 | 10.55 | 10.74 | 10.95 | 11.13 | -
WB | S | -52.7 | -31.8 | 90 | 1 | 8.1752 | 1.3375 | 23.6248 | 0 | 5.56 | 6.88 | 7.74 | 6.52 | 7.83 | 6.51 | -
WB | W | -52.7 | -31.8 | 90 | 1 | 8.1752 | 1.3375 | 23.6248 | 0 | 8.2 | 8.17 | 8.92 | 8.28 | 10.08 | 8.52 | -
WG | S | -81 | -54 | 81 | 1 | 0.97589 | 7.4686 | 53.0241 | 0 | 15.23 | 15.8 | 18.36 | 19.34 | 20.27 | 21.17 | -
WG | W | -81 | -54 | 81 | 1 | 0.97589 | 7.4686 | 53.0241 | 0 | 12.82 | 20.12 | 21.84 | 22.94 | 24.02 | 25.04 | -
WP | S | -110 | -55 | 84 | 1 | 0.041 | 0 | 54.959 | 0 | 7.11 | 5.67 | 6.03 | 6.17 | 6.29 | 6.42 | -
WP | W | -110 | -55 | 84 | 1 | 0.041 | 0 | 54.959 | 0 | 7.98 | 4.79 | 4.96 | 5.06 | 5.17 | 5.27 | -