## Intro
Powercor 2024 Distribution System Limitation Template
This Distribution Systems Limitations template is intended to make the Distribution Annual Planning Report (DAPR) limitation data more accessible and usable. Any information provided in this System Limitations template should be read in conjunction with the Powercor 2024 DAPR. It should also be noted that the information in this template and the DAPR are based on high-level risk assessments produced for the DAPR. As such the numbers are indicative and subject to change. Therefore the information in this template should not be used to make investment decisions, and should only be used to assist in discussions with Powercor. Finalised data will be produced in a detailed risk assessment conducted at the RIT-D or business case stage. However Powercor invites interested parties to submit their proposals or to engage in joint planning with Powercor as early as possible in order to defer or avoid the proposed augmentation. Powercor also publishes its own Network Limitation maps in order to assist with the visualisation of the limitation data presented within this template and the DAPR. The data in this template will be updated annually and will be published along with the DAPR. We welcome any feedback to improve the content or usability of this template.

## Powercor Limitations
Owner | Asset Name | Asset Code | Network Element | Voltage level (kV) | Rating |  |  |  | Nameplate Rating | Location |  |  |  | Residential customers affected |  | Business Case | [7 empty] | Demand Reduction required to defer investment by 1 year |  | Emergency Generation |  | Load Transfer capability (MVA) | Power Factor | 10% POE | [14 empty] | 50% POE | [14 empty] | Weighted Energy at Risk (MWh)
[5 empty] | Summer |  | Winter |  |  | Start |  | End |  |  |  | Constraint Primary Driver | Investment Description | Preferred network investment |  |  |  | Proposed Timing | Annual Deferral Value | [6 empty] | Summer Forecast Maximum Demand (MVA) |  |  |  |  | Maximum Load at risk (MVA) (N-1) |  |  |  |  | Hours at Risk (Hrs) |  |  |  |  | Summer Forecast Maximum Demand (MVA) |  |  |  |  | Maximum Load at risk (MVA) (N-1) |  |  |  |  | Hours at Risk (Hrs)
[5 empty] | N Rating (MVA) | N-1 Rating (MVA) | N Rating (MVA) | N-1 Rating (MVA) |  | Longitude | Latitude | Longitude | Latitude | Count | Percent |  |  | capital cost ($) | cost accuracy plus | cost accuracy minus | Operating cost ($) |  |  | (MW) | (MVA) | (MW) | (MVA) |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029
Powercor | Bacchus Marsh | BMH | zss | 66/22 | 38.2 | 19.1 | 40.4 | 20.2 | 26 | 144.4085 | -37.6996 | 144.4085 | -37.6996 | 11707 | 91.48% | capacity | Powercor’s preferred network option is to rebuild BMH ZSS. See the DAPR report for more details. | 27103486 | 30% | 30% | 271034.86 | 2027 | 1155522.1504 | 11.9509 | 12.0717 | 0 | 0 | 3.0484 | 0.99 | 30.9601 | 32.3694 | 33.4318 | 34.7001 | 35.9034 | 11.8601 | 13.2694 | 14.3318 | 15.6001 | 16.8034 | 307.25 | 477 | 608.75 | 767.75 | 937 | 28.8671 | 30.1811 | 31.1717 | 32.3542 | 33.4762 | 9.7671 | 11.0811 | 12.0717 | 13.2542 | 14.3762 | 168.25 | 299 | 408.5 | 539.75 | 669.75 | 375.7565 | 690.5285 | 1004.0996 | 1449.6222 | 1961.4538
Powercor | Drysdale | DDL | zss | 66/22 | 79.4 | 39.7 | 94.4 | 47.2 | 66 | 144.5643 | -38.1827 | 144.5643 | -38.1827 | 34735 | 94.3% | capacity | Powercor’s preferred network option is to install a new transformer at DDL. See the DAPR report for more details. | 7599586 | 30% | 30% | 75995.86 | 2028 | 323998.5424 | 32.4116 | 32.4116 | 0 | 0 | 4.5726 | 1 | 78.2133 | 73.8816 | 76.0749 | 78.7068 | 81.1414 | 38.5133 | 34.1816 | 36.3749 | 39.0068 | 41.4414 | 168 | 166.75 | 225.25 | 305.5 | 384.75 | 71.6595 | 67.6907 | 69.7002 | 72.1116 | 74.3422 | 31.9595 | 27.9907 | 30.0002 | 32.4116 | 34.6422 | 79.5 | 73 | 101.75 | 149 | 193.5 | 869.76 | 703.569 | 888.5981 | 1185.8571 | 1501.7171
Powercor | Wemen | WMN | zss | 66/22 | 33 | 17.2 | 33 | 20.2 | 46 | 142.6833 | -34.7539 | 142.6833 | -34.7539 | 159 | 42.74% | capacity | Powercor’s preferred network option is to augment WMN line to WETS - BSP sub-transmission line. See the DAPR report for more details. | 754205 | 30% | 30% | 7542.05 | 2027 | 32154.5569 | 7.1932 | 7.34 | 0 | 0 | 5.3347 | 0.98 | 27.81 | 27.85 | 28.12 | 28.61 | 28.98 | 10.61 | 10.65 | 10.92 | 11.41 | 11.78 | 295 | 299 | 312 | 342.5 | 372 | 24.25 | 24.3 | 24.54 | 24.97 | 25.28 | 7.05 | 7.1 | 7.34 | 7.77 | 8.08 | 129.5 | 131 | 135.5 | 144.5 | 150.5 | 497.649 | 504.782 | 538.983 | 605.374 | 656.44
Powercor | Cohuna #2 Transformer Replacement | CHA | zss | 66/22 | 15.2 | 0 | 15.2 | 0 | 26 | 144.2195 | -35.8803 | 144.2195 | -35.8803 | 2740 | 62.41% | asset condition | Powercor’s preferred network option is to replace the #2 transformer at CHA. See the DAPR report for more details. | 7530000 | 30% | 30% | 75300 | 2027 | 321031.833 | 17.9732 | 18.34 | 0 | 0 | 1.9434 | 0.98 | 26.89 | 26.39 | 26.47 | 26.88 | 27.15 | 26.89 | 26.39 | 26.47 | 26.88 | 27.15 | 8760 | 8760 | 8760 | 8760 | 8760 | 18.82 | 18.49 | 18.34 | 18.45 | 18.5 | 18.82 | 18.49 | 18.34 | 18.45 | 18.5 | 8760 | 8760 | 8760 | 8760 | 8760 | 71655 | 70228 | 70459 | 71627 | 72369
Powercor | Geelong CB C 66kV Circuit Breaker | GL | zss | 66 | 0 | 0 | 0 | 0 | 80 | 144.3404 | -38.1286 | 144.3404 | -38.1286 | 18367 | 92.19% | asset condition | Powercor’s preferred network option is to replace the 66kV Bus tie circuit breaker C at GL. See the DAPR report for more details. | 450000 | 30% | 30% | 4500 | 2027 | 19185.1693 | 42.1047 | 42.53 | 0 | 0 | 14.4895 | 0.99 | 42.21 | 45.47 | 46.21 | 46.92 | 47.48 | 42.21 | 45.47 | 46.21 | 46.92 | 47.48 | - | - | - | - | - | 38.29 | 41.62 | 42.53 | 43.26 | 43.79 | 38.29 | 41.62 | 42.53 | 43.26 | 43.79 | - | - | - | - | - | - | - | - | - | -
Powercor | Mooroopna #1 Transformer Replacement | MNA | zss | 66/22 | 37 | 0 | 42.5 | 0 | 66 | 145.3491 | -36.3757 | 145.3491 | -36.3757 | 9136 | 83.64% | asset condition | Powercor’s preferred network option is to replace the #1 transformer at MNA. See the DAPR report for more details. | 7471321 | 30% | 30% | 74713.21 | 2028 | 318530.1296 | 43.953 | 44.85 | 0 | 0 | 10.6694 | 0.98 | 48.59 | 48.89 | 49.4 | 50.05 | 50.53 | 48.59 | 48.89 | 49.4 | 50.05 | 50.53 | 8760 | 8760 | 8760 | 8760 | 8760 | 43.64 | 43.9 | 44.32 | 44.85 | 45.32 | 43.64 | 43.9 | 44.32 | 44.85 | 45.32 | 8760 | 8760 | 8760 | 8760 | 8760 | 184714 | 185878 | 187734 | 190173 | 191993
Powercor | Ouyen 1, 3, 5, 7 22kV Circuit Breaker | OYN | zss | 22 | 32 | 15.2 | 38.8 | 15.2 | 26 | 142.3153 | -35.0584 | 142.3153 | -35.0584 | 2092 | 65.81% | asset condition | Powercor’s preferred network option is to replace the 22kV circuit breakers at OYN. See the DAPR report for more details. | 840000 | 30% | 30% | 8400 | 2026 | 35812.316 | 7.087 | 7.46 | 0 | 0 | 0 | 0.95 | 7.96 | 7.87 | 7.85 | 7.86 | 7.84 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | 7.55 | 7.46 | 7.43 | 7.44 | 7.41 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | -
Powercor | Shepparton North #2 Transformer Replacement | SHN | zss | 66/22 | 40 | 0 | 44.1 | 0 | 66 | 145.4114 | -36.3537 | 145.4114 | -36.3537 | 9575 | 85.62% | asset condition | Powercor’s preferred network option is to replace the #2 transformer at SHN. See the DAPR report for more details. | 6772571 | 30% | 30% | 67725.71 | 2030 | 288739.825 | 36.25 | 36.25 | 0 | 0 | 0 | 1 | 42.39 | 38.73 | 39.16 | 39.78 | 40.25 | 42.39 | 38.73 | 39.16 | 39.78 | 40.25 | 8760 | 8760 | 8760 | 8760 | 8760 | 38.29 | 34.74 | 35.22 | 35.82 | 36.25 | 38.29 | 34.74 | 35.22 | 35.82 | 36.25 | 8760 | 8760 | 8760 | 8760 | 8760 | 143883 | 131084 | 132616 | 134798 | 136468
Note on AA1: Lin, Tim: E.g. contracting backup generators in a hospital to become embedded generators during unuasually high peaks

## Sub-T Aug Sum
Sub transmission line | Season | Line N Import Rating (MVA) | Line Power Factor at Maximum Demand | Embedded Generation Capacity (MVA) | Load Transfer Capability (MVA) | Hours load is > 95% of Maximum Demand (Hrs) | Actual Maximum Demand (MVA) | 50% POE |  |  |  |  | 50% POE load above N Import Rating (%) | 50% POE load above N Import Rating (MVA) | 50% POE
[8 empty] | Forecast Maximum Demand (MVA) | [6 empty] | Energy at Risk (MWh) |  |  |  |  | Hours at Risk (Hrs)
|  |  | 2024 | 2024 | 2025 | 2024 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2025 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029
ATS-ATD | S | 102.3 | 0.99502 | 0 | - | - | 20.1 | 18 | 29.6 | 61.5 | 80 | 83.3 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-ATD | W | 130.3 | 0.99502 | 0 | - | - | 20.1 | 20.9 | 44.9 | 73.2 | 82.7 | 83.3 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-NRB | S | 52.6 | 0.85944 | 0 | - | - | 24.9 | 26.7 | 26.5 | 26.5 | 26.5 | 26.5 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-NRB | W | 52.6 | 0.91758 | 0 | - | - | 36.4 | 36.6 | 36.7 | 36.9 | 37.6 | 37.5 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GHP | S | 74.3 | 0.98936 | 18.9423 | - | - | 65.8 | 66.7 | 68.2 | 69.6 | 71.3 | 72.7 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GHP | W | 87.5 | 0.98961 | 18.9423 | - | - | 67.4 | 60.8 | 62.3 | 64 | 65.5 | 66.5 | - | - | - | - | - | - | - | - | - | - | - | -
BETS-MRO | S | 76.6 | 0.93529 | 13.5952 | - | - | 64.9 | 59.1 | 59.6 | 60.7 | 61.6 | 62 | - | - | - | - | - | - | - | - | - | - | - | -
BETS-MRO | W | 89.2 | 0.93846 | 13.5952 | - | - | 65 | 56.6 | 57.1 | 57.4 | 58.5 | 59.7 | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-CHM | S | 26.2 | 0.91304 | 1.3729 | - | - | 2.3 | 2.4 | 2.3 | 2.3 | 2.3 | 2.3 | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-CHM | W | 35.4 | 0.91304 | 1.3729 | - | - | 2.3 | 2.2 | 2.2 | 2.1 | 2.1 | 2.1 | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SA1 | S | 116.6 | 0.97635 | 38.9298 | - | - | 88.8 | 90.4 | 92.9 | 95 | 97.5 | 99.3 | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SA1 | W | 122.3 | 0.97635 | 38.9298 | - | - | 88.8 | 70.3 | 72.1 | 74 | 76.2 | 77.6 | - | - | - | - | - | - | - | - | - | - | - | -
BGR-ART | S | 45.7 | 0.99342 | 14.1862 | - | - | 15.2 | 12.6 | 12.4 | 12.4 | 12.5 | 12.5 | - | - | - | - | - | - | - | - | - | - | - | -
BGR-ART | W | 47.4 | 0.99422 | 14.1862 | - | - | 17.3 | 13.9 | 13.7 | 13.7 | 13.8 | 13.8 | - | - | - | - | - | - | - | - | - | - | - | -
MBN-DTN | S | 74.3 | 0.94521 | 19.9415 | - | - | 21.9 | 23.9 | 24 | 24 | 24.1 | 24.2 | - | - | - | - | - | - | - | - | - | - | - | -
MBN-DTN | W | 86.9 | 0.94421 | 19.9415 | - | - | 23.3 | 25.6 | 25.7 | 25.7 | 25.9 | 25.9 | - | - | - | - | - | - | - | - | - | - | - | -
BETS-CMN | S | 64 | 0.99652 | 29.0396 | - | - | 57.4 | 54.4 | 54.8 | 55.2 | 55.6 | 56.3 | - | - | - | - | - | - | - | - | - | - | - | -
BETS-CMN | W | 65.2 | 0.99652 | 29.0396 | - | - | 57.5 | 50.8 | 51 | 51.6 | 52.3 | 52.8 | - | - | - | - | - | - | - | - | - | - | - | -
CMN-MRO | S | 26.3 | 0.98252 | 42.6348 | 3.2008 | - | 28.6 | 27.7 | 27.8 | 27.9 | 27.8 | 28.5 | - | - | - | - | - | - | - | - | - | - | - | -
CMN-MRO | W | 35.4 | 0.98311 | 42.6348 | 3.2008 | - | 29.6 | 28.7 | 28.9 | 28.6 | 29.2 | 29.4 | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-STL2 | S | 25.7 | 0.99685 | 6.6493 | 0.9 | 0.5 | 31.7 | 30.5 | 30.5 | 29.4 | 29.7 | 29.6 | 18.68% | 4.8 | 4.2563 | 4.2563 | 2.5503 | 2.9684 | 2.8292 | 3 | 3 | 1.5 | 1.5 | 1.5
HOTS-STL2 | W | 34.9 | 1 | 6.6493 | 0.9 | 0.75 | 30.8 | 31.2 | 29.9 | 30.2 | 30.2 | 30.2 | - | - | - | - | - | - | - | - | - | - | - | -
BPA-HTH | S | 17.7 | 0.97297 | 0 | - | - | 3.7 | 3.7 | 3.7 | 3.8 | 3.8 | 3.8 | - | - | - | - | - | - | - | - | - | - | - | -
BPA-HTH | W | 35.4 | 0.95455 | 0 | - | - | 4.4 | 4.5 | 4.5 | 4.5 | 4.6 | 4.6 | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-STL1 | S | 49.2 | 0.99099 | 6.6493 | - | - | 33.3 | 32 | 32 | 31 | 31.2 | 31.1 | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-STL1 | W | 57.2 | 0.99385 | 6.6493 | - | - | 32.5 | 33 | 31.7 | 31.9 | 31.9 | 32 | - | - | - | - | - | - | - | - | - | - | - | -
AL-BLTS | S | 91.4 | 0.87942 | 12.6295 | - | - | 76.3 | 77.9 | 78.2 | 78.6 | 78.9 | 79.3 | - | - | - | - | - | - | - | - | - | - | - | -
AL-BLTS | W | 91.4 | 0.88162 | 12.6295 | - | - | 88.7 | 85.2 | 85.8 | 86.1 | 86.8 | 87 | - | - | - | - | - | - | - | - | - | - | - | -
BETS-BGO | S | 109.7 | 0.96507 | 17.7292 | 9.7549 | - | 91.6 | 93.7 | 94.6 | 95.7 | 97.3 | 99.4 | - | - | - | - | - | - | - | - | - | - | - | -
BETS-BGO | W | 114.3 | 0.96417 | 17.7292 | 9.7549 | - | 92.1 | 82.3 | 83.1 | 84.3 | 86.1 | 87.1 | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-MDA2 | S | 104 | 0.9247 | 20.3504 | - | - | 99.6 | 110.5 | 110.6 | 111.1 | 111.5 | 112.9 | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-MDA2 | W | 114.3 | 0.92828 | 20.3504 | - | - | 97.6 | 83.1 | 83.1 | 83.5 | 84.4 | 85 | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-MDA1 | S | 104 | 0.91566 | 20.3504 | - | - | 91.3 | 101.5 | 101.7 | 102 | 103 | 104.2 | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-MDA1 | W | 114.3 | 0.91676 | 20.3504 | - | - | 90.1 | 75.9 | 75.9 | 76.3 | 77.1 | 77.4 | - | - | - | - | - | - | - | - | - | - | - | -
HKT-LV | S | 135.5 | 0.97816 | 64.4246 | - | - | 109.9 | 106.4 | 111 | 108.8 | 115.5 | 120.7 | - | - | - | - | - | - | - | - | - | - | - | -
HKT-LV | W | 142.3 | 0.9782 | 64.4246 | - | - | 110.1 | 85.2 | 89.3 | 89.7 | 95.9 | 99.5 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-FDN | S | 102.9 | 0.95495 | 0 | - | - | 33.3 | 35.5 | 36.2 | 36.5 | 37.4 | 37.7 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-FDN | W | 134.9 | 0.95821 | 0 | - | - | 33.5 | 37.2 | 37.5 | 37.8 | 38.4 | 38.5 | - | - | - | - | - | - | - | - | - | - | - | -
WETS-WSF | S | 84.6 | 0.99548 | 0 | - | - | 22.1 | 21.9 | 21.9 | 22.1 | 22.5 | 22.8 | - | - | - | - | - | - | - | - | - | - | - | -
WETS-WSF | W | 106.3 | 0.99602 | 0 | - | - | 25.1 | 18.3 | 18.4 | 18.6 | 19 | 19.1 | - | - | - | - | - | - | - | - | - | - | - | -
WSF-WMN | S | 31.4 | 0.99548 | 1.7882 | - | - | 22.1 | 21.8 | 21.9 | 22.1 | 22.5 | 22.8 | - | - | - | - | - | - | - | - | - | - | - | -
WSF-WMN | W | 43.4 | 0.996 | 1.7882 | - | - | 25 | 18.3 | 18.4 | 18.6 | 19 | 19.1 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-AC | S | 102.3 | 0.88904 | 0.481 | - | - | 74.8 | 75.9 | 76.2 | 76.7 | 77.1 | 77.9 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-AC | W | 108 | 0.89211 | 0.481 | - | - | 86.2 | 83.8 | 83.5 | 84.3 | 85.2 | 85.3 | - | - | - | - | - | - | - | - | - | - | - | -
GB-GL | S | 89.7 | 0.94674 | 20.4248 | 7.621 | - | 92 | 88.2 | 91.5 | 92.6 | 93.7 | 94.9 | - | - | - | - | - | - | - | - | - | - | - | -
GB-GL | W | 100.6 | 0.94812 | 20.4248 | 7.621 | - | 90.6 | 70.7 | 73.7 | 74.7 | 75.8 | 76.5 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-SHN2 | S | 88 | 0.99085 | 18.8331 | - | - | 32.8 | 39.4 | 35.6 | 35.7 | 36.8 | 37.4 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-SHN2 | W | 112 | 0.99088 | 18.8331 | - | - | 32.9 | 33.8 | 29.2 | 29.6 | 30 | 30.2 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-HTN | S | 47.4 | 0.84921 | 10.833 | - | - | 25.2 | 27 | 26.8 | 26.3 | 26.8 | 26.7 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-HTN | W | 48 | 0.9386 | 10.833 | - | - | 34.2 | 35.3 | 35.3 | 35 | 35.9 | 36 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-SHN1 | S | 88 | 0.99085 | 18.8331 | - | - | 32.8 | 39.4 | 35.6 | 35.7 | 36.8 | 37.4 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-SHN1 | W | 112 | 0.99088 | 18.8331 | - | - | 32.9 | 33.8 | 29.2 | 29.6 | 30 | 30.2 | - | - | - | - | - | - | - | - | - | - | - | -
KWF-NHL | S | 44 | 1 | 4.3923 | - | - | 8.2 | 12.6 | 12.4 | 12.4 | 12.4 | 12.4 | - | - | - | - | - | - | - | - | - | - | - | -
KWF-NHL | W | 43.4 | 1 | 4.3923 | - | - | 9 | 13.8 | 13.6 | 13.6 | 13.6 | 13.6 | - | - | - | - | - | - | - | - | - | - | - | -
WETS-BPA | S | 31.4 | 1 | 0 | - | - | 6.6 | 6.8 | 6.7 | 6.7 | 6.8 | 6.8 | - | - | - | - | - | - | - | - | - | - | - | -
WETS-BPA | W | 43.4 | 1 | 0 | - | - | 7.4 | 7 | 7 | 7.1 | 7.1 | 7.1 | - | - | - | - | - | - | - | - | - | - | - | -
KRT-PLD1/CWF | S | 40 | 0.9878 | 23.1277 | - | - | 16.4 | 14.3 | 14 | 13.9 | 13.8 | 13.8 | - | - | - | - | - | - | - | - | - | - | - | -
KRT-PLD1/CWF | W | 45.7 | 0.99408 | 23.1277 | - | - | 16.9 | 17.4 | 17.3 | 17.3 | 17.4 | 17.3 | - | - | - | - | - | - | - | - | - | - | - | -
NKA-CME | S | 74.3 | 0.98714 | 41.5972 | - | - | 31.1 | 35.7 | 35.8 | 36 | 36.3 | 36.6 | - | - | - | - | - | - | - | - | - | - | - | -
NKA-CME | W | 86.9 | 0.98485 | 41.5972 | - | - | 33 | 30.8 | 30.8 | 31.1 | 31.4 | 31.6 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-WBE | S | 109.7 | 0.95228 | 65.516 | 10.0979 | 1 | 136.2 | 132.8 | 138.5 | 122.6 | 127.2 | 131.4 | 21.06% | 23.1 | 151.0866 | 235.5231 | 50.2246 | 88.5744 | 133.5867 | 15.75 | 20.5 | 7.75 | 11 | 14.25
ATS-WBE | W | 134.9 | 0.95182 | 65.516 | 10.0979 | 1.25 | 137 | 97.7 | 102 | 91.2 | 94.6 | 97.4 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-CDN | S | 76.6 | 0.99598 | 5.6786 | - | - | 49.7 | 53.9 | 54.2 | 55.5 | 56.1 | 56.6 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-CDN | W | 85.7 | 0.99585 | 5.6786 | - | - | 48.2 | 51.5 | 53.6 | 54.2 | 54.9 | 55 | - | - | - | - | - | - | - | - | - | - | - | -
NSF-NKA | S | 102.9 | 0.97582 | 23.1854 | - | - | 57.9 | 64.8 | 65.2 | 66.8 | 67.6 | 68.4 | - | - | - | - | - | - | - | - | - | - | - | -
NSF-NKA | W | 114.3 | 0.97479 | 23.1854 | - | - | 59.5 | 54.8 | 55.6 | 56.4 | 57.2 | 57.5 | - | - | - | - | - | - | - | - | - | - | - | -
MDA-MBN | S | 74.3 | 0.94171 | 40.2919 | - | - | 54.9 | 61.9 | 62.4 | 62.9 | 63.6 | 64.2 | - | - | - | - | - | - | - | - | - | - | - | -
MDA-MBN | W | 86.9 | 0.94465 | 40.2919 | - | - | 54.2 | 42.6 | 42.8 | 43.2 | 43.7 | 44.1 | - | - | - | - | - | - | - | - | - | - | - | -
BAN-BGR | S | 46.3 | 0.98758 | 44.3748 | - | - | 16.1 | 13.1 | 13 | 12.9 | 13 | 13.1 | - | - | - | - | - | - | - | - | - | - | - | -
BAN-BGR | W | 49.7 | 0.98378 | 44.3748 | - | - | 18.5 | 14.6 | 14.4 | 14.4 | 14.4 | 14.4 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-TYA | S | 102.3 | 0.70039 | 0 | - | - | 25.7 | 36.6 | 35.3 | 34 | 33.9 | 34.4 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-TYA | W | 130.3 | 0.75 | 0 | - | - | 26.4 | 29.2 | 39.1 | 39.3 | 37.7 | 36.7 | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-TNA2 | S | 109.7 | 0.97842 | 65.2379 | 36.962 | 1.25 | 120.5 | 129.3 | 144.6 | 112.7 | 118.1 | 122.6 | 17.87% | 19.6 | 74.3423 | 299.7399 | 3.5186 | 13.4073 | 30.9607 | 8 | 25.75 | 1 | 2.75 | 4.75
DPTS-TNA2 | W | 134.9 | 0.97842 | 65.2379 | 36.962 | 4 | 120.5 | 113.8 | 139 | 97.1 | 101 | 104.4 | - | - | - | - | - | - | - | - | - | - | - | -
KGTS-SHL | S | 40 | 0.9902 | 44.9393 | - | - | 20.4 | 22 | 21.5 | 21.4 | 21.4 | 21.4 | - | - | - | - | - | - | - | - | - | - | - | -
KGTS-SHL | W | 49.7 | 0.96164 | 44.9393 | - | - | 36.5 | 26.3 | 26.1 | 26.1 | 26.2 | 26.1 | - | - | - | - | - | - | - | - | - | - | - | -
BETS-EHK | S | 111.4 | 0.9587 | 23.4658 | - | - | 92 | 94.6 | 95.5 | 96.6 | 98.2 | 100.1 | - | - | - | - | - | - | - | - | - | - | - | -
BETS-EHK | W | 111.4 | 0.95887 | 23.4658 | - | - | 92.4 | 82.5 | 83.3 | 84.6 | 86.3 | 87.3 | - | - | - | - | - | - | - | - | - | - | - | -
GHP-BCG | S | 109.7 | 0.97101 | 18.9423 | - | - | 34.5 | 34 | 34.2 | 34.8 | 35.8 | 36.6 | - | - | - | - | - | - | - | - | - | - | - | -
GHP-BCG | W | 134.9 | 0.97101 | 18.9423 | - | - | 34.5 | 32.2 | 33.1 | 34 | 34.6 | 35.1 | - | - | - | - | - | - | - | - | - | - | - | -
TRG-WBL1 | S | 47.4 | 0.94256 | 28.6721 | - | - | 38.3 | 37.7 | 36.8 | 36.7 | 36.7 | 37.3 | - | - | - | - | - | - | - | - | - | - | - | -
TRG-WBL1 | W | 49.7 | 0.94431 | 28.6721 | - | - | 41.3 | 40.4 | 40.9 | 41.2 | 41.6 | 41.8 | - | - | - | - | - | - | - | - | - | - | - | -
TRG-WBL2 | S | 45.7 | 0.98251 | 28.6721 | - | - | 34.3 | 33.5 | 32.7 | 32.6 | 32.6 | 33.1 | - | - | - | - | - | - | - | - | - | - | - | -
TRG-WBL2 | W | 46.3 | 0.97849 | 28.6721 | - | - | 37.2 | 36.1 | 36.1 | 36.3 | 36.9 | 37 | - | - | - | - | - | - | - | - | - | - | - | -
AWT-LV | S | 109.7 | 0.97896 | 64.4246 | 13.1463 | - | 109.3 | 105.8 | 115.1 | 120 | 131.8 | 144.1 | - | - | - | - | - | - | - | - | - | - | - | -
AWT-LV | W | 134.9 | 0.97876 | 64.4246 | 13.1463 | - | 108.3 | 84.1 | 91.2 | 93.6 | 100.6 | 109.2 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GCY | S | 90.3 | 0.94011 | 11.3272 | 16.4 | 1 | 110.2 | 105.4 | 109.2 | 110.3 | 111.8 | 113 | 16.72% | 15.1 | 72.091 | 109.8862 | 124.2 | 144.9026 | 162.7709 | 10 | 15.5 | 17 | 19 | 20
GTS-GCY | W | 96.6 | 0.94297 | 11.3272 | 16.4 | 3 | 105.2 | 83.2 | 86.5 | 87.6 | 89 | 89.7 | - | - | - | - | - | - | - | - | - | - | - | -
FDN-CRO | S | 109.7 | 0.95706 | 5.4569 | - | - | 32.6 | 33.9 | 34.5 | 34.8 | 35.7 | 36.1 | - | - | - | - | - | - | - | - | - | - | - | -
FDN-CRO | W | 134.9 | 0.95706 | 5.4569 | - | - | 32.6 | 35 | 35.2 | 35.6 | 36.1 | 36.2 | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAN2 | S | 96 | 0.91163 | 44.3748 | - | - | 89.4 | 88 | 94.9 | 74.6 | 75.6 | 76.7 | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAN2 | W | 114.3 | 0.91348 | 44.3748 | - | - | 89 | 91 | 73.7 | 74.5 | 76 | 76.7 | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAN1 | S | 96 | 0.91704 | 44.3748 | - | - | 89.2 | 87.8 | 94.7 | 74.7 | 75.6 | 76.7 | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAN1 | W | 114.3 | 0.91779 | 44.3748 | - | - | 88.8 | 90.8 | 73.7 | 74.6 | 76 | 76.7 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-SHP | S | 101.7 | 1 | 13.4153 | - | - | 36.9 | 40.4 | 40.2 | 40.3 | 40.8 | 41 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-SHP | W | 116 | 1 | 13.4153 | - | - | 36.6 | 30.4 | 30.3 | 30.6 | 30.9 | 31 | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-ATD | S | 97.2 | 1 | 0 | - | - | 20 | 22 | 29.5 | 61.3 | 79.6 | 82.8 | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-ATD | W | 125.7 | 0.93627 | 0 | - | - | 20.4 | 21.8 | 44.8 | 72.8 | 82.3 | 82.8 | - | - | - | - | - | - | - | - | - | - | - | -
STL-ART | S | 38.3 | 0.96313 | 20.8355 | - | - | 21.7 | 19.5 | 19.8 | 18.4 | 18.7 | 18.7 | - | - | - | - | - | - | - | - | - | - | - | -
STL-ART | W | 43.4 | 0.97403 | 20.8355 | - | - | 23.1 | 23 | 21.6 | 21.9 | 22 | 22.1 | - | - | - | - | - | - | - | - | - | - | - | -
BETS-CTN | S | 26.3 | 0.99163 | 17.2207 | - | - | 23.9 | 23.8 | 23.5 | 23.5 | 23.7 | 23.9 | - | - | - | - | - | - | - | - | - | - | - | -
BETS-CTN | W | 30.3 | 0.99163 | 17.2207 | - | - | 23.9 | 20.6 | 20.5 | 20.6 | 20.8 | 20.9 | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-HSM2 | S | 49.2 | 0.99007 | 20.6709 | - | - | 40.3 | 42.9 | 42.5 | 42.6 | 42.8 | 42.9 | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-HSM2 | W | 52.6 | 0.99007 | 20.6709 | - | - | 40.3 | 35.6 | 35.4 | 35.6 | 35.9 | 35.8 | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-HSM1 | S | 49.2 | 0.99012 | 20.6709 | - | - | 40.5 | 43.1 | 42.7 | 42.8 | 43 | 43.2 | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-HSM1 | W | 52.6 | 0.99012 | 20.6709 | - | - | 40.5 | 35.8 | 35.6 | 35.7 | 36 | 36 | - | - | - | - | - | - | - | - | - | - | - | -
HTH-OYN | S | 17.7 | 0.94118 | 3.5341 | - | - | 6.8 | 7.3 | 7.2 | 7.2 | 7.2 | 7.2 | - | - | - | - | - | - | - | - | - | - | - | -
HTH-OYN | W | 35.4 | 0.95775 | 3.5341 | - | - | 7.1 | 6.7 | 6.6 | 6.6 | 6.7 | 6.6 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-CRO | S | 91.4 | 0.95732 | 5.4569 | - | - | 32.8 | 35.5 | 36.2 | 36.4 | 37.4 | 37.7 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-CRO | W | 91.4 | 0.95758 | 5.4569 | - | - | 33 | 36.7 | 37.5 | 37.8 | 38.4 | 38.5 | - | - | - | - | - | - | - | - | - | - | - | -
SHP-KYM | S | 84.6 | 0.88584 | 26.3305 | - | - | 21.9 | 26.6 | 26.7 | 26.6 | 26.7 | 26.8 | - | - | - | - | - | - | - | - | - | - | - | -
SHP-KYM | W | 106.3 | 0.87736 | 26.3305 | - | - | 21.2 | 22.4 | 22.4 | 22.3 | 22.5 | 22.5 | - | - | - | - | - | - | - | - | - | - | - | -
HCP-WBE | S | 109.7 | 0.98159 | 65.516 | 10.0979 | 0.5 | 124.9 | 121.9 | 126.7 | 113.4 | 117.1 | 120.5 | 11.12% | 12.2 | 6.7358 | 13.8092 | 1.4621 | 3.2663 | 5.4788 | 1.25 | 2.25 | 0.5 | 0.75 | 1
HCP-WBE | W | 134.9 | 0.9808 | 65.516 | 10.0979 | 1.25 | 125 | 90.7 | 94.5 | 84.7 | 87.9 | 90.4 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-KYM1 | S | 79.4 | 0.998 | 12.9152 | - | - | 50 | 53.5 | 53.3 | 53.5 | 54.1 | 54.5 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-KYM1 | W | 90.3 | 0.998 | 12.9152 | - | - | 49.9 | 39.6 | 39.6 | 40 | 40.5 | 40.6 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-KYM2 | S | 79.4 | 0.99802 | 12.9152 | - | - | 50.6 | 54.1 | 53.9 | 54.1 | 54.7 | 55.1 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-KYM2 | W | 90.3 | 1 | 12.9152 | - | - | 50.4 | 40.1 | 40.1 | 40.5 | 40.9 | 41.1 | - | - | - | - | - | - | - | - | - | - | - | -
YSW-BMH | S | 36.6 | 0.95469 | 14.8598 | - | - | 30.9 | 31.8 | 33 | 34.2 | 35.2 | 36.3 | - | - | - | - | - | - | - | - | - | - | - | -
YSW-BMH | W | 37.2 | 0.95724 | 14.8598 | - | - | 30.4 | 27 | 28.2 | 29.5 | 30.4 | 31.5 | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-TNA1 | S | 109.7 | 0.98005 | 65.2379 | 36.962 | 1.25 | 120.3 | 129.1 | 144.6 | 112.5 | 117.9 | 122.4 | 17.68% | 19.4 | 73.823 | 295.8615 | 3.1093 | 12.4643 | 29.6572 | 8.5 | 22.25 | 1 | 2.5 | 4.5
DPTS-TNA1 | W | 134.9 | 0.98005 | 65.2379 | 36.962 | 0.5 | 120.3 | 113.6 | 138.9 | 97 | 100.9 | 104.3 | - | - | - | - | - | - | - | - | - | - | - | -
WPD-TQY1 | S | 107 | 0.99171 | 51.2568 | - | - | 36.2 | 32.9 | 35 | 35.4 | 36.1 | 37.6 | - | - | - | - | - | - | - | - | - | - | - | -
WPD-TQY1 | W | 108.6 | 0.99174 | 51.2568 | - | - | 36.3 | 35.3 | 36.7 | 37.4 | 39 | 39.7 | - | - | - | - | - | - | - | - | - | - | - | -
KYM-ECA2 | S | 45.7 | 0.9975 | 32.7942 | - | - | 40 | 43.4 | 43.6 | 44 | 44.5 | 45.1 | - | - | - | - | - | - | - | - | - | - | - | -
KYM-ECA2 | W | 53.2 | 0.99752 | 32.7942 | - | - | 40.3 | 32.2 | 32.2 | 32.5 | 32.9 | 33.1 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-AWT | S | 109.7 | 0.97527 | 0 | 13.1463 | - | 113.2 | 110.4 | 120.4 | 128 | 143.5 | 158.3 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-AWT | W | 134.9 | 0.97509 | 0 | 13.1463 | - | 112.4 | 88.3 | 97.2 | 103 | 113.4 | 123.6 | - | - | - | - | - | - | - | - | - | - | - | -
KYM-ECA1 | S | 45.7 | 0.99496 | 32.7942 | - | - | 39.7 | 43.1 | 43 | 43.4 | 43.9 | 44.1 | - | - | - | - | - | - | - | - | - | - | - | -
KYM-ECA1 | W | 52.6 | 0.99499 | 32.7942 | - | - | 39.9 | 32 | 31.9 | 32.2 | 32.6 | 32.8 | - | - | - | - | - | - | - | - | - | - | - | -
KGTS-GSF | S | 48.6 | 0.99485 | 0 | - | - | 19.4 | 20.9 | 20.5 | 20.3 | 20.3 | 20.3 | - | - | - | - | - | - | - | - | - | - | - | -
KGTS-GSF | W | 52.6 | 0.96657 | 0 | - | - | 32.9 | 24.6 | 24.4 | 24.4 | 24.5 | 24.4 | - | - | - | - | - | - | - | - | - | - | - | -
GLE-DDL1 | S | 74.3 | 0.98191 | 64.0766 | - | - | 77.4 | 77.7 | 72.6 | 74.8 | 78.1 | 81 | - | - | - | - | - | - | - | - | - | - | - | -
GLE-DDL1 | W | 86.9 | 0.98191 | 64.0766 | - | - | 77.4 | 53 | 55 | 57.2 | 59.6 | 61.4 | - | - | - | - | - | - | - | - | - | - | - | -
GLE-DDL2 | S | 74.3 | 0.98084 | 64.0766 | - | - | 78.3 | 78.7 | 73.2 | 75.8 | 79.1 | 82.1 | - | - | - | - | - | - | - | - | - | - | - | -
GLE-DDL2 | W | 86.9 | 0.98084 | 64.0766 | - | - | 78.3 | 53.4 | 55.5 | 57.6 | 60.1 | 61.9 | - | - | - | - | - | - | - | - | - | - | - | -
GCY-GL | S | 109.7 | 0.96341 | 29.8298 | - | - | 57.4 | 54 | 57.6 | 58.5 | 59.5 | 60.1 | - | - | - | - | - | - | - | - | - | - | - | -
GCY-GL | W | 134.9 | 0.96679 | 29.8298 | - | - | 54.2 | 46.6 | 49.6 | 50.4 | 51.3 | 51.8 | - | - | - | - | - | - | - | - | - | - | - | -
GSF-SHL | S | 76.6 | 0.99474 | 44.9393 | - | - | 19 | 20.4 | 20 | 19.9 | 19.9 | 19.9 | - | - | - | - | - | - | - | - | - | - | - | -
GSF-SHL | W | 89.2 | 0.97476 | 44.9393 | - | - | 31.7 | 24.1 | 23.9 | 23.9 | 24 | 23.9 | - | - | - | - | - | - | - | - | - | - | - | -
YSF-HTH | S | 17.7 | 0.9434 | 0 | - | - | 10.6 | 10.7 | 10.5 | 10.2 | 10.6 | 10.6 | - | - | - | - | - | - | - | - | - | - | - | -
YSF-HTH | W | 35.4 | 0.97248 | 0 | - | - | 10.9 | 9.4 | 9.3 | 9.3 | 9.3 | 9.3 | - | - | - | - | - | - | - | - | - | - | - | -
KRT-PLD2/YWF | S | 29.7 | 0.99422 | 23.1277 | - | - | 17.3 | 15.4 | 15.1 | 15 | 14.9 | 14.9 | - | - | - | - | - | - | - | - | - | - | - | -
KRT-PLD2/YWF | W | 29.7 | 1 | 23.1277 | - | - | 17.8 | 18.5 | 18.3 | 18.4 | 18.4 | 18.4 | - | - | - | - | - | - | - | - | - | - | - | -
CTN-CBW | S | 98.9 | 0 | 17.2207 | - | - | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | - | - | - | - | - | - | - | - | - | - | - | -
CTN-CBW | W | 106.3 | 0 | 17.2207 | - | - | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-HCP | S | 109.7 | 0.95364 | 0 | 10.0979 | 0.5 | 135.9 | 132.5 | 138.2 | 122.7 | 126.9 | 131 | 20.78% | 22.8 | 49.7645 | 93.1858 | 12.5903 | 23.2021 | 41.3486 | 7.5 | 11 | 2 | 4.25 | 6.5
ATS-HCP | W | 134.9 | 0.95315 | 0 | 10.0979 | 1.25 | 136.6 | 97.6 | 101.8 | 91 | 94.5 | 97.2 | - | - | - | - | - | - | - | - | - | - | - | -
KRT-WBL | S | 46.9 | 0.861 | 22.7987 | - | - | 25.9 | 24.5 | 23.9 | 23.8 | 23.8 | 24.4 | - | - | - | - | - | - | - | - | - | - | - | -
KRT-WBL | W | 47.4 | 0.8374 | 22.7987 | - | - | 24.6 | 19.9 | 20 | 20.3 | 20.6 | 20.7 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-SCI | S | 90.8 | 0.78218 | 0 | - | - | 40.4 | 41 | 41.1 | 41.2 | 41.4 | 41.5 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-SCI | W | 116 | 0.77916 | 0 | - | - | 40.3 | 41.1 | 41.2 | 41.3 | 41.6 | 41.5 | - | - | - | - | - | - | - | - | - | - | - | -
SBY-GSB2 | S | 76.6 | 0.99273 | 18.1573 | - | - | 55 | 49.1 | 49.8 | 51 | 52.4 | 53.8 | - | - | - | - | - | - | - | - | - | - | - | -
SBY-GSB2 | W | 89.2 | 0.98962 | 18.1573 | - | - | 57.8 | 57.2 | 58.4 | 60 | 61.8 | 63.1 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-WNS | S | 91.4 | 0.94373 | 0 | - | - | 62.2 | 69.1 | 69.5 | 71.3 | 72.9 | 73.7 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-WNS | W | 91.4 | 0.94072 | 0 | - | - | 64.1 | 57.7 | 58.6 | 59.6 | 60.5 | 60.8 | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-YSF | S | 84.6 | 0.92661 | 0 | - | - | 10.9 | 11 | 10.8 | 10.5 | 11 | 10.9 | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-YSF | W | 106.3 | 0.96396 | 0 | - | - | 11.1 | 9.7 | 9.6 | 9.5 | 9.6 | 9.6 | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-SU1 | S | 109.7 | 0.96474 | 32.1099 | - | - | 93.6 | 93.3 | 97.4 | 102.2 | 105 | 107.2 | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-SU1 | W | 133.7 | 0.96474 | 32.1099 | - | - | 93.6 | 80.4 | 83 | 87.5 | 89.7 | 91.3 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-BCG | S | 109.7 | 0.98296 | 0 | - | - | 76.3 | 78.1 | 80.5 | 82.2 | 84 | 85.6 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-BCG | W | 134.9 | 0.98483 | 0 | - | - | 79.1 | 74.4 | 76.3 | 78.4 | 80.1 | 81.3 | - | - | - | - | - | - | - | - | - | - | - | -
WPD-TQY2 | S | 107 | 0.99171 | 51.2568 | - | - | 36.2 | 32.9 | 35 | 35.4 | 36.7 | 37.6 | - | - | - | - | - | - | - | - | - | - | - | -
WPD-TQY2 | W | 108.6 | 0.99174 | 51.2568 | - | - | 36.3 | 35.8 | 36.7 | 37.5 | 39 | 39.7 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-LVN | S | 109.7 | 0.97111 | 13.257 | - | - | 79.6 | 89.6 | 93.3 | 93.9 | 95 | 95.8 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-LVN | W | 134.9 | 0.97111 | 13.257 | - | - | 79.6 | 93.9 | 95.3 | 96.3 | 97.7 | 98.5 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GB | S | 135.5 | 0.92883 | 1.9222 | 7.621 | - | 111 | 106.4 | 110 | 111.1 | 112.5 | 113.9 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GB | W | 142.3 | 0.93032 | 1.9222 | 7.621 | - | 106.2 | 83.4 | 86.6 | 87.7 | 89 | 89.8 | - | - | - | - | - | - | - | - | - | - | - | -
COB-CDN | S | 49.2 | 1 | 6.7909 | - | - | 30.8 | 32.6 | 32.9 | 34.1 | 34.6 | 35.1 | - | - | - | - | - | - | - | - | - | - | - | -
COB-CDN | W | 57.2 | 0.99668 | 6.7909 | - | - | 30.1 | 31.8 | 33.6 | 34 | 34.5 | 34.8 | - | - | - | - | - | - | - | - | - | - | - | -
KSF-RVL | S | 84.6 | 0.97382 | 5.4815 | - | - | 19.1 | 19 | 20.1 | 22.2 | 22.7 | 23.1 | - | - | - | - | - | - | - | - | - | - | - | -
KSF-RVL | W | 106.3 | 0.97778 | 5.4815 | - | - | 18 | 11.9 | 13.5 | 14.7 | 15 | 15.2 | - | - | - | - | - | - | - | - | - | - | - | -
BCG-WIN | S | 91.4 | 0.97877 | 16.3808 | - | - | 42.4 | 44.3 | 45.2 | 46.9 | 47.6 | 48 | - | - | - | - | - | - | - | - | - | - | - | -
BCG-WIN | W | 91.4 | 0.97908 | 16.3808 | - | - | 47.8 | 46.8 | 50.3 | 51.1 | 52 | 52.3 | - | - | - | - | - | - | - | - | - | - | - | -
CPL-AL | S | 91.4 | 0.8864 | 12.6295 | - | - | 66.9 | 69 | 69.2 | 69.5 | 69.7 | 69.9 | - | - | - | - | - | - | - | - | - | - | - | -
CPL-AL | W | 91.4 | 0.88808 | 12.6295 | - | - | 68.8 | 69.3 | 69.8 | 69.9 | 70.4 | 70.2 | - | - | - | - | - | - | - | - | - | - | - | -
SBY-GSB1 | S | 51.4 | 0.99638 | 18.1573 | - | - | 55.2 | 49.4 | 50.2 | 51.3 | 52.7 | 54.1 | - | - | - | - | - | - | - | - | - | - | - | -
SBY-GSB1 | W | 69.7 | 0.99483 | 18.1573 | - | - | 58 | 57.5 | 58.7 | 60.3 | 62.2 | 63.5 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-SRC | S | 109.7 | 0.95731 | 0 | - | - | 93.7 | 94.3 | 96 | 98.4 | 102 | 103 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-SRC | W | 134.9 | 0.9582 | 0 | - | - | 90.9 | 85 | 87.4 | 90.3 | 92.8 | 93.5 | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-TYA | S | 88 | 0.7305 | 0 | - | - | 28.2 | 39.1 | 37.8 | 36.6 | 36.5 | 37 | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-TYA | W | 112 | 0.77241 | 0 | - | - | 29 | 31.6 | 41.7 | 42.1 | 40.5 | 39.4 | - | - | - | - | - | - | - | - | - | - | - | -
BCG-WPD | S | 91.4 | 0.99036 | 24.2982 | - | - | 93.4 | 96.4 | 99 | 101.3 | 103.9 | 106.1 | - | - | - | - | - | - | - | - | - | - | - | -
BCG-WPD | W | 91.4 | 0.99036 | 24.2982 | - | - | 93.4 | 88.1 | 89.9 | 92.6 | 94.7 | 96.5 | - | - | - | - | - | - | - | - | - | - | - | -
BATS-YSW/BGL | S | 36.6 | 0.9973 | 0 | 3.0484 | - | 37.1 | 38.9 | 40.4 | 41.9 | 43.5 | 45 | - | - | - | - | - | - | - | - | - | - | - | -
BATS-YSW/BGL | W | 37.1 | 1 | 0 | 3.0484 | - | 34.1 | 30.8 | 32.2 | 33.6 | 34.8 | 36 | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAS1 | S | 83.5 | 0.97587 | 54.4501 | - | - | 82.9 | 83.8 | 86 | 76.6 | 82.5 | 80.1 | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAS1 | W | 102.9 | 0.97587 | 54.4501 | - | - | 82.9 | 87.7 | 76.2 | 85.9 | 85.1 | 86.5 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-HKT | S | 135.5 | 0.9711 | 0 | - | - | 114.2 | 111.3 | 121.3 | 128.6 | 144.4 | 159 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-HKT | W | 142.3 | 0.97004 | 0 | - | - | 113.5 | 88.8 | 97.7 | 103.5 | 114.1 | 124.2 | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SSE1 | S | 89.7 | 0.93416 | 20.3397 | - | - | 72.9 | 73.5 | 74.1 | 74.8 | 75.9 | 76.7 | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SSE1 | W | 94.3 | 0.93416 | 20.3397 | - | - | 72.9 | 66.6 | 66.9 | 67.9 | 69.2 | 69.9 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-NSF | S | 98.3 | 0.95254 | 0 | - | - | 61.1 | 68.5 | 68.7 | 70.6 | 71.6 | 72.4 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-NSF | W | 114.3 | 0.94921 | 0 | - | - | 63 | 56.9 | 57.9 | 58.9 | 59.6 | 60 | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-KWF | S | 44 | 0.69173 | 0 | - | - | 13.3 | 19.6 | 19.3 | 19.3 | 19.3 | 19.3 | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-KWF | W | 43.4 | 0.70833 | 0 | - | - | 14.4 | 20.4 | 20.3 | 20.2 | 20.3 | 20.2 | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SA2 | S | 108 | 0.97525 | 38.9298 | - | - | 88.9 | 90.4 | 93.2 | 95.2 | 97.5 | 99.5 | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SA2 | W | 122.3 | 0.97525 | 38.9298 | - | - | 88.9 | 70.4 | 72.2 | 74 | 76.4 | 77.7 | - | - | - | - | - | - | - | - | - | - | - | -
NRB-HTN | S | 52.6 | 0.84651 | 10.833 | - | - | 21.5 | 23.2 | 23.1 | 23 | 23 | 23 | - | - | - | - | - | - | - | - | - | - | - | -
NRB-HTN | W | 53.2 | 0.87708 | 10.833 | - | - | 30.1 | 30.2 | 30.7 | 30.6 | 31.1 | 31.1 | - | - | - | - | - | - | - | - | - | - | - | -
GSB-WND2 | S | 46.3 | 1 | 36.0095 | - | - | 26.7 | 19.6 | 19.9 | 20.5 | 21.1 | 21.6 | - | - | - | - | - | - | - | - | - | - | - | -
GSB-WND2 | W | 49.7 | 1 | 36.0095 | - | - | 29.6 | 25.4 | 26 | 26.8 | 27.6 | 28.2 | - | - | - | - | - | - | - | - | - | - | - | -
KGTS-CHA | S | 31.4 | 0.94771 | 8.1803 | - | - | 15.3 | 19.7 | 19.3 | 19.2 | 19.3 | 19.3 | - | - | - | - | - | - | - | - | - | - | - | -
KGTS-CHA | W | 43.4 | 0.94771 | 8.1803 | - | - | 15.3 | 15.9 | 15.6 | 15.6 | 15.8 | 15.8 | - | - | - | - | - | - | - | - | - | - | - | -
GSB-WND1 | S | 109.7 | 1 | 36.0095 | - | - | 26.2 | 19.4 | 19.7 | 20.2 | 20.8 | 21.3 | - | - | - | - | - | - | - | - | - | - | - | -
GSB-WND1 | W | 114.3 | 1 | 36.0095 | - | - | 29 | 25 | 25.6 | 26.3 | 27.1 | 27.7 | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SSE2 | S | 89.4 | 0.93544 | 20.3397 | - | - | 72.8 | 73.5 | 74.1 | 74.7 | 75.8 | 76.6 | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SSE2 | W | 100.6 | 0.93544 | 20.3397 | - | - | 72.8 | 66.5 | 66.8 | 67.9 | 69.2 | 69.8 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF1 | S | 87.5 | 0.88448 | 0.34125 | - | - | 27.7 | 27.6 | 27.6 | 27.6 | 27.7 | 27.6 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF1 | W | 87.5 | 0.88448 | 0.34125 | - | - | 27.7 | 27.5 | 27.7 | 27.7 | 27.6 | 27.6 | - | - | - | - | - | - | - | - | - | - | - | -
MDA-BNG | S | 104 | 0.93779 | 20.3504 | - | - | 43.4 | 51.8 | 52.2 | 52.7 | 53 | 53.7 | - | - | - | - | - | - | - | - | - | - | - | -
MDA-BNG | W | 114.3 | 0.94588 | 20.3504 | - | - | 38.8 | 36.8 | 37 | 37.2 | 37.7 | 37.8 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GLE2 | S | 109.7 | 0.92421 | 23.7374 | 3.0484 | 1 | 142.5 | 153.3 | 149.2 | 152.9 | 159.9 | 166.7 | 39.74% | 43.6 | 199.9883 | 160.0868 | 196.1285 | 281.1967 | 384.8405 | 13.5 | 12 | 14 | 17.5 | 23.5
GTS-GLE2 | W | 133.7 | 0.92143 | 23.7374 | 3.0484 | 1 | 145.1 | 116.7 | 119.8 | 123.9 | 129.1 | 132.3 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GLE1 | S | 109.7 | 0.9539 | 23.7374 | 3.0484 | 2 | 134.5 | 143.2 | 139.3 | 143.2 | 148.6 | 152.4 | 30.54% | 33.5 | 331.7117 | 259.4687 | 331.7117 | 448.0652 | 544.2772 | 20.5 | 16 | 20.5 | 24 | 28
GTS-GLE1 | W | 133.7 | 0.95238 | 23.7374 | 3.0484 | 1 | 136.5 | 112.1 | 115.3 | 118.9 | 122.7 | 125.5 | - | - | - | - | - | - | - | - | - | - | - | -
MGW-CLC | S | 74.3 | 0.9912 | 12.7479 | - | - | 34.1 | 35.4 | 36.7 | 38.2 | 38.4 | 38.6 | - | - | - | - | - | - | - | - | - | - | - | -
MGW-CLC | W | 86.9 | 0.99183 | 12.7479 | - | - | 36.7 | 35.6 | 38.5 | 39 | 39.5 | 39.6 | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAS2/BGF | S | 93.2 | 0.9727 | 54.4501 | - | - | 87.9 | 88.9 | 91.1 | 81.5 | 87.7 | 85.1 | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAS2/BGF | W | 94.9 | 0.97353 | 54.4501 | - | - | 86.9 | 91.8 | 80.3 | 90.2 | 89.4 | 90.8 | - | - | - | - | - | - | - | - | - | - | - | -
STN-MNA | S | 48.6 | 0.95758 | 37.7458 | - | - | 49.5 | 48.4 | 54.8 | 55.1 | 55.7 | 56.3 | - | - | - | - | - | - | - | - | - | - | - | -
STN-MNA | W | 52.6 | 0.95481 | 37.7458 | - | - | 50.9 | 43 | 43.3 | 43.6 | 44.1 | 44.5 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-KRT2 | S | 97.2 | 0.85901 | 8.9893 | - | - | 38.3 | 37.8 | 37 | 36.8 | 36.8 | 37.3 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-KRT2 | W | 116 | 0.85343 | 8.9893 | - | - | 42.3 | 41.9 | 41.9 | 42.2 | 42.8 | 43 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-KRT1 | S | 44 | 0.97879 | 8.9893 | - | - | 33 | 32.9 | 32.2 | 32 | 32.1 | 32.5 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-KRT1 | W | 44.6 | 0.98077 | 8.9893 | - | - | 36.4 | 36.5 | 36.8 | 37.1 | 37.5 | 37.6 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-WPD | S | 108 | 0.97242 | 24.2982 | - | - | 97.9 | 100.9 | 103 | 105.6 | 109.3 | 111.9 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-WPD | W | 135.5 | 0.97143 | 24.2982 | - | - | 98 | 91.7 | 93.7 | 95.9 | 98.3 | 101.1 | - | - | - | - | - | - | - | - | - | - | - | -
BGO-EHK | S | 48.6 | 0.96325 | 41.195 | 14.2513 | - | 51.7 | 52.7 | 53.9 | 54.9 | 56.1 | 57.2 | - | - | - | - | - | - | - | - | - | - | - | -
BGO-EHK | W | 49.2 | 0.96332 | 41.195 | 14.2513 | - | 51.8 | 46.6 | 47.5 | 48.5 | 49.6 | 50.5 | - | - | - | - | - | - | - | - | - | - | - | -
WNS-NKA | S | 91.4 | 0.97094 | 23.1854 | - | - | 58.5 | 65 | 65.6 | 67 | 68.3 | 69.1 | - | - | - | - | - | - | - | - | - | - | - | -
WNS-NKA | W | 91.4 | 0.96844 | 23.1854 | - | - | 60.2 | 55.3 | 56.1 | 57 | 57.8 | 58 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-STN | S | 91.4 | 0.94565 | 19.3432 | - | - | 92 | 97.1 | 104.1 | 104.9 | 106.1 | 107.3 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-STN | W | 91.4 | 0.94433 | 19.3432 | - | - | 93.4 | 77 | 77.4 | 78.2 | 78.8 | 79.9 | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-SU2 | S | 109.7 | 0.96182 | 32.1099 | - | - | 94.3 | 94.8 | 98.9 | 104 | 106.9 | 109 | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-SU2 | W | 133.7 | 0.96186 | 32.1099 | - | - | 94.4 | 81.3 | 83.8 | 88.4 | 90.7 | 92.3 | - | - | - | - | - | - | - | - | - | - | - | -
RVL-BSP | S | 84.6 | 0.99451 | 5.4815 | - | - | 18.2 | 18.3 | 19.4 | 21.2 | 21.6 | 22 | - | - | - | - | - | - | - | - | - | - | - | -
RVL-BSP | W | 106.3 | 0.98817 | 5.4815 | - | - | 16.9 | 11.4 | 12.8 | 13.9 | 14.2 | 14.4 | - | - | - | - | - | - | - | - | - | - | - | -
WIN-MGW | S | 98.3 | 0.96369 | 16.3808 | - | - | 35.8 | 38.1 | 38.8 | 40.6 | 41.1 | 41.6 | - | - | - | - | - | - | - | - | - | - | - | -
WIN-MGW | W | 99.5 | 0.96382 | 16.3808 | - | - | 38.7 | 37.4 | 40.8 | 41.5 | 42.4 | 42.8 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-MNA | S | 88 | 0.93277 | 18.4025 | 1.5 | 0.5 | 95.2 | 99.7 | 107.7 | 109.4 | 110.7 | 112.1 | 13.3% | 11.7 | 35.03 | 100.9218 | 121.1653 | 139.011 | 160.2289 | 5.75 | 12.25 | 14 | 15.5 | 18.25
SHTS-MNA | W | 114.4 | 0.93175 | 18.4025 | 1.5 | 0.75 | 96.7 | 79.1 | 79.6 | 80.4 | 81 | 82.2 | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-SCI | S | 97.2 | 0.99738 | 0 | - | - | 76.4 | 92 | 92.3 | 92.6 | 93.4 | 93.7 | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-SCI | W | 125.7 | 0.99738 | 0 | - | - | 76.4 | 92.3 | 92.4 | 92.9 | 93.7 | 93.7 | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-MLN2 | S | 109.7 | 0.95473 | 55.7824 | - | - | 99.4 | 106.4 | 120.2 | 120.4 | 135.1 | 146 | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-MLN2 | W | 134.9 | 0.95377 | 55.7824 | - | - | 99.5 | 78.7 | 86 | 86.6 | 101.4 | 105 | - | - | - | - | - | - | - | - | - | - | - | -
CDN-CLC | S | 74.3 | 0.99274 | 18.4266 | - | - | 41.3 | 42.4 | 43.8 | 45.3 | 45.8 | 46.1 | - | - | - | - | - | - | - | - | - | - | - | -
CDN-CLC | W | 86.9 | 0.99358 | 18.4266 | - | - | 46.7 | 46 | 49.3 | 50 | 50.5 | 50.7 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-COB | S | 109.7 | 0.98614 | 1.1122 | - | - | 43.3 | 47.2 | 47.4 | 48.5 | 49 | 49.4 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-COB | W | 116 | 0.99038 | 1.1122 | - | - | 41.6 | 45 | 46.7 | 47.1 | 47.6 | 47.8 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF3 | S | 87.5 | 0.88448 | 0.34125 | - | - | 27.7 | 27.7 | 27.6 | 27.6 | 27.8 | 27.6 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF3 | W | 87.5 | 0.88448 | 0.34125 | - | - | 27.7 | 27.6 | 27.7 | 27.7 | 27.7 | 27.6 | - | - | - | - | - | - | - | - | - | - | - | -
BSP-BBD | S | 65.2 | 0.95804 | 1.0402 | - | - | 28.6 | 34.1 | 33.8 | 34 | 34.2 | 34.3 | - | - | - | - | - | - | - | - | - | - | - | -
BSP-BBD | W | 67.4 | 0.96552 | 1.0402 | - | - | 23.2 | 18.2 | 18 | 18.1 | 18.2 | 18.2 | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-LVN | S | 109.7 | 0.97121 | 13.257 | - | - | 79.9 | 90 | 93.8 | 94.5 | 95.6 | 96.6 | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-LVN | W | 122.3 | 0.97121 | 13.257 | - | - | 79.9 | 94.6 | 95.8 | 97 | 98.4 | 99.3 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-FNS | S | 88 | 0.96039 | 15.1917 | - | - | 93.4 | 93.9 | 95.6 | 98 | 100.8 | 102.6 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-FNS | W | 112 | 0.96137 | 15.1917 | - | - | 90.6 | 84.7 | 87.1 | 89.9 | 91.8 | 93.2 | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-MLN1 | S | 109.7 | 0.95477 | 55.7824 | - | - | 99.5 | 107.2 | 121.4 | 121 | 135.5 | 148.8 | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-MLN1 | W | 134.9 | 0.95477 | 55.7824 | - | - | 99.5 | 79 | 86.3 | 87 | 102.1 | 105.7 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-TRG2 | S | 91.5 | 0.98752 | 14.8627 | - | - | 64.1 | 64.6 | 64.1 | 64 | 64.4 | 64.8 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-TRG2 | W | 91.5 | 0.98385 | 14.8627 | - | - | 68.1 | 68.8 | 69 | 70.2 | 71.1 | 71.4 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-TRG1 | S | 91.5 | 0.98752 | 14.8627 | - | - | 64.1 | 64.6 | 64.1 | 64 | 64.4 | 64.7 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-TRG1 | W | 91.5 | 0.98385 | 14.8627 | - | - | 68.1 | 68.7 | 68.9 | 70.2 | 71.1 | 71.4 | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-MBN | S | 97.2 | 0.91562 | 19.9415 | - | - | 55.7 | 62.2 | 62.4 | 62.6 | 63.2 | 64.1 | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-MBN | W | 114.3 | 0.91621 | 19.9415 | - | - | 54.9 | 45.4 | 45.4 | 45.7 | 46.2 | 46.4 | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-KSF | S | 84.6 | 0.97423 | 0 | - | - | 19.4 | 19.3 | 20.6 | 22.7 | 23.2 | 23.6 | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-KSF | W | 106.3 | 0.97283 | 0 | - | - | 18.4 | 12.2 | 13.7 | 14.9 | 15.3 | 15.5 | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-BMH | S | 32.6 | 0.94985 | 14.8598 | 3.0484 | - | 33.9 | 34.6 | 37.7 | 39 | 41.5 | 43 | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-BMH | W | 37.7 | 0.95137 | 14.8598 | 3.0484 | - | 32.9 | 29.1 | 29.8 | 30.8 | 32.6 | 34.3 | - | - | - | - | - | - | - | - | - | - | - | -
AC-CPL | S | 102.9 | 0.89246 | 0.481 | - | - | 71.6 | 72.7 | 73 | 73.4 | 73.8 | 74.6 | - | - | - | - | - | - | - | - | - | - | - | -
AC-CPL | W | 108 | 0.89506 | 0.481 | - | - | 81 | 79.8 | 79.5 | 80.3 | 81.1 | 81.2 | - | - | - | - | - | - | - | - | - | - | - | -
FNS-SRC | S | 109.7 | 0.94715 | 15.1917 | - | - | 47.3 | 48.6 | 48.5 | 48.7 | 51.1 | 51.9 | - | - | - | - | - | - | - | - | - | - | - | -
FNS-SRC | W | 125.7 | 0.98 | 15.1917 | - | - | 45 | 45.9 | 45.9 | 46.1 | 46.4 | 47 | - | - | - | - | - | - | - | - | - | - | - | -
WETS-BSP | S | 84.6 | 0.94235 | 0 | - | - | 50.3 | 57.1 | 57.9 | 60.8 | 61.3 | 61.8 | - | - | - | - | - | - | - | - | - | - | - | -
WETS-BSP | W | 106.3 | 0.95059 | 0 | - | - | 42.5 | 30.7 | 32.1 | 33.3 | 33.8 | 34 | - | - | - | - | - | - | - | - | - | - | - | -

## ZSS Aug Sum
Zone Substation | Season | Station N Import Rating (MVA) | Station N-1 Import Rating (MVA) | Station Nameplate Rating (MVA) | Station Power Factor at Maximum Demand | Embedded Generation Capacity (MVA) | Load Transfer Capability (MVA) | Hours load is > 95% of Maximum Demand (Hrs) | Actual Maximum Demand (MVA) | 10% POE |  |  |  |  | 50% POE |  |  |  |  | 50% POE load above N-1 Import Rating (%) | 50% POE load above N-1 Import Rating (MVA) | 10% POE | [14 empty] | 50% POE | [14 empty] | Weighted POE
[10 empty] | Forecast Maximum Demand (MVA) |  |  |  |  | Forecast Maximum Demand (MVA) | [6 empty] | Energy at Risk (MWh) |  |  |  |  | Expected Energy at Risk (MWh) |  |  |  |  | Hours at Risk (Hrs) |  |  |  |  | Energy at Risk (MWh) |  |  |  |  | Expected Energy at Risk (MWh) |  |  |  |  | Hours at Risk (Hrs) |  |  |  |  | Energy at Risk (MWh) |  |  |  |  | Expected Energy at Risk (MWh)
[5 empty] | 2024 | 2024 | 2025 | 2024 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2025 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029
AC | S | 60 | 30 | 40 | 0.94 | 0.481 | 0 | 1.65 | 5.45 | 7.94 | 7.99 | 8.04 | 8.12 | 8.2 | 5.79 | 5.82 | 5.86 | 5.92 | 5.98 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AC | W | 60 | 30 | 40 | 0.93 | 0.481 | 0 | 1.65 | 5.66 | 6.2 | 6.23 | 6.28 | 6.35 | 6.38 | 4.17 | 4.19 | 4.23 | 4.27 | 4.3 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AL | S | 34.2 | 0 | 30 | 0.97 | 12.6295 | 0 | 2.61 | 22.33 | 24.64 | 24.57 | 24.78 | 25.1 | 25.31 | 20.95 | 21.06 | 21.3 | 21.6 | 21.86 | 100% | 20.95 | 74440.09 | 71751.3 | 72323.5 | 73649.99 | 74071.3 | 69.65 | 67.14 | 67.67 | 68.91 | 69.31 | 8760 | 8760 | 8758.5 | 8750 | 8743 | 59932.31 | 57331.21 | 57495.95 | 58155.69 | 58590.37 | 56.08 | 53.64 | 53.8 | 54.41 | 54.82 | 8759 | 8742 | 8727 | 8702 | 8666 | 64284.644 | 61657.237 | 61944.215 | 62803.98 | 63234.649 | 60.151 | 57.69 | 57.961 | 58.76 | 59.167
AL | W | 38.6 | 0 | 30 | 0.99 | 12.6295 | 0 | 2.61 | 16.96 | 18.85 | 18.99 | 19.28 | 19.67 | 19.87 | 17.75 | 17.91 | 18.21 | 18.54 | 18.75 | 100% | 17.75 | 74440.09 | 71751.3 | 72323.5 | 73649.99 | 74071.3 | 69.65 | 67.14 | 67.67 | 68.91 | 69.31 | 8760 | 8760 | 8758.5 | 8750 | 8743 | 59932.31 | 57331.21 | 57495.95 | 58155.69 | 58590.37 | 56.08 | 53.64 | 53.8 | 54.41 | 54.82 | 8759 | 8742 | 8727 | 8702 | 8666 | 64284.644 | 61657.237 | 61944.215 | 62803.98 | 63234.649 | 60.151 | 57.69 | 57.961 | 58.76 | 59.167
ART | S | 28.2 | 13.6 | 20 | 0.99 | 14.1862 | 2.2863 | 1.37 | 12.48 | 16.19 | 16.05 | 16.08 | 16.13 | 16.17 | 14.34 | 14.17 | 14.16 | 14.24 | 14.27 | 5.441% | 0.74 | 13.91 | 14.45 | 17.24 | 20.29 | 23.17 | 0.01 | 0.01 | 0.02 | 0.02 | 0.02 | 18 | 20 | 23 | 27.5 | 29.5 | 0.62 | 0.44 | 0.49 | 0.65 | 0.76 | 0 | 0 | 0 | 0 | 0 | 1.5 | 1.5 | 1.5 | 2 | 2 | 4.607 | 4.643 | 5.515 | 6.542 | 7.483 | 0.003 | 0.003 | 0.006 | 0.006 | 0.006
ART | W | 31.4 | 15.2 | 20 | 1 | 14.1862 | 2.2863 | 1.37 | 17.2 | 14.85 | 14.68 | 14.71 | 14.8 | 14.8 | 13.93 | 13.79 | 13.77 | 13.83 | 13.83 | - | - | 13.91 | 14.45 | 17.24 | 20.29 | 23.17 | 0.01 | 0.01 | 0.02 | 0.02 | 0.02 | 18 | 20 | 23 | 27.5 | 29.5 | 0.62 | 0.44 | 0.49 | 0.65 | 0.76 | 0 | 0 | 0 | 0 | 0 | 1.5 | 1.5 | 1.5 | 2 | 2 | 4.607 | 4.643 | 5.515 | 6.542 | 7.483 | 0.003 | 0.003 | 0.006 | 0.006 | 0.006
BAN | S | 145.4 | 96.4 | 120 | 0.99 | 44.3748 | 8.3831 | 4.22 | 84.9 | 101.08 | 107.66 | 86.73 | 88.4 | 89.45 | 85.47 | 91.56 | 73.04 | 74.16 | 75.14 | - | - | 7.64 | 85.32 | 0 | 0 | 0 | 0.01 | 0.12 | 0 | 0 | 0 | 4 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.292 | 25.596 | 0 | 0 | 0 | 0.003 | 0.036 | 0 | 0 | 0
BAN | W | 157.5 | 104.4 | 120 | 1 | 44.3748 | 8.3831 | 4.22 | 87.13 | 95.39 | 77.04 | 77.88 | 79.59 | 79.93 | 90.06 | 73.94 | 74.97 | 76.34 | 77.06 | - | - | 7.64 | 85.32 | 0 | 0 | 0 | 0.01 | 0.12 | 0 | 0 | 0 | 4 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.292 | 25.596 | 0 | 0 | 0 | 0.003 | 0.036 | 0 | 0 | 0
BAS | S | 116.8 | 76 | 99 | 1 | 54.4501 | 9.7168 | 4.12 | 72.78 | 86.39 | 88.51 | 78.61 | 83.94 | 81.32 | 79.82 | 81.7 | 73.4 | 78.7 | 76.45 | 5.026% | 3.82 | 81.92 | 151.32 | 4.3 | 59.99 | 21.29 | 0.06 | 0.11 | 0 | 0.04 | 0.02 | 22 | 37 | 3 | 21.5 | 13.5 | 6.39 | 16.39 | 0 | 4.47 | 0.19 | 0 | 0.01 | 0 | 0 | 0 | 3 | 7.5 | 0 | 2.5 | 0.5 | 29.049 | 56.869 | 1.29 | 21.126 | 6.52 | 0.018 | 0.04 | 0 | 0.012 | 0.006
BAS | W | 130.1 | 84.6 | 99 | 1 | 54.4501 | 9.7168 | 4.12 | 79.54 | 87.91 | 76.33 | 84.93 | 84.22 | 85.46 | 83.22 | 73.13 | 81.74 | 80.98 | 82.17 | - | - | 81.92 | 151.32 | 4.3 | 59.99 | 21.29 | 0.06 | 0.11 | 0 | 0.04 | 0.02 | 22 | 37 | 3 | 21.5 | 13.5 | 6.39 | 16.39 | 0 | 4.47 | 0.19 | 0 | 0.01 | 0 | 0 | 0 | 3 | 7.5 | 0 | 2.5 | 0.5 | 29.049 | 56.869 | 1.29 | 21.126 | 6.52 | 0.018 | 0.04 | 0 | 0.012 | 0.006
BBD | S | 92.4 | 45.2 | 66 | 0.98 | 1.0402 | 0 | 6.54 | 28.46 | 37.8 | 37.48 | 37.51 | 37.79 | 37.9 | 33.44 | 33.17 | 33.18 | 33.42 | 33.53 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BBD | W | 99.5 | 49.5 | 66 | 0.91 | 1.0402 | 0 | 6.54 | 18.55 | 25.58 | 25.4 | 25.45 | 25.67 | 25.68 | 22.47 | 22.3 | 22.33 | 22.54 | 22.55 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BGO | S | 77 | 38.5 | 66 | 0.99 | 17.7292 | 13.1463 | 2.82 | 38.96 | 46.76 | 45.75 | 45.93 | 46.56 | 46.91 | 40.63 | 40.39 | 40.53 | 41.01 | 41.43 | 5.532% | 2.13 | 103.68 | 87.68 | 105.66 | 144.82 | 174.14 | 0.05 | 0.04 | 0.05 | 0.07 | 0.08 | 39 | 36.5 | 44.5 | 58 | 66.5 | 3.25 | 2.93 | 3.57 | 5.71 | 8.51 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 4 | 5.5 | 8 | 33.379 | 28.355 | 34.197 | 47.443 | 58.199 | 0.015 | 0.012 | 0.015 | 0.021 | 0.024
BGO | W | 90.8 | 45.4 | 66 | 1 | 17.7292 | 13.1463 | 2.82 | 35.94 | 36.5 | 36.51 | 36.71 | 37.23 | 37.5 | 35.23 | 35.17 | 35.4 | 35.78 | 35.98 | - | - | 103.68 | 87.68 | 105.66 | 144.82 | 174.14 | 0.05 | 0.04 | 0.05 | 0.07 | 0.08 | 39 | 36.5 | 44.5 | 58 | 66.5 | 3.25 | 2.93 | 3.57 | 5.71 | 8.51 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 4 | 5.5 | 8 | 33.379 | 28.355 | 34.197 | 47.443 | 58.199 | 0.015 | 0.012 | 0.015 | 0.021 | 0.024
BMH | S | 38.2 | 19.1 | 26 | 0.99 | 14.8598 | 3.0484 | 4.01 | 27.83 | 30.9601 | 32.3694 | 33.4318 | 34.7001 | 35.9034 | 28.8671 | 30.1811 | 31.1717 | 32.3542 | 33.4762 | 51.14% | 9.7671 | 587.7734 | 1032.4165 | 1452.1715 | 2027.4743 | 2675.5184 | 2.5862 | 4.5426 | 6.3896 | 8.9209 | 11.7723 | 307.25 | 477 | 608.75 | 767.75 | 937 | 284.8921 | 544.0051 | 812.0688 | 1201.9712 | 1655.4261 | 1.2535 | 2.3936 | 3.5731 | 5.2887 | 7.2839 | 168.25 | 299 | 408.5 | 539.75 | 669.75 | 375.7565 | 690.5285 | 1004.0996 | 1449.6222 | 1961.4538 | 1.6533 | 3.0383 | 4.418 | 6.3783 | 8.6304
BMH | W | 40.4 | 20.2 | 26 | 1 | 14.8598 | 3.0484 | 4.01 | 24.66 | 25.4458 | 26.86 | 27.8257 | 28.8811 | 29.8626 | 24.1502 | 25.4924 | 26.4089 | 27.4106 | 28.3422 | 19.56% | 3.9502 | 587.7734 | 1032.4165 | 1452.1715 | 2027.4743 | 2675.5184 | 2.5862 | 4.5426 | 6.3896 | 8.9209 | 11.7723 | 307.25 | 477 | 608.75 | 767.75 | 937 | 284.8921 | 544.0051 | 812.0688 | 1201.9712 | 1655.4261 | 1.2535 | 2.3936 | 3.5731 | 5.2887 | 7.2839 | 168.25 | 299 | 408.5 | 539.75 | 669.75 | 375.7565 | 690.5285 | 1004.0996 | 1449.6222 | 1961.4538 | 1.6533 | 3.0383 | 4.418 | 6.3783 | 8.6304
CDN | S | 34.4 | 17.2 | 20 | 0.99 | 5.6786 | 0 | 0.49 | 12.04 | 15.39 | 15.2 | 15.19 | 15.28 | 15.4 | 13.76 | 13.69 | 13.73 | 13.86 | 13.97 | - | - | 0.35 | 0.36 | 0.44 | 0.68 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.105 | 0.108 | 0.132 | 0.204 | 0.216 | 0 | 0 | 0 | 0 | 0
CDN | W | 36.4 | 18.2 | 20 | 0.99 | 5.6786 | 0 | 0.49 | 12.53 | 18.9 | 18.92 | 19.09 | 19.34 | 19.37 | 16.54 | 16.56 | 16.67 | 16.89 | 16.92 | - | - | 0.35 | 0.36 | 0.44 | 0.68 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.105 | 0.108 | 0.132 | 0.204 | 0.216 | 0 | 0 | 0 | 0 | 0
CHA | S | 38.6 | 15.2 | 26 | 0.98 | 8.1803 | 1.9434 | 13.43 | 14.28 | 26.89 | 26.39 | 26.47 | 26.88 | 27.15 | 18.82 | 18.49 | 18.34 | 18.45 | 18.5 | 23.82% | 3.62 | 4053.33 | 3418.41 | 3667.53 | 3866.34 | 3972.51 | 5.26 | 4.44 | 4.76 | 5.02 | 5.16 | 1183.5 | 1080.5 | 1167.5 | 1217.5 | 1237 | 100.72 | 66.32 | 60.62 | 62.33 | 61.68 | 0.13 | 0.09 | 0.08 | 0.08 | 0.08 | 84 | 63.5 | 59.5 | 59 | 57.5 | 1286.503 | 1071.947 | 1142.693 | 1203.533 | 1234.929 | 1.669 | 1.395 | 1.484 | 1.562 | 1.604
CHA | W | 39 | 15.2 | 26 | 1 | 8.1803 | 1.9434 | 13.43 | 12.22 | 24.03 | 23.99 | 24.09 | 24.35 | 24.43 | 15.33 | 15.05 | 15.08 | 15.27 | 15.24 | 0.8553% | 0.13 | 4053.33 | 3418.41 | 3667.53 | 3866.34 | 3972.51 | 5.26 | 4.44 | 4.76 | 5.02 | 5.16 | 1183.5 | 1080.5 | 1167.5 | 1217.5 | 1237 | 100.72 | 66.32 | 60.62 | 62.33 | 61.68 | 0.13 | 0.09 | 0.08 | 0.08 | 0.08 | 84 | 63.5 | 59.5 | 59 | 57.5 | 1286.503 | 1071.947 | 1142.693 | 1203.533 | 1234.929 | 1.669 | 1.395 | 1.484 | 1.562 | 1.604
CHM | S | 36.9 | 0 | 33 | 0.98 | 1.3729 | 0 | 3.41 | 1.98 | 2.36 | 2.24 | 2.21 | 2.21 | 2.21 | 2.17 | 2.11 | 2.1 | 2.1 | 2.1 | 100% | 2.17 | 7402.17 | 7244.78 | 7069.67 | 7006.42 | 6855.93 | 1.78 | 1.74 | 1.7 | 1.68 | 1.65 | 8682 | 8537 | 8319 | 8080.5 | 7864 | 5536.77 | 5367.29 | 5295.11 | 5278.13 | 5191.69 | 1.33 | 1.29 | 1.27 | 1.27 | 1.25 | 8437.5 | 8159 | 7846 | 7583.5 | 7328 | 6096.39 | 5930.537 | 5827.478 | 5796.617 | 5690.962 | 1.465 | 1.425 | 1.399 | 1.393 | 1.37
CHM | W | 44.1 | 0 | 33 | 0.96 | 1.3729 | 0 | 3.41 | 1.96 | 2.28 | 2.22 | 2.18 | 2.18 | 2.16 | 1.87 | 1.76 | 1.74 | 1.74 | 1.74 | 100% | 1.87 | 7402.17 | 7244.78 | 7069.67 | 7006.42 | 6855.93 | 1.78 | 1.74 | 1.7 | 1.68 | 1.65 | 8682 | 8537 | 8319 | 8080.5 | 7864 | 5536.77 | 5367.29 | 5295.11 | 5278.13 | 5191.69 | 1.33 | 1.29 | 1.27 | 1.27 | 1.25 | 8437.5 | 8159 | 7846 | 7583.5 | 7328 | 6096.39 | 5930.537 | 5827.478 | 5796.617 | 5690.962 | 1.465 | 1.425 | 1.399 | 1.393 | 1.37
CLC | S | 101.2 | 49.2 | 79 | 1 | 12.7479 | 0 | 4.3 | 35.86 | 42.46 | 43.95 | 45.47 | 45.9 | 46.07 | 39.16 | 40.51 | 42.08 | 42.35 | 42.55 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CLC | W | 112.3 | 54.8 | 79 | 1 | 12.7479 | 0 | 4.3 | 37.66 | 38.86 | 41.6 | 42.2 | 42.69 | 42.84 | 36.63 | 39.44 | 39.97 | 40.4 | 40.56 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CME | S | 50.4 | 32.3 | 39 | 1 | 18.4119 | 0 | 2.55 | 31.41 | 44.16 | 44.14 | 44.44 | 44.89 | 45.22 | 35.98 | 36.01 | 36.18 | 36.5 | 36.78 | 11.39% | 3.68 | 445.05 | 458.48 | 505.66 | 570.83 | 621.71 | 0.5 | 0.51 | 0.57 | 0.64 | 0.69 | 130 | 135 | 145.5 | 158.5 | 169.5 | 13.27 | 13.87 | 15.93 | 20.06 | 24.17 | 0.01 | 0.02 | 0.02 | 0.02 | 0.03 | 11 | 11 | 12 | 14.5 | 16.5 | 142.804 | 147.253 | 162.849 | 185.291 | 203.432 | 0.157 | 0.167 | 0.185 | 0.206 | 0.228
CME | W | 59.4 | 37.3 | 39 | 0.98 | 18.4119 | 0 | 2.55 | 26.7 | 35.7 | 35.8 | 36 | 36.37 | 36.53 | 29.87 | 29.87 | 30.11 | 30.41 | 30.54 | - | - | 445.05 | 458.48 | 505.66 | 570.83 | 621.71 | 0.5 | 0.51 | 0.57 | 0.64 | 0.69 | 130 | 135 | 145.5 | 158.5 | 169.5 | 13.27 | 13.87 | 15.93 | 20.06 | 24.17 | 0.01 | 0.02 | 0.02 | 0.02 | 0.03 | 11 | 11 | 12 | 14.5 | 16.5 | 142.804 | 147.253 | 162.849 | 185.291 | 203.432 | 0.157 | 0.167 | 0.185 | 0.206 | 0.228
CMN | S | 86 | 43 | 66 | 1 | 29.0396 | 0 | 4.14 | 24.8 | 31.13 | 31.46 | 31.86 | 32.46 | 32.94 | 27.08 | 27.39 | 27.65 | 28.02 | 28.37 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CMN | W | 99 | 49.5 | 66 | 1 | 29.0396 | 0 | 4.14 | 27.91 | 28.85 | 29 | 29.4 | 29.82 | 30.19 | 27.63 | 27.83 | 28.26 | 28.72 | 29.06 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COB | S | 38.5 | 15 | 31 | 0.9 | 1.1122 | 2.1339 | 2 | 12.36 | 17.16 | 16.92 | 16.84 | 16.81 | 16.75 | 14.3 | 14.1 | 14.03 | 14 | 13.95 | - | - | 5.53 | 3.99 | 3.62 | 3.52 | 3.11 | 0 | 0 | 0 | 0 | 0 | 8.5 | 6 | 6 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.659 | 1.197 | 1.086 | 1.056 | 0.933 | 0 | 0 | 0 | 0 | 0
COB | W | 39 | 15 | 31 | 0.92 | 1.1122 | 2.1339 | 2 | 12.64 | 17.3 | 17.1 | 17.04 | 17.01 | 16.91 | 14 | 13.84 | 13.8 | 13.78 | 13.71 | - | - | 5.53 | 3.99 | 3.62 | 3.52 | 3.11 | 0 | 0 | 0 | 0 | 0 | 8.5 | 6 | 6 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.659 | 1.197 | 1.086 | 1.056 | 0.933 | 0 | 0 | 0 | 0 | 0
CRO | S | 74.7 | 34.3 | 60 | 0.97 | 5.4569 | 11.0124 | 7.22 | 31.35 | 37.59 | 38.57 | 38.98 | 39.56 | 40.07 | 33.09 | 33.79 | 34.1 | 34.65 | 35.1 | - | - | 5.28 | 10.52 | 13.61 | 22.23 | 32.67 | 0 | 0.01 | 0.01 | 0.01 | 0.02 | 5 | 8.5 | 13.5 | 19.5 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.584 | 3.156 | 4.083 | 6.669 | 9.801 | 0 | 0.003 | 0.003 | 0.003 | 0.006
CRO | W | 82.4 | 38 | 60 | 0.98 | 5.4569 | 11.0124 | 7.22 | 31.75 | 38.71 | 39 | 39.58 | 40.34 | 40.64 | 33.96 | 34.29 | 34.69 | 35.32 | 35.5 | - | - | 5.28 | 10.52 | 13.61 | 22.23 | 32.67 | 0 | 0.01 | 0.01 | 0.01 | 0.02 | 5 | 8.5 | 13.5 | 19.5 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.584 | 3.156 | 4.083 | 6.669 | 9.801 | 0 | 0.003 | 0.003 | 0.003 | 0.006
CTN | S | 55 | 33.7 | 41 | 0.94 | 17.2207 | 0 | 1.56 | 20.51 | 21.61 | 21.42 | 21.44 | 21.58 | 21.68 | 19.78 | 19.62 | 19.66 | 19.8 | 19.88 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CTN | W | 59.1 | 38.4 | 41 | 0.96 | 17.2207 | 0 | 1.56 | 18.11 | 20.06 | 19.99 | 20.09 | 19.87 | 19.86 | 17.44 | 17.36 | 17.44 | 17.61 | 17.58 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DDL | S | 79.4 | 39.7 | 66 | 1 | 40.3392 | 4.5726 | 5.12 | 73.53 | 78.2133 | 73.8816 | 76.0749 | 78.7068 | 81.1414 | 71.6595 | 67.6907 | 69.7002 | 72.1116 | 74.3422 | 80.5% | 31.9595 | 1219.6088 | 1039.0795 | 1346.7079 | 1824.7048 | 2310.9661 | 5.285 | 4.5027 | 5.8357 | 7.9071 | 10.0142 | 168 | 166.75 | 225.25 | 305.5 | 384.75 | 719.8248 | 559.7788 | 692.2653 | 912.0652 | 1154.8961 | 3.1192 | 2.4257 | 2.9998 | 3.9523 | 5.0045 | 79.5 | 73 | 101.75 | 149 | 193.5 | 869.76 | 703.569 | 888.5981 | 1185.8571 | 1501.7171 | 3.769 | 3.0488 | 3.8506 | 5.1387 | 6.5074
DDL | W | 94.4 | 47.2 | 66 | 1 | 40.3392 | 4.5726 | 5.12 | 52.91 | 55.2949 | 57.1269 | 59.1215 | 61.4304 | 63.1323 | 51.0605 | 52.7522 | 54.594 | 56.7261 | 58.2977 | 8.179% | 3.8605 | 1219.6088 | 1039.0795 | 1346.7079 | 1824.7048 | 2310.9661 | 5.285 | 4.5027 | 5.8357 | 7.9071 | 10.0142 | 168 | 166.75 | 225.25 | 305.5 | 384.75 | 719.8248 | 559.7788 | 692.2653 | 912.0652 | 1154.8961 | 3.1192 | 2.4257 | 2.9998 | 3.9523 | 5.0045 | 79.5 | 73 | 101.75 | 149 | 193.5 | 869.76 | 703.569 | 888.5981 | 1185.8571 | 1501.7171 | 3.769 | 3.0488 | 3.8506 | 5.1387 | 6.5074
DLF | S | 42 | 86.5 | 66 | 1 | 0.34125 | 0 | 11.96 | 14.49 | 18.07 | 19.49 | 20.39 | 21.32 | 22.21 | 16.23 | 17.55 | 18.37 | 19.22 | 20.02 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DLF | W | 49.3 | 99.3 | 66 | 1 | 0.34125 | 0 | 11.96 | 10.53 | 16.82 | 17.8 | 18.61 | 19.45 | 20.18 | 13.27 | 14.08 | 14.73 | 15.4 | 16 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ECA | S | 52.8 | 34.6 | 39 | 0.94 | 19.879 | 4.7631 | 2.89 | 37.57 | 41.8 | 41.58 | 41.81 | 42.26 | 42.64 | 37.24 | 37.13 | 37.35 | 37.76 | 38.07 | 7.63% | 2.64 | 116.43 | 109.55 | 125.61 | 155.83 | 185.84 | 0.17 | 0.16 | 0.18 | 0.23 | 0.27 | 55.5 | 54.5 | 59.5 | 72.5 | 83.5 | 4.73 | 4.46 | 5.54 | 8.05 | 10.86 | 0.01 | 0.01 | 0.01 | 0.01 | 0.02 | 4 | 3.5 | 5 | 7.5 | 10 | 38.24 | 35.987 | 41.561 | 52.384 | 63.354 | 0.058 | 0.055 | 0.061 | 0.076 | 0.095
ECA | W | 60.6 | 40.4 | 39 | 0.99 | 19.879 | 4.7631 | 2.89 | 30.19 | 36.24 | 36.4 | 36.81 | 37.29 | 37.5 | 28.78 | 28.74 | 28.97 | 29.32 | 29.49 | - | - | 116.43 | 109.55 | 125.61 | 155.83 | 185.84 | 0.17 | 0.16 | 0.18 | 0.23 | 0.27 | 55.5 | 54.5 | 59.5 | 72.5 | 83.5 | 4.73 | 4.46 | 5.54 | 8.05 | 10.86 | 0.01 | 0.01 | 0.01 | 0.01 | 0.02 | 4 | 3.5 | 5 | 7.5 | 10 | 38.24 | 35.987 | 41.561 | 52.384 | 63.354 | 0.058 | 0.055 | 0.061 | 0.076 | 0.095
EHK | S | 72.8 | 36.4 | 54 | 0.99 | 23.4658 | 20.9578 | 3.33 | 50.03 | 55.03 | 56.36 | 57.47 | 58.7 | 59.79 | 51.3 | 52.46 | 53.36 | 54.46 | 55.38 | 40.93% | 14.9 | 1558.57 | 2205.35 | 2895.2 | 3664.22 | 4355.83 | 1.63 | 2.31 | 3.03 | 3.84 | 4.56 | 352 | 478 | 588.5 | 702.5 | 797 | 577.5 | 818.26 | 1085.54 | 1413.22 | 1716.38 | 0.61 | 0.86 | 1.14 | 1.48 | 1.8 | 138 | 191 | 254.5 | 305 | 355.5 | 871.821 | 1234.387 | 1628.438 | 2088.52 | 2508.215 | 0.916 | 1.295 | 1.707 | 2.188 | 2.628
EHK | W | 82 | 41 | 54 | 1 | 23.4658 | 20.9578 | 3.33 | 44.85 | 47.25 | 48.1 | 49.1 | 50.25 | 51.03 | 45.63 | 46.46 | 47.42 | 48.48 | 49.25 | 11.29% | 4.63 | 1558.57 | 2205.35 | 2895.2 | 3664.22 | 4355.83 | 1.63 | 2.31 | 3.03 | 3.84 | 4.56 | 352 | 478 | 588.5 | 702.5 | 797 | 577.5 | 818.26 | 1085.54 | 1413.22 | 1716.38 | 0.61 | 0.86 | 1.14 | 1.48 | 1.8 | 138 | 191 | 254.5 | 305 | 355.5 | 871.821 | 1234.387 | 1628.438 | 2088.52 | 2508.215 | 0.916 | 1.295 | 1.707 | 2.188 | 2.628
FNS | S | 130.8 | 87.2 | 99 | 0.99 | 15.1917 | 0 | 3.31 | 44.63 | 50.87 | 53.06 | 55.68 | 58.34 | 59.32 | 44.14 | 45.87 | 48.06 | 50.42 | 51.26 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FNS | W | 147.9 | 98.6 | 99 | 1 | 15.1917 | 0 | 3.31 | 37.08 | 40.34 | 42.67 | 45.21 | 46.7 | 47.42 | 38.28 | 40.59 | 43.12 | 44.6 | 45.25 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GB | S | 56.4 | 37.6 | 36 | 0.95 | 1.9222 | 0 | 15.12 | 15.44 | 16.81 | 16.89 | 16.88 | 16.88 | 17 | 15.25 | 15.26 | 15.25 | 15.36 | 15.43 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GB | W | 56.4 | 37.6 | 36 | 0.95 | 1.9222 | 0 | 15.12 | 13.56 | 15.25 | 15.34 | 15.47 | 15.66 | 15.77 | 13.98 | 14.06 | 14.15 | 14.29 | 14.4 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GCY | S | 75.6 | 37.8 | 66 | 0.98 | 11.3272 | 16.3852 | 4.24 | 46.37 | 53.25 | 53.52 | 53.5 | 53.87 | 54.05 | 46.1 | 45.88 | 45.93 | 46.16 | 46.57 | 21.96% | 8.3 | 989.53 | 646.86 | 554.35 | 613.42 | 711.25 | 0.48 | 0.31 | 0.27 | 0.29 | 0.34 | 227 | 156.5 | 121.5 | 133 | 165.5 | 150.91 | 100.9 | 94.05 | 105.05 | 130.93 | 0.07 | 0.05 | 0.05 | 0.05 | 0.06 | 68 | 39.5 | 37 | 40.5 | 47.5 | 402.496 | 264.688 | 232.14 | 257.561 | 305.026 | 0.193 | 0.128 | 0.116 | 0.122 | 0.144
GCY | W | 87.8 | 43.9 | 66 | 1 | 11.3272 | 16.3852 | 4.24 | 33.44 | 36.07 | 36.04 | 36.27 | 36.71 | 36.99 | 34.71 | 34.7 | 34.93 | 35.28 | 35.51 | - | - | 989.53 | 646.86 | 554.35 | 613.42 | 711.25 | 0.48 | 0.31 | 0.27 | 0.29 | 0.34 | 227 | 156.5 | 121.5 | 133 | 165.5 | 150.91 | 100.9 | 94.05 | 105.05 | 130.93 | 0.07 | 0.05 | 0.05 | 0.05 | 0.06 | 68 | 39.5 | 37 | 40.5 | 47.5 | 402.496 | 264.688 | 232.14 | 257.561 | 305.026 | 0.193 | 0.128 | 0.116 | 0.122 | 0.144
GHP | S | 99 | 49.5 | 66 | 1 | 18.9423 | 0 | 4.2 | 33.55 | 37.34 | 37.66 | 38.49 | 39.49 | 40.29 | 33.35 | 33.55 | 34.07 | 35.03 | 35.78 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GHP | W | 99 | 49.5 | 66 | 1 | 18.9423 | 0 | 4.2 | 25.9 | 29.67 | 30.27 | 31 | 31.97 | 32.52 | 27.51 | 28.1 | 28.83 | 29.61 | 30.12 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GL | S | 102.1 | 47.6 | 80 | 0.99 | 18.5026 | 14.4895 | 2.31 | 40.63 | 42.21 | 45.47 | 46.21 | 46.92 | 47.48 | 38.29 | 41.62 | 42.53 | 43.26 | 43.79 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GL | W | 116.3 | 47.6 | 80 | 1 | 18.5026 | 14.4895 | 2.31 | 33.62 | 37.05 | 40.16 | 40.82 | 41.69 | 42.06 | 35.09 | 37.89 | 38.54 | 39.34 | 39.75 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GLE | S | 84.3 | 53.3 | 79 | 0.99 | 23.7374 | 6.0968 | 3.37 | 51.27 | 65.05 | 66.1 | 67.07 | 68.31 | 69.31 | 58.97 | 60.49 | 61.25 | 62.42 | 63.28 | 10.64% | 5.67 | 197.78 | 263.96 | 369.54 | 515.64 | 665.34 | 0.2 | 0.26 | 0.37 | 0.51 | 0.66 | 50 | 63.5 | 84.5 | 112 | 140.5 | 29.02 | 53.2 | 77.26 | 122.76 | 165.79 | 0.03 | 0.05 | 0.08 | 0.12 | 0.16 | 14 | 19.5 | 28.5 | 42 | 51 | 79.648 | 116.428 | 164.944 | 240.624 | 315.655 | 0.081 | 0.113 | 0.167 | 0.237 | 0.31
GLE | W | 99.1 | 59.1 | 79 | 1 | 23.7374 | 6.0968 | 3.37 | 48.69 | 59.85 | 60.67 | 61.54 | 62.72 | 63.36 | 54.46 | 55.25 | 56.16 | 57.2 | 57.84 | - | - | 197.78 | 263.96 | 369.54 | 515.64 | 665.34 | 0.2 | 0.26 | 0.37 | 0.51 | 0.66 | 50 | 63.5 | 84.5 | 112 | 140.5 | 29.02 | 53.2 | 77.26 | 122.76 | 165.79 | 0.03 | 0.05 | 0.08 | 0.12 | 0.16 | 14 | 19.5 | 28.5 | 42 | 51 | 79.648 | 116.428 | 164.944 | 240.624 | 315.655 | 0.081 | 0.113 | 0.167 | 0.237 | 0.31
GSB | S | 99 | 49.5 | 66 | 1 | 18.1573 | 0 | 1.68 | 23.41 | 31.85 | 32.24 | 32.95 | 33.79 | 34.67 | 28.94 | 29.33 | 29.92 | 30.64 | 31.33 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GSB | W | 99 | 49.5 | 66 | 1 | 18.1573 | 0 | 1.68 | 27.39 | 32.48 | 33.01 | 33.79 | 34.68 | 35.26 | 31.14 | 31.63 | 32.36 | 33.23 | 33.78 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HSM | S | 59.6 | 39.7 | 39 | 1 | 20.6709 | 3.3914 | 4.49 | 39.13 | 43.58 | 42.99 | 43.07 | 43.28 | 43.39 | 41.13 | 40.78 | 40.87 | 41.05 | 41.17 | 3.602% | 1.43 | 21.34 | 14.74 | 17.46 | 22.32 | 25.45 | 0.03 | 0.02 | 0.03 | 0.03 | 0.04 | 17.5 | 14 | 17.5 | 20.5 | 22 | 2.12 | 1.36 | 1.64 | 2.2 | 2.61 | 0 | 0 | 0 | 0 | 0 | 2.5 | 2 | 3 | 3.5 | 3.5 | 7.886 | 5.374 | 6.386 | 8.236 | 9.462 | 0.009 | 0.006 | 0.009 | 0.009 | 0.012
HSM | W | 60.6 | 40.4 | 39 | 1 | 20.6709 | 3.3914 | 4.49 | 36.62 | 36.52 | 36.21 | 36.28 | 36.57 | 36.56 | 34.62 | 34.43 | 34.55 | 34.83 | 34.81 | - | - | 21.34 | 14.74 | 17.46 | 22.32 | 25.45 | 0.03 | 0.02 | 0.03 | 0.03 | 0.04 | 17.5 | 14 | 17.5 | 20.5 | 22 | 2.12 | 1.36 | 1.64 | 2.2 | 2.61 | 0 | 0 | 0 | 0 | 0 | 2.5 | 2 | 3 | 3.5 | 3.5 | 7.886 | 5.374 | 6.386 | 8.236 | 9.462 | 0.009 | 0.006 | 0.009 | 0.009 | 0.012
HTN | S | 51.7 | 34.2 | 39 |  | 10.833 | 0 | 3.5 |  | 28.49 | 28.11 | 28.1 | 27.99 | 27.99 | 25.26 | 24.86 | 24.79 | 24.88 | 24.89 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HTN | W | 58.1 | 38.4 | 39 | 1 | 10.833 | 0 | 3.5 | 19.34 | 24.23 | 24.11 | 24.22 | 24.43 | 24.44 | 23.54 | 23.42 | 23.54 | 23.74 | 23.74 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KRT | S | 52.5 | 33.4 | 39 | 1 | 8.9893 | 3.1627 | 8.24 | 24.53 | 37.69 | 37.56 | 37.53 | 37.75 | 38.07 | 29.39 | 29.21 | 29.18 | 29.21 | 29.35 | - | - | 68.04 | 68.08 | 69.57 | 84.17 | 104.29 | 0.09 | 0.09 | 0.09 | 0.11 | 0.14 | 53 | 53 | 55.5 | 59.5 | 68.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.412 | 20.424 | 20.871 | 25.251 | 31.287 | 0.027 | 0.027 | 0.027 | 0.033 | 0.042
KRT | W | 57.8 | 37.6 | 39 | 1 | 8.9893 | 3.1627 | 8.24 | 25.26 | 32.24 | 32.42 | 32.75 | 33.13 | 33.24 | 28.54 | 28.63 | 28.87 | 29.23 | 29.37 | - | - | 68.04 | 68.08 | 69.57 | 84.17 | 104.29 | 0.09 | 0.09 | 0.09 | 0.11 | 0.14 | 53 | 53 | 55.5 | 59.5 | 68.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.412 | 20.424 | 20.871 | 25.251 | 31.287 | 0.027 | 0.027 | 0.027 | 0.033 | 0.042
KYM | S | 52.6 | 33.8 | 39 | 0.98 | 12.9152 | 0 | 4.65 | 27.88 | 28.71 | 28.41 | 28.48 | 28.78 | 28.89 | 26.42 | 26.27 | 26.33 | 26.6 | 26.73 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KYM | W | 59 | 38.8 | 39 | 0.99 | 12.9152 | 0 | 4.65 | 20.74 | 20.4 | 20.43 | 20.59 | 20.84 | 20.9 | 19.21 | 19.25 | 19.41 | 19.67 | 19.73 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LV | S | 119.7 | 79.8 | 99 | 1 | 64.4246 | 15.7755 | 5.83 | 103.36 | 109.33 | 113.74 | 108.97 | 112.33 | 115.47 | 99.4 | 103.13 | 98.72 | 101.64 | 104.32 | 24.56% | 19.6 | 2045.79 | 3776.55 | 2657.3 | 4038.88 | 5606.21 | 1.47 | 2.72 | 1.92 | 2.91 | 4.04 | 266 | 460.5 | 358 | 499 | 638.5 | 487.67 | 836.01 | 529.23 | 812.31 | 1141.94 | 0.35 | 0.6 | 0.38 | 0.59 | 0.82 | 72 | 110.5 | 82.5 | 117.5 | 152.5 | 955.106 | 1718.172 | 1167.651 | 1780.281 | 2481.221 | 0.686 | 1.236 | 0.842 | 1.286 | 1.786
LV | W | 143.1 | 95.4 | 99 | 1 | 64.4246 | 15.7755 | 5.83 | 74.32 | 94.83 | 97.47 | 94.37 | 97.55 | 100.16 | 80.05 | 82.35 | 79.42 | 82.13 | 84.11 | - | - | 2045.79 | 3776.55 | 2657.3 | 4038.88 | 5606.21 | 1.47 | 2.72 | 1.92 | 2.91 | 4.04 | 266 | 460.5 | 358 | 499 | 638.5 | 487.67 | 836.01 | 529.23 | 812.31 | 1141.94 | 0.35 | 0.6 | 0.38 | 0.59 | 0.82 | 72 | 110.5 | 82.5 | 117.5 | 152.5 | 955.106 | 1718.172 | 1167.651 | 1780.281 | 2481.221 | 0.686 | 1.236 | 0.842 | 1.286 | 1.786
LVN | S | 111 | 79.7 | 129 | 0.99 | 13.257 | 4.9537 | 2.82 | 64.44 | 83.59 | 90.64 | 91.7 | 93.02 | 94.34 | 72.27 | 75.65 | 76.33 | 77.26 | 78.09 | - | - | 35.01 | 86.94 | 107.54 | 138.88 | 169.87 | 0.08 | 0.19 | 0.23 | 0.3 | 0.37 | 10 | 25.5 | 27 | 32.5 | 36.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.503 | 26.082 | 32.262 | 41.664 | 50.961 | 0.024 | 0.057 | 0.069 | 0.09 | 0.111
LVN | W | 120 | 85 | 129 | 0.96 | 13.257 | 4.9537 | 2.82 | 65.36 | 96.69 | 98 | 99.29 | 100.81 | 101.75 | 76.3 | 77.53 | 78.48 | 79.73 | 80.52 | - | - | 35.01 | 86.94 | 107.54 | 138.88 | 169.87 | 0.08 | 0.19 | 0.23 | 0.3 | 0.37 | 10 | 25.5 | 27 | 32.5 | 36.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.503 | 26.082 | 32.262 | 41.664 | 50.961 | 0.024 | 0.057 | 0.069 | 0.09 | 0.111
MBN | S | 83.2 | 37.6 | 59 | 0.98 | 19.9415 | 13.1463 | 2.58 | 43.68 | 52.78 | 53.35 | 53.88 | 54.72 | 55.47 | 47.6 | 48.11 | 48.66 | 49.47 | 50.11 | 26.6% | 10 | 436.65 | 558.18 | 681.85 | 843.78 | 993.2 | 0.39 | 0.5 | 0.61 | 0.76 | 0.89 | 103 | 127 | 152.5 | 184 | 210.5 | 117.54 | 153.41 | 196.69 | 258.04 | 310.48 | 0.11 | 0.14 | 0.18 | 0.23 | 0.28 | 41 | 50 | 62 | 75.5 | 87.5 | 213.273 | 274.841 | 342.238 | 433.762 | 515.296 | 0.194 | 0.248 | 0.309 | 0.389 | 0.463
MBN | W | 80.8 | 40.4 | 59 | 1 | 19.9415 | 13.1463 | 2.58 | 28.63 | 34.33 | 34.68 | 35.13 | 35.82 | 36.24 | 27.84 | 28.08 | 28.47 | 28.98 | 29.23 | - | - | 436.65 | 558.18 | 681.85 | 843.78 | 993.2 | 0.39 | 0.5 | 0.61 | 0.76 | 0.89 | 103 | 127 | 152.5 | 184 | 210.5 | 117.54 | 153.41 | 196.69 | 258.04 | 310.48 | 0.11 | 0.14 | 0.18 | 0.23 | 0.28 | 41 | 50 | 62 | 75.5 | 87.5 | 213.273 | 274.841 | 342.238 | 433.762 | 515.296 | 0.194 | 0.248 | 0.309 | 0.389 | 0.463
MDA | S | 79.4 | 39.7 | 66 | 0.98 | 20.3504 | 16.9568 | 2.91 | 51.03 | 56.64 | 56.48 | 56.86 | 57.43 | 57.86 | 51.43 | 51.1 | 51.1 | 51.41 | 51.7 | 29.55% | 11.73 | 582.49 | 650.12 | 877.8 | 1145.79 | 1362.58 | 0.28 | 0.31 | 0.42 | 0.55 | 0.65 | 130 | 146 | 196.5 | 255 | 295 | 197.88 | 206.74 | 251.4 | 314.04 | 367.1 | 0.1 | 0.1 | 0.12 | 0.15 | 0.18 | 58 | 62 | 77 | 93 | 108.5 | 313.263 | 339.754 | 439.32 | 563.565 | 665.744 | 0.154 | 0.163 | 0.21 | 0.27 | 0.321
MDA | W | 89.2 | 44.6 | 66 | 1 | 20.3504 | 16.9568 | 2.91 | 39.05 | 43.99 | 43.59 | 43.76 | 44.1 | 44.25 | 41.92 | 41.68 | 41.82 | 42.18 | 42.32 | - | - | 582.49 | 650.12 | 877.8 | 1145.79 | 1362.58 | 0.28 | 0.31 | 0.42 | 0.55 | 0.65 | 130 | 146 | 196.5 | 255 | 295 | 197.88 | 206.74 | 251.4 | 314.04 | 367.1 | 0.1 | 0.1 | 0.12 | 0.15 | 0.18 | 58 | 62 | 77 | 93 | 108.5 | 313.263 | 339.754 | 439.32 | 563.565 | 665.744 | 0.154 | 0.163 | 0.21 | 0.27 | 0.321
MLN | S | 119.7 | 79.8 | 99 | 1 | 55.7824 | 10.7075 | 3.86 | 90.63 | 107.55 | 118.59 | 118.87 | 128.33 | 138.31 | 96.01 | 106.03 | 106.33 | 115.65 | 124.87 | 20.31% | 16.21 | 983.65 | 2753.06 | 3166.2 | 6862.01 | 13493.28 | 0.71 | 1.98 | 2.28 | 32.21 | 237.98 | 111.5 | 284.5 | 330 | 600 | 981 | 202.22 | 751.95 | 836.54 | 2084.25 | 4669.54 | 0.15 | 0.54 | 0.6 | 1.5 | 11.86 | 38.5 | 88 | 99 | 218.5 | 431 | 436.649 | 1352.283 | 1535.438 | 3517.578 | 7316.662 | 0.318 | 0.972 | 1.104 | 10.713 | 79.696
MLN | W | 131.4 | 83.4 | 99 | 1 | 55.7824 | 10.7075 | 3.86 | 73.23 | 80.89 | 87.42 | 88.08 | 99.88 | 104.81 | 74.12 | 79.93 | 80.53 | 92.23 | 96.72 | - | - | 983.65 | 2753.06 | 3166.2 | 6862.01 | 13493.28 | 0.71 | 1.98 | 2.28 | 32.21 | 237.98 | 111.5 | 284.5 | 330 | 600 | 981 | 202.22 | 751.95 | 836.54 | 2084.25 | 4669.54 | 0.15 | 0.54 | 0.6 | 1.5 | 11.86 | 38.5 | 88 | 99 | 218.5 | 431 | 436.649 | 1352.283 | 1535.438 | 3517.578 | 7316.662 | 0.318 | 0.972 | 1.104 | 10.713 | 79.696
MNA | S | 74 | 37 | 66 | 0.98 | 18.4025 | 10.6694 | 3.04 | 38.55 | 48.59 | 48.89 | 49.4 | 50.05 | 50.53 | 43.64 | 43.9 | 44.32 | 44.85 | 45.32 | 17.95% | 6.64 | 264.79 | 309.05 | 377.94 | 462.48 | 534.69 | 0.13 | 0.15 | 0.18 | 0.22 | 0.26 | 86 | 99 | 119 | 141.5 | 161 | 42.56 | 50.07 | 63.17 | 80.3 | 98.64 | 0.02 | 0.02 | 0.03 | 0.04 | 0.05 | 22 | 26.5 | 30.5 | 38.5 | 46 | 109.229 | 127.764 | 157.601 | 194.954 | 229.455 | 0.053 | 0.059 | 0.075 | 0.094 | 0.113
MNA | W | 85 | 42.5 | 66 | 0.99 | 18.4025 | 10.6694 | 3.04 | 31.79 | 33.24 | 33.35 | 33.69 | 34.26 | 34.49 | 31.09 | 31.28 | 31.61 | 32.1 | 32.34 | - | - | 264.79 | 309.05 | 377.94 | 462.48 | 534.69 | 0.13 | 0.15 | 0.18 | 0.22 | 0.26 | 86 | 99 | 119 | 141.5 | 161 | 42.56 | 50.07 | 63.17 | 80.3 | 98.64 | 0.02 | 0.02 | 0.03 | 0.04 | 0.05 | 22 | 26.5 | 30.5 | 38.5 | 46 | 109.229 | 127.764 | 157.601 | 194.954 | 229.455 | 0.053 | 0.059 | 0.075 | 0.094 | 0.113
MRO | S | 36.6 | 18.3 | 26 | 1 | 13.5952 | 2.9341 | 5.18 | 21.94 | 23.37 | 23.37 | 23.48 | 23.65 | 23.78 | 21.63 | 21.56 | 21.67 | 21.82 | 21.93 | 18.2% | 3.33 | 234.7 | 253.08 | 285.98 | 330.86 | 368.9 | 0.19 | 0.2 | 0.23 | 0.26 | 0.29 | 150.5 | 164 | 181 | 207 | 231.5 | 58.83 | 60.29 | 71.36 | 85.65 | 97.21 | 0.05 | 0.05 | 0.06 | 0.07 | 0.08 | 56 | 59 | 69 | 78.5 | 83.5 | 111.591 | 118.127 | 135.746 | 159.213 | 178.717 | 0.092 | 0.095 | 0.111 | 0.127 | 0.143
MRO | W | 40.4 | 20.2 | 26 | 1 | 13.5952 | 2.9341 | 5.18 | 19.29 | 20.3 | 20.2 | 20.35 | 20.55 | 20.65 | 18.62 | 18.55 | 18.62 | 18.79 | 18.82 | - | - | 234.7 | 253.08 | 285.98 | 330.86 | 368.9 | 0.19 | 0.2 | 0.23 | 0.26 | 0.29 | 150.5 | 164 | 181 | 207 | 231.5 | 58.83 | 60.29 | 71.36 | 85.65 | 97.21 | 0.05 | 0.05 | 0.06 | 0.07 | 0.08 | 56 | 59 | 69 | 78.5 | 83.5 | 111.591 | 118.127 | 135.746 | 159.213 | 178.717 | 0.092 | 0.095 | 0.111 | 0.127 | 0.143
NHL | S | 26 | 13 | 20 | 1 | 4.3923 | 0 | 1.72 | 8.91 | 16.83 | 16.56 | 16.5 | 16.55 | 16.51 | 13.7 | 13.48 | 13.45 | 13.46 | 13.42 | 5.385% | 0.7 | 22.92 | 21.54 | 24.02 | 28.12 | 29.26 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 20.5 | 21.5 | 25 | 26.5 | 27.5 | 0.48 | 0.27 | 0.24 | 0.24 | 0.21 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 7.212 | 6.651 | 7.374 | 8.604 | 8.925 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006
NHL | W | 32.4 | 16.2 | 20 | 0.99 | 4.3923 | 0 | 1.72 | 7.91 | 17.07 | 16.82 | 16.81 | 16.86 | 16.81 | 13.6 | 13.39 | 13.37 | 13.41 | 13.37 | - | - | 22.92 | 21.54 | 24.02 | 28.12 | 29.26 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 20.5 | 21.5 | 25 | 26.5 | 27.5 | 0.48 | 0.27 | 0.24 | 0.24 | 0.21 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 7.212 | 6.651 | 7.374 | 8.604 | 8.925 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006
NKA | S | 48.8 | 30.5 | 39 | 0.99 | 23.1854 | 1.9815 | 8.69 | 26.52 | 32.45 | 32.81 | 34.08 | 34.59 | 34.92 | 29.04 | 29.41 | 30.69 | 31.17 | 31.53 | - | - | 9.24 | 16.26 | 56.55 | 84.02 | 105.73 | 0.02 | 0.03 | 0.09 | 0.14 | 0.17 | 14.5 | 20.5 | 50 | 65.5 | 79 | 0 | 0 | 0.16 | 0.95 | 1.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 2.772 | 4.878 | 17.077 | 25.871 | 33.091 | 0.006 | 0.009 | 0.027 | 0.042 | 0.051
NKA | W | 57.4 | 30.5 | 39 | 1 | 23.1854 | 1.9815 | 8.69 | 23.15 | 26.81 | 27.54 | 28.09 | 28.51 | 28.56 | 24.78 | 25.66 | 26.18 | 26.66 | 26.8 | - | - | 9.24 | 16.26 | 56.55 | 84.02 | 105.73 | 0.02 | 0.03 | 0.09 | 0.14 | 0.17 | 14.5 | 20.5 | 50 | 65.5 | 79 | 0 | 0 | 0.16 | 0.95 | 1.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 2.772 | 4.878 | 17.077 | 25.871 | 33.091 | 0.006 | 0.009 | 0.027 | 0.042 | 0.051
OYN | S | 32 | 15.2 | 26 | 0.95 | 3.5341 | 0 | 5.42 | 6.99 | 7.96 | 7.87 | 7.85 | 7.86 | 7.84 | 7.55 | 7.46 | 7.43 | 7.44 | 7.41 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OYN | W | 38.8 | 15.2 | 26 | 0.87 | 3.5341 | 0 | 5.42 | 6.18 | 6.83 | 6.77 | 6.77 | 6.79 | 6.77 | 6.52 | 6.47 | 6.47 | 6.5 | 6.47 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PLD | S | 44.2 | 22.1 | 32 | 1 | 14.1384 | 0 | 1.56 | 14.47 | 16.16 | 15.92 | 15.78 | 15.73 | 15.68 | 14.91 | 14.66 | 14.54 | 14.48 | 14.5 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PLD | W | 48 | 24 | 32 | 1 | 14.1384 | 0 | 1.56 | 16.83 | 17.99 | 17.9 | 17.94 | 18.02 | 17.99 | 17.34 | 17.25 | 17.28 | 17.35 | 17.31 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RVL | S | 32.8 | 20.4 | 37 | 1 | 5.4815 | 5.1061 | 2.06 | 21.51 | 24.72 | 25.95 | 28.18 | 28.77 | 29.19 | 21.55 | 22.75 | 24.89 | 25.42 | 25.82 | 5.637% | 1.15 | 57.28 | 117.48 | 336.71 | 423.54 | 489.65 | 0.09 | 0.19 | 0.55 | 0.69 | 0.8 | 46.5 | 75.5 | 160.5 | 182.5 | 198.5 | 1.46 | 6.88 | 46.91 | 68.16 | 87.67 | 0 | 0.01 | 0.08 | 0.11 | 0.14 | 2 | 10 | 38 | 50 | 60.5 | 18.206 | 40.06 | 133.85 | 174.774 | 208.264 | 0.027 | 0.064 | 0.221 | 0.284 | 0.338
RVL | W | 35.9 | 22.9 | 37 | 0.97 | 5.4815 | 5.1061 | 2.06 | 10.96 | 17.37 | 19.2 | 20.78 | 21.23 | 21.53 | 14.61 | 16.4 | 17.79 | 18.19 | 18.41 | - | - | 57.28 | 117.48 | 336.71 | 423.54 | 489.65 | 0.09 | 0.19 | 0.55 | 0.69 | 0.8 | 46.5 | 75.5 | 160.5 | 182.5 | 198.5 | 1.46 | 6.88 | 46.91 | 68.16 | 87.67 | 0 | 0.01 | 0.08 | 0.11 | 0.14 | 2 | 10 | 38 | 50 | 60.5 | 18.206 | 40.06 | 133.85 | 174.774 | 208.264 | 0.027 | 0.064 | 0.221 | 0.284 | 0.338
SA | S | 124.5 | 81.2 | 93 | 1 | 38.9298 | 3.5819 | 4.2 | 85.61 | 93.46 | 95.82 | 97.62 | 99.79 | 101.71 | 85.51 | 87.81 | 89.51 | 91.56 | 93.22 | 5.308% | 4.31 | 118.83 | 214.08 | 321.9 | 478.62 | 656.01 | 0.13 | 0.23 | 0.34 | 0.5 | 0.69 | 28 | 45.5 | 60.5 | 78.5 | 99.5 | 8.15 | 22.47 | 47.33 | 89.16 | 139.02 | 0.01 | 0.02 | 0.05 | 0.09 | 0.15 | 4 | 10 | 16.5 | 24.5 | 33.5 | 41.354 | 79.953 | 129.701 | 205.998 | 294.117 | 0.046 | 0.083 | 0.137 | 0.213 | 0.312
SA | W | 137.3 | 89.6 | 93 | 1 | 38.9298 | 3.5819 | 4.2 | 67.63 | 70.84 | 72.45 | 74.12 | 76.3 | 77.44 | 67.98 | 69.55 | 71.23 | 73.21 | 74.4 | - | - | 118.83 | 214.08 | 321.9 | 478.62 | 656.01 | 0.13 | 0.23 | 0.34 | 0.5 | 0.69 | 28 | 45.5 | 60.5 | 78.5 | 99.5 | 8.15 | 22.47 | 47.33 | 89.16 | 139.02 | 0.01 | 0.02 | 0.05 | 0.09 | 0.15 | 4 | 10 | 16.5 | 24.5 | 33.5 | 41.354 | 79.953 | 129.701 | 205.998 | 294.117 | 0.046 | 0.083 | 0.137 | 0.213 | 0.312
SHL | S | 55.5 | 36.7 | 39 | 1 | 44.9393 | 2.7817 | 4.66 | 34.69 | 41.31 | 40.26 | 39.79 | 39.41 | 39.32 | 37.05 | 36.39 | 36.2 | 36.24 | 36.21 | 0.9537% | 0.35 | 38.31 | 19 | 12.82 | 9.3 | 8.85 | 0.05 | 0.02 | 0.02 | 0.01 | 0.01 | 24 | 17.5 | 12 | 9 | 8 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 11.661 | 5.7 | 3.846 | 2.79 | 2.655 | 0.015 | 0.006 | 0.006 | 0.003 | 0.003
SHL | W | 60.6 | 40.4 | 39 | 0.98 | 44.9393 | 2.7817 | 4.66 | 27.04 | 30.36 | 30.07 | 30.05 | 30.14 | 30.05 | 27.43 | 27.21 | 27.23 | 27.33 | 27.24 | - | - | 38.31 | 19 | 12.82 | 9.3 | 8.85 | 0.05 | 0.02 | 0.02 | 0.01 | 0.01 | 24 | 17.5 | 12 | 9 | 8 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 11.661 | 5.7 | 3.846 | 2.79 | 2.655 | 0.015 | 0.006 | 0.006 | 0.003 | 0.003
SHN | S | 80 | 40 | 66 | 1 | 18.8331 | 0 | 3.22 | 32.28 | 42.39 | 38.73 | 39.16 | 39.78 | 40.25 | 38.29 | 34.74 | 35.22 | 35.82 | 36.25 | - | - | 5.08 | 0 | 0 | 0 | 0.18 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.524 | 0 | 0 | 0 | 0.054 | 0 | 0 | 0 | 0 | 0
SHN | W | 88.2 | 44.1 | 66 | 1 | 18.8331 | 0 | 3.22 | 29.91 | 34.7 | 29.95 | 30.22 | 30.65 | 30.86 | 33.22 | 28.74 | 28.99 | 29.41 | 29.6 | - | - | 5.08 | 0 | 0 | 0 | 0.18 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.524 | 0 | 0 | 0 | 0.054 | 0 | 0 | 0 | 0 | 0
SHP | S | 84.9 | 36.6 | 66 | 0.98 | 13.4153 | 0 | 5.48 | 19.71 | 36.1 | 35.57 | 34.78 | 34.81 | 34.68 | 24.16 | 24.08 | 24.09 | 24.26 | 24.36 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SHP | W | 91.4 | 41.9 | 66 | 0.99 | 13.4153 | 0 | 5.48 | 16.69 | 30.71 | 29.94 | 29.56 | 28.55 | 28.05 | 19.2 | 19.19 | 19.29 | 19.42 | 19.43 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SSE | S | 131.8 | 89.7 | 99 | 0.98 | 20.3397 | 0 | 3.33 | 68.06 | 73.83 | 74.84 | 75.67 | 77 | 78.07 | 68.67 | 69.14 | 69.71 | 70.58 | 71.41 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SSE | W | 148.5 | 99 | 99 | 0.99 | 20.3397 | 0 | 3.33 | 59.88 | 64.82 | 65.38 | 66.4 | 67.55 | 68.27 | 62.67 | 63.01 | 63.91 | 64.96 | 65.58 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
STL | S | 37 | 18.5 | 26 | 0.97 | 6.6493 | 4.0772 | 6.53 | 17.34 | 19.54 | 19.47 | 19.33 | 19.29 | 19.21 | 18.29 | 18.22 | 18.12 | 18.05 | 17.95 | - | - | 0.89 | 0.87 | 0.49 | 0.42 | 0.26 | 0 | 0 | 0 | 0 | 0 | 2.5 | 3.5 | 3 | 3 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.267 | 0.261 | 0.147 | 0.126 | 0.078 | 0 | 0 | 0 | 0 | 0
STL | W | 37.6 | 18.8 | 26 | 0.96 | 6.6493 | 4.0772 | 6.53 | 15.7 | 19.56 | 19.46 | 19.33 | 19.3 | 19.2 | 18.29 | 18.11 | 18.03 | 17.99 | 17.88 | - | - | 0.89 | 0.87 | 0.49 | 0.42 | 0.26 | 0 | 0 | 0 | 0 | 0 | 2.5 | 3.5 | 3 | 3 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.267 | 0.261 | 0.147 | 0.126 | 0.078 | 0 | 0 | 0 | 0 | 0
STN | S | 112.3 | 61.9 | 79 | 0.98 | 19.3432 | 0 | 3.04 | 49.61 | 51.58 | 58.21 | 58.67 | 59.44 | 60.05 | 48.58 | 54.73 | 55.06 | 55.69 | 56.21 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
STN | W | 114.7 | 61.9 | 79 | 1 | 19.3432 | 0 | 3.04 | 35.42 | 45.3 | 45.54 | 45.94 | 46.55 | 46.9 | 42.25 | 42.46 | 42.78 | 43.31 | 43.62 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SU | S | 139.5 | 93 | 99 | 1 | 32.1099 | 9.7549 | 3.8 | 88.12 | 97.27 | 100.28 | 104.34 | 106.7 | 108.69 | 86.68 | 89.89 | 93.63 | 96.02 | 97.92 | - | - | 6 | 22.3 | 86.54 | 160.15 | 254.27 | 0 | 0.02 | 0.06 | 0.12 | 0.18 | 2.5 | 9 | 22.5 | 37 | 54.5 | 0 | 0 | 0.1 | 3.71 | 9.48 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0.5 | 2 | 4.5 | 1.8 | 6.69 | 26.032 | 50.642 | 82.917 | 0 | 0.006 | 0.018 | 0.036 | 0.061
SU | W | 148.5 | 99 | 99 | 1 | 32.1099 | 9.7549 | 3.8 | 72.71 | 84.43 | 86.81 | 90 | 91.36 | 92.53 | 75.71 | 77.84 | 81.67 | 83.46 | 84.81 | - | - | 6 | 22.3 | 86.54 | 160.15 | 254.27 | 0 | 0.02 | 0.06 | 0.12 | 0.18 | 2.5 | 9 | 22.5 | 37 | 54.5 | 0 | 0 | 0.1 | 3.71 | 9.48 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0.5 | 2 | 4.5 | 1.8 | 6.69 | 26.032 | 50.642 | 82.917 | 0 | 0.006 | 0.018 | 0.036 | 0.061
TNA | S | 142.8 | 95.2 | 99 | 1 | 65.2379 | 36.962 | 2.77 | 116.41 | 145.38 | 160.5 | 129.53 | 136.14 | 141.54 | 123.61 | 136.15 | 109.11 | 113.9 | 117.88 | 29.84% | 28.41 | 3043.88 | 8681.33 | 1558.28 | 2785.72 | 4179.3 | 4.22 | 112.02 | 0.75 | 1.34 | 2.01 | 222 | 621 | 155.5 | 239.5 | 336.5 | 544.95 | 1873.86 | 96.62 | 247.76 | 469.78 | 0.26 | 0.9 | 0.05 | 0.12 | 0.23 | 62.5 | 153.5 | 20.5 | 48 | 71.5 | 1294.629 | 3916.101 | 535.118 | 1009.148 | 1582.636 | 1.448 | 34.236 | 0.26 | 0.486 | 0.764
TNA | W | 142.8 | 95.2 | 99 | 1 | 65.2379 | 36.962 | 2.77 | 90.85 | 127.43 | 150.2 | 112.15 | 117.27 | 121.02 | 110.2 | 131.74 | 95.47 | 98.91 | 101.91 | 15.76% | 15 | 3043.88 | 8681.33 | 1558.28 | 2785.72 | 4179.3 | 4.22 | 112.02 | 0.75 | 1.34 | 2.01 | 222 | 621 | 155.5 | 239.5 | 336.5 | 544.95 | 1873.86 | 96.62 | 247.76 | 469.78 | 0.26 | 0.9 | 0.05 | 0.12 | 0.23 | 62.5 | 153.5 | 20.5 | 48 | 71.5 | 1294.629 | 3916.101 | 535.118 | 1009.148 | 1582.636 | 1.448 | 34.236 | 0.26 | 0.486 | 0.764
TQY | S | 99 | 49.5 | 66 | 1 | 26.9586 | 0 | 8.15 | 37.43 | 39.32 | 41.39 | 42.06 | 43.07 | 44.04 | 34.37 | 36.21 | 36.83 | 37.72 | 38.78 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TQY | W | 99 | 49.5 | 66 | 1 | 26.9586 | 0 | 8.15 | 29.52 | 39.54 | 40.73 | 41.65 | 42.73 | 43.65 | 36.79 | 38.02 | 38.9 | 40.01 | 40.82 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TRG | S | 58.3 | 19.2 | 46 | 0.98 | 14.8627 | 5.1442 | 1.81 | 16.42 | 23.95 | 23.98 | 24.15 | 24.5 | 24.84 | 18.04 | 18.04 | 18.23 | 18.54 | 18.78 | - | - | 58.55 | 61.18 | 67.98 | 83.66 | 99.43 | 0.05 | 0.06 | 0.06 | 0.08 | 0.09 | 39.5 | 43 | 46 | 50 | 57.5 | 0 | 0.07 | 0.22 | 0.43 | 0.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 1 | 17.565 | 18.403 | 20.548 | 25.399 | 30.2 | 0.015 | 0.018 | 0.018 | 0.024 | 0.027
TRG | W | 58.8 | 19.4 | 46 | 1 | 14.8627 | 5.1442 | 1.81 | 16.79 | 21.12 | 21.28 | 21.61 | 22.08 | 22.21 | 19.44 | 19.59 | 19.89 | 20.31 | 20.45 | 0.2062% | 0.04 | 58.55 | 61.18 | 67.98 | 83.66 | 99.43 | 0.05 | 0.06 | 0.06 | 0.08 | 0.09 | 39.5 | 43 | 46 | 50 | 57.5 | 0 | 0.07 | 0.22 | 0.43 | 0.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 1 | 17.565 | 18.403 | 20.548 | 25.399 | 30.2 | 0.015 | 0.018 | 0.018 | 0.024 | 0.027
WBE | S | 123.7 | 82.8 | 99 | 1 | 65.516 | 8.7642 | 4.81 | 120.43 | 131.22 | 136.79 | 123.94 | 127.69 | 130.96 | 116.73 | 120.98 | 109.12 | 112.54 | 115.43 | 40.98% | 33.93 | 6300.8 | 11563.8 | 5863.69 | 8339.2 | 10857.74 | 24.76 | 108.56 | 4.41 | 13.89 | 33.78 | 567.5 | 903.5 | 560 | 738.5 | 907 | 1460.58 | 2492.9 | 1063.24 | 1691.06 | 2380.54 | 1.05 | 1.8 | 0.77 | 1.22 | 1.72 | 147.5 | 248 | 134.5 | 199.5 | 266 | 2912.646 | 5214.17 | 2503.375 | 3685.502 | 4923.7 | 8.163 | 33.828 | 1.862 | 5.021 | 11.338
WBE | W | 137.3 | 92.2 | 99 | 1 | 65.516 | 8.7642 | 4.81 | 81.75 | 97.66 | 100.2 | 89.55 | 92.96 | 95.46 | 88.64 | 92.09 | 83.17 | 86.1 | 88.36 | - | - | 6300.8 | 11563.8 | 5863.69 | 8339.2 | 10857.74 | 24.76 | 108.56 | 4.41 | 13.89 | 33.78 | 567.5 | 903.5 | 560 | 738.5 | 907 | 1460.58 | 2492.9 | 1063.24 | 1691.06 | 2380.54 | 1.05 | 1.8 | 0.77 | 1.22 | 1.72 | 147.5 | 248 | 134.5 | 199.5 | 266 | 2912.646 | 5214.17 | 2503.375 | 3685.502 | 4923.7 | 8.163 | 33.828 | 1.862 | 5.021 | 11.338
WBL | S | 82 | 49.2 | 79 | 0.98 | 13.8094 | 8.7642 | 4.71 | 51.88 | 55.5 | 54.71 | 54.68 | 54.89 | 55 | 50.14 | 49.6 | 49.41 | 49.53 | 49.72 | 1.911% | 0.94 | 46.92 | 34.94 | 35.9 | 42.64 | 47.83 | 0.15 | 0.11 | 0.12 | 0.14 | 0.16 | 23.5 | 21 | 21.5 | 25 | 28.5 | 0.64 | 0.01 | 0 | 0 | 0.07 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0.5 | 0 | 0 | 0.5 | 14.524 | 10.489 | 10.77 | 12.792 | 14.398 | 0.045 | 0.033 | 0.036 | 0.042 | 0.048
WBL | W | 90.7 | 54.8 | 79 | 1 | 13.8094 | 8.7642 | 4.71 | 48.34 | 53.09 | 53.31 | 53.78 | 54.36 | 54.62 | 47.71 | 47.84 | 48.29 | 48.8 | 49.07 | - | - | 46.92 | 34.94 | 35.9 | 42.64 | 47.83 | 0.15 | 0.11 | 0.12 | 0.14 | 0.16 | 23.5 | 21 | 21.5 | 25 | 28.5 | 0.64 | 0.01 | 0 | 0 | 0.07 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0.5 | 0 | 0 | 0.5 | 14.524 | 10.489 | 10.77 | 12.792 | 14.398 | 0.045 | 0.033 | 0.036 | 0.042 | 0.048
WIN | S | 29.7 | 10.5 | 20 | 0.92 | 16.3808 | 0 | 2.58 | 9.31 | 9.91 | 9.99 | 10.07 | 10.2 | 10.32 | 9.23 | 9.3 | 9.37 | 9.49 | 9.59 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WIN | W | 30.7 | 10.5 | 20 | 0.9 | 16.3808 | 0 | 2.58 | 9.72 | 10.38 | 10.48 | 10.61 | 10.77 | 10.84 | 9.85 | 9.95 | 10.07 | 10.23 | 10.3 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WMN | S | 33 | 17.2 | 46 | 0.98 | 1.7882 | 5.3347 | 5.22 | 24.65 | 27.81 | 27.85 | 28.12 | 28.61 | 28.98 | 24.25 | 24.3 | 24.54 | 24.97 | 25.28 | 40.99% | 7.05 | 991.52 | 1002.72 | 1060.35 | 1172.5 | 1264.39 | 0.48 | 0.48 | 0.51 | 0.56 | 0.61 | 295 | 299 | 312 | 342.5 | 372 | 285.99 | 291.38 | 315.54 | 362.32 | 395.89 | 0.14 | 0.14 | 0.15 | 0.17 | 0.19 | 129.5 | 131 | 135.5 | 144.5 | 150.5 | 497.649 | 504.782 | 538.983 | 605.374 | 656.44 | 0.242 | 0.242 | 0.258 | 0.287 | 0.316
WMN | W | 33 | 20.2 | 46 | 1 | 1.7882 | 5.3347 | 5.22 | 15.48 | 20.9 | 20.95 | 21.23 | 21.63 | 21.8 | 18.01 | 18.09 | 18.32 | 18.68 | 18.8 | - | - | 991.52 | 1002.72 | 1060.35 | 1172.5 | 1264.39 | 0.48 | 0.48 | 0.51 | 0.56 | 0.61 | 295 | 299 | 312 | 342.5 | 372 | 285.99 | 291.38 | 315.54 | 362.32 | 395.89 | 0.14 | 0.14 | 0.15 | 0.17 | 0.19 | 129.5 | 131 | 135.5 | 144.5 | 150.5 | 497.649 | 504.782 | 538.983 | 605.374 | 656.44 | 0.242 | 0.242 | 0.258 | 0.287 | 0.316
WND | S | 76.6 | 37.5 | 66 | 0.99 | 17.8521 | 1.1432 | 6.69 | 22.86 | 25.03 | 25.49 | 26.11 | 26.71 | 27.32 | 21.61 | 21.97 | 22.53 | 23.18 | 23.8 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WND | W | 86.4 | 42.7 | 66 | 1 | 17.8521 | 1.1432 | 6.69 | 28.98 | 27.06 | 27.63 | 28.39 | 29.16 | 29.75 | 25.14 | 25.71 | 26.42 | 27.2 | 27.74 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WPD | S | 96.5 | 56.8 | 81 | 1 | 24.2982 | 2.2863 | 4.7 | 51.38 | 60.54 | 63.02 | 65.57 | 68.29 | 71 | 54.3 | 56.55 | 58.77 | 61.37 | 63.7 | - | - | 11.61 | 47.32 | 128.94 | 285.09 | 537.08 | 0.01 | 0.05 | 0.13 | 0.29 | 0.55 | 8.5 | 21.5 | 44 | 78 | 128.5 | 0 | 0 | 3.02 | 21.95 | 65.52 | 0 | 0 | 0 | 0.02 | 0.07 | 0 | 0 | 2.5 | 13.5 | 26.5 | 3.483 | 14.196 | 40.796 | 100.892 | 206.988 | 0.003 | 0.015 | 0.039 | 0.101 | 0.214
WPD | W | 106.2 | 62.6 | 81 | 1 | 24.2982 | 2.2863 | 4.7 | 43.98 | 48.84 | 50.73 | 52.84 | 55.29 | 57.17 | 46.47 | 48.32 | 50.35 | 52.55 | 54.38 | - | - | 11.61 | 47.32 | 128.94 | 285.09 | 537.08 | 0.01 | 0.05 | 0.13 | 0.29 | 0.55 | 8.5 | 21.5 | 44 | 78 | 128.5 | 0 | 0 | 3.02 | 21.95 | 65.52 | 0 | 0 | 0 | 0.02 | 0.07 | 0 | 0 | 2.5 | 13.5 | 26.5 | 3.483 | 14.196 | 40.796 | 100.892 | 206.988 | 0.003 | 0.015 | 0.039 | 0.101 | 0.214