## Intro
Powercor 2024 Distribution System Limitation Template
This Distribution Systems Limitations template is intended to make the Distribution Annual Planning Report (DAPR) limitation data more accessible and usable. Any information provided in this System Limitations template should be read in conjunction with the Powercor 2024 DAPR. It should also be noted that the information in this template and the DAPR are based on high-level risk assessments produced for the DAPR. As such the numbers are indicative and subject to change. Therefore the information in this template should not be used to make investment decisions, and should only be used to assist in discussions with Powercor. Finalised data will be produced in a detailed risk assessment conducted at the RIT-D or business case stage. However Powercor invites interested parties to submit their proposals or to engage in joint planning with Powercor as early as possible in order to defer or avoid the proposed augmentation. Powercor also publishes its own Network Limitation maps in order to assist with the visualisation of the limitation data presented within this template and the DAPR. The data in this template will be updated annually and will be published along with the DAPR. We welcome any feedback to improve the content or usability of this template.

## Powercor Limitations
Owner | Asset Name | Asset Code | Network Element | Voltage level (kV) | Rating |  |  |  | Nameplate Rating | Location |  |  |  | Residential customers affected |  | Business Case | [7 empty] | Demand Reduction required to defer investment by 1 year |  | Emergency Generation |  | Load Transfer capability (MVA) | Power Factor | 10% POE | [14 empty] | 50% POE | [14 empty] | Weighted Energy at Risk (MWh) |  |  |  |  | Weighted Expected Energy at Risk (MWh)
[5 empty] | Summer |  | Winter |  |  | Start |  | End |  |  |  | Constraint Primary Driver | Investment Description | Preferred network investment |  |  |  | Proposed Timing | Annual Deferral Value | [6 empty] | Summer Forecast Maximum Demand (MVA) |  |  |  |  | Maximum Load at risk (MVA) (N-1) |  |  |  |  | Hours at Risk (Hrs) |  |  |  |  | Summer Forecast Maximum Demand (MVA) |  |  |  |  | Maximum Load at risk (MVA) (N-1) |  |  |  |  | Hours at Risk (Hrs)
[5 empty] | N Rating (MVA) | N-1 Rating (MVA) | N Rating (MVA) | N-1 Rating (MVA) |  | Longitude | Latitude | Longitude | Latitude | Count | Percent |  |  | capital cost ($) | cost accuracy plus | cost accuracy minus | Operating cost ($) |  |  | (MW) | (MVA) | (MW) | (MVA) |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029
Note on AA1: Lin, Tim: E.g. contracting backup generators in a hospital to become embedded generators during unuasually high peaks

## Sub-T Aug Sum
Sub transmission line | Season | Line N Import Rating (MVA) | Line Power Factor at Minimum Demand | Embedded Generation Capacity (MVA) | Load Transfer Capability (MVA) | Hours load is > 95% of Minimum Demand (Hrs) | Actual Minimum Demand (MVA) | 50% POE |  |  |  |  | 50% POE load above N Import Rating (%) | 50% POE load above N Import Rating (MVA) | 50% POE
[8 empty] | Forecast Minimum Demand (MVA) | [6 empty] | Energy at Risk (MWh) |  |  |  |  | Expected Energy at Risk (MWh) |  |  |  |  | Hours at Risk (Hrs)
|  |  | 2024 | 2024 | 2025 | 2024 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2025 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029
ATS-ATD | S | 102.3 | 1 |  |  |  | 11.6 | 3 | 4.9 | 28.7 | 54.4 | 62 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-ATD | W | 130.3 | 1 |  |  |  | 11.6 | 2.9 | 13.8 | 43.9 | 60.3 | 62 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-NRB | S | 52.6 | 0.53204 |  |  |  | 82.7 | 82.4 | 82.7 | 82.8 | 82.7 | 82.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-NRB | W | 52.6 | 0.53019 |  |  |  | 82.8 | 82.6 | 82.8 | 82.5 | 82.8 | 82.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GHP | S | 74.3 | 0.86728 |  |  |  | 32.4 | 35.4 | 39.6 | 42.1 | 44.6 | 46.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GHP | W | 87.5 | 0.88746 |  |  |  | 31.1 | 35.6 | 37.5 | 39.9 | 41.8 | 43.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BETS-MRO | S | 76.6 | 0.97059 |  |  |  | 3.4 | 14.5 | 14.8 | 18.5 | 22.1 | 25.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BETS-MRO | W | 89.2 | 0.96429 |  |  |  | 2.8 | 3.3 | 4.2 | 5.3 | 6.2 | 6.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-CHM | S | 26.2 | 0.055556 |  |  |  | 1.8 | 1.8 | 1.8 | 1.9 | 2 | 2.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-CHM | W | 35.4 | 0.055556 |  |  |  | 1.8 | 1.8 | 1.8 | 1.9 | 2 | 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SA1 | S | 116.6 | 0.5 |  |  |  | 6 | 9.4 | 13.6 | 20.1 | 27.2 | 33.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SA1 | W | 122.3 | 0.5 |  |  |  | 6 | 5.8 | 9.7 | 15 | 20.2 | 25.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BGR-ART | S | 45.7 | 0.88525 |  |  |  | 30.5 | 30.4 | 30.4 | 30.4 | 30.5 | 30.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BGR-ART | W | 47.4 | 0.88525 |  |  |  | 30.5 | 30.4 | 30.5 | 30.4 | 30.4 | 30.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MBN-DTN | S | 74.3 | 0.35897 |  |  |  | 3.9 | 2.6 | 3 | 3.5 | 4 | 4.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MBN-DTN | W | 86.9 | 0.5 |  |  |  | 1.6 | 1.6 | 1.6 | 1.7 | 1.7 | 1.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BETS-CMN | S | 64 | 0.9697 |  |  |  | 3.3 | 15 | 15.3 | 19.1 | 22.8 | 26.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BETS-CMN | W | 65.2 | 1 |  |  |  | 2.7 | 3.1 | 4 | 5.1 | 6 | 6.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CMN-MRO | S | 26.3 | 1 |  |  |  | 3 | 12 | 11.2 | 14.2 | 17.1 | 19.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CMN-MRO | W | 35.4 | 1 |  |  |  | 2.7 | 2.1 | 3.1 | 4 | 4.7 | 5.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-STL2 | S | 25.7 | 0.61972 |  |  |  | 14.2 | 14.6 | 15 | 15.7 | 16.5 | 17.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-STL2 | W | 34.9 | 0.63768 |  |  |  | 13.8 | 14 | 14.5 | 14.9 | 15.3 | 15.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BPA-HTH | S | 17.7 | 0 |  |  |  | 0.8 | 1 | 1.2 | 1.4 | 1.6 | 1.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BPA-HTH | W | 35.4 | 0 |  |  |  | 1 | 1.2 | 1.3 | 1.5 | 1.7 | 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-STL1 | S | 49.2 | 0.7377 |  |  |  | 18.3 | 19.6 | 20.1 | 21 | 22.1 | 23 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-STL1 | W | 57.2 | 0.7377 |  |  |  | 18.3 | 18.8 | 19.4 | 20 | 20.6 | 21.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
AL-BLTS | S | 91.4 | 0.57407 |  |  |  | 5.4 | 6.2 | 6 | 6.3 | 10.8 | 13.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
AL-BLTS | W | 91.4 | 0.60606 |  |  |  | 6.6 | 5.6 | 5.4 | 8.5 | 11 | 11.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BETS-BGO | S | 109.7 | 0.95455 |  |  |  | 4.4 | 1.9 | 5.5 | 11.9 | 18.3 | 23.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BETS-BGO | W | 114.3 | 0.95455 |  |  |  | 4.4 | 2.3 | 3.1 | 8.3 | 12.7 | 16.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-MDA2 | S | 104 | 0.32558 |  |  |  | 4.3 | 3.2 | 3.9 | 6.7 | 9.7 | 12.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-MDA2 | W | 114.3 | 0.38235 |  |  |  | 3.4 | 2.5 | 1.4 | 2.9 | 4.7 | 6.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-MDA1 | S | 72 | 0.30769 |  |  |  | 3.9 | 2.9 | 3.5 | 6 | 8.7 | 10.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-MDA1 | W | 90.9 | 0.35484 |  |  |  | 3.1 | 2.3 | 1.1 | 2.6 | 4.2 | 5.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HKT-LV | S | 135.5 | 0.90769 |  |  |  | 13 | 26.9 | 34.7 | 39.9 | 48.6 | 65.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HKT-LV | W | 142.3 | 0.90769 |  |  |  | 13 | 20.8 | 28.1 | 37.6 | 56.7 | 78.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-FDN | S | 102.9 | 0.66667 |  |  |  | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-FDN | W | 134.9 | 0 |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WETS-WSF | S | 84.6 | 0.99545 |  |  |  | 88 | 88.1 | 88.1 | 88 | 88 | 88 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WETS-WSF | W | 106.3 | 0.99553 |  |  |  | 89.5 | 91.5 | 91.5 | 91.4 | 91.5 | 91.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WSF-WMN | S | 31.4 | 1 |  |  |  | 1.4 | 6.1 | 6.1 | 6.2 | 6.3 | 6.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WSF-WMN | W | 43.4 | 1 |  |  |  | 1.2 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-AC | S | 102.3 | 0.52941 |  |  |  | 5.1 | 12.3 | 12.9 | 13.8 | 15 | 15.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-AC | W | 108 | 0.2093 |  |  |  | 4.3 | 12.5 | 13 | 14.1 | 14.7 | 14.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GB-GL | S | 89.7 | 1 |  |  |  | 14.4 | 12.6 | 12.9 | 9.2 | 5.9 | 5.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GB-GL | W | 100.6 | 1 |  |  |  | 14.4 | 15.3 | 14.2 | 10.4 | 7.5 | 5.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-SHN2 | S | 88 | 0.98571 |  |  |  | 7 | 3.6 | 5 | 6.2 | 7.3 | 8.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-SHN2 | W | 112 | 0.97143 |  |  |  | 7 | 1.6 | 4.6 | 5.6 | 6.5 | 7.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-HTN | S | 47.4 | 0.34797 |  |  |  | 61.5 | 61.6 | 61.4 | 61.9 | 61.8 | 61.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-HTN | W | 48 | 0.34853 |  |  |  | 61.4 | 61.3 | 61.8 | 61.6 | 61.4 | 61.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-SHN1 | S | 88 | 0.98571 |  |  |  | 7 | 3.6 | 5 | 6.2 | 7.3 | 8.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-SHN1 | W | 112 | 0.97143 |  |  |  | 7 | 1.6 | 4.6 | 5.6 | 6.5 | 7.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KWF-NHL | S | 44 | 0.81395 |  |  |  | 4.3 | 6.9 | 7.2 | 7.7 | 8.2 | 8.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KWF-NHL | W | 43.4 | 0.8 |  |  |  | 4 | 6.6 | 6.8 | 7.1 | 7.4 | 7.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WETS-BPA | S | 31.4 | 0 |  |  |  | 1.5 | 1.6 | 1.7 | 1.9 | 2.1 | 2.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WETS-BPA | W | 43.4 | 0 |  |  |  | 1.6 | 1.8 | 1.9 | 2 | 2.2 | 2.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KRT-PLD1/CWF | S | 40 | 0.85169 |  |  |  | 23.6 | 25 | 25.8 | 26.7 | 27.6 | 28.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KRT-PLD1/CWF | W | 45.7 | 0.8502 |  |  |  | 24.7 | 24.8 | 25.6 | 26.3 | 26.9 | 27.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
NKA-CME | S | 74.3 | 1 |  |  |  | 10.5 | 12.9 | 14.3 | 15.8 | 17.3 | 18.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
NKA-CME | W | 86.9 | 1 |  |  |  | 11.4 | 12.1 | 13.6 | 15 | 16.1 | 17.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-WBE | S | 109.7 | 0.86087 |  |  |  | 11.5 | 20.8 | 29 | 35.3 | 43 | 48.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-WBE | W | 134.9 | 0.86726 |  |  |  | 11.3 | 16.8 | 24.2 | 27.1 | 31.7 | 36.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-CDN | S | 76.6 | 0.83191 |  |  |  | 47 | 45.4 | 44.7 | 44.2 | 43.6 | 43.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-CDN | W | 85.7 | 0.82064 |  |  |  | 40.7 | 44.2 | 43.7 | 45.7 | 47.1 | 48.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
NSF-NKA | S | 102.9 | 0.95515 |  |  |  | 104.8 | 104.7 | 104.7 | 105.4 | 104.6 | 105.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
NSF-NKA | W | 114.3 | 0.95579 |  |  |  | 106.3 | 105.5 | 105.2 | 104.8 | 105 | 104.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MDA-MBN | S | 74.3 | 0.70968 |  |  |  | 3.1 | 4.4 | 5.2 | 6.6 | 7.8 | 8.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MDA-MBN | W | 86.9 | 0.72222 |  |  |  | 1.8 | 2 | 2.2 | 2.5 | 2.9 | 3.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BAN-BGR | S | 46.3 | 0.74266 |  |  |  | 57.9 | 61.3 | 62.1 | 62.9 | 64 | 65 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BAN-BGR | W | 49.7 | 0.74093 |  |  |  | 57.9 | 60.4 | 61.1 | 61.8 | 62.2 | 62.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-TYA | S | 102.3 | 0.54237 |  |  |  | 5.9 | 5.4 | 5.4 | 8.8 | 14.4 | 17.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-TYA | W | 130.3 | 0.54217 |  |  |  | 8.3 | 5.5 | 5.8 | 11.9 | 15.3 | 15.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-TNA2 | S | 109.7 | 0.92925 |  |  |  | 21.2 | 20.5 | 17.7 | 13.6 | 13.3 | 13.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-TNA2 | W | 134.9 | 0.92925 |  |  |  | 21.2 | 13.4 | 14.1 | 13.4 | 13.4 | 14.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KGTS-SHL | S | 40 | 1 |  |  |  | 8.9 | 10 | 10.3 | 10.6 | 11.3 | 11.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KGTS-SHL | W | 49.7 | 0.98969 |  |  |  | 9.7 | 11.3 | 11.9 | 12.5 | 13.1 | 13.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BETS-EHK | S | 111.4 | 0.81081 |  |  |  | 3.7 | 2 | 5.5 | 11.9 | 18.3 | 23.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BETS-EHK | W | 111.4 | 0.83784 |  |  |  | 3.7 | 2.9 | 3 | 8.3 | 12.7 | 16.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GHP-BCG | S | 109.7 | 0.87647 |  |  |  | 34 | 33.5 | 32.9 | 33.3 | 33.8 | 34.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GHP-BCG | W | 134.9 | 0.89297 |  |  |  | 32.7 | 31.7 | 32 | 32.7 | 33.3 | 34.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TRG-WBL1 | S | 47.4 | 0.65741 |  |  |  | 10.8 | 11.4 | 12.6 | 14.4 | 16.1 | 17.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TRG-WBL1 | W | 49.7 | 0.8284 |  |  |  | 16.9 | 17 | 17.1 | 17 | 16.9 | 17 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TRG-WBL2 | S | 45.7 | 0.59302 |  |  |  | 8.6 | 9.1 | 10.1 | 11.6 | 13 | 14.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TRG-WBL2 | W | 46.3 | 0.76642 |  |  |  | 13.7 | 13.7 | 13.8 | 13.7 | 13.7 | 13.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
AWT-LV | S | 109.7 | 0.90769 |  |  |  | 13 | 26.8 | 34.7 | 39.9 | 47.7 | 53.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
AWT-LV | W | 134.9 | 0.90769 |  |  |  | 13 | 20.8 | 28.1 | 31.8 | 37 | 41.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GCY | S | 90.3 | 1 |  |  |  | 18 | 15.2 | 15.4 | 11.7 | 7.8 | 6.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GCY | W | 96.6 | 1 |  |  |  | 18 | 18.2 | 16.9 | 13.1 | 9.9 | 7.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FDN-CRO | S | 109.7 | 1 |  |  |  | 0.2 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FDN-CRO | W | 134.9 | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAN2 | S | 96 | 0.77987 |  |  |  | 31.8 | 41.2 | 41.4 | 45 | 50.6 | 55.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAN2 | W | 114.3 | 0.77358 |  |  |  | 31.8 | 30.7 | 33.6 | 38.4 | 42.2 | 46 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAN1 | S | 96 | 0.78125 |  |  |  | 32 | 41.4 | 41.6 | 45.3 | 50.9 | 55.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAN1 | W | 114.3 | 0.77187 |  |  |  | 32 | 30.9 | 33.8 | 38.6 | 42.5 | 46.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-SHP | S | 101.7 | 0.89531 |  |  |  | 100.3 | 106.5 | 107.6 | 108.4 | 109.6 | 110.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-SHP | W | 116 | 0.89178 |  |  |  | 99.8 | 102.8 | 103.3 | 104.8 | 105.3 | 106.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-ATD | S | 97.2 | 0.99145 |  |  |  | 11.7 | 2.1 | 5.3 | 28.7 | 54.2 | 61.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-ATD | W | 125.7 | 0.99145 |  |  |  | 11.7 | 2.4 | 13.9 | 43.8 | 60 | 61.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
STL-ART | S | 38.3 | 0.7717 |  |  |  | 31.1 | 34.2 | 34.7 | 35.5 | 36.4 | 37.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
STL-ART | W | 43.4 | 0.7717 |  |  |  | 31.1 | 33.2 | 33.8 | 34.3 | 34.9 | 35.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BETS-CTN | S | 26.3 | 0.72152 |  |  |  | 23.7 | 22.9 | 23.5 | 24.4 | 25.1 | 25.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BETS-CTN | W | 30.3 | 0.7489 |  |  |  | 22.7 | 22.2 | 22.7 | 23.2 | 23.6 | 24.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-HSM2 | S | 49.2 | 0.65517 |  |  |  | 2.9 | 3.6 | 6.2 | 9.4 | 12.6 | 15.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-HSM2 | W | 52.6 | 0.65517 |  |  |  | 2.9 | 3.2 | 5.8 | 8.5 | 10.8 | 13.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-HSM1 | S | 49.2 | 0.65517 |  |  |  | 2.9 | 3.6 | 6.2 | 9.4 | 12.6 | 15.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-HSM1 | W | 52.6 | 0.65517 |  |  |  | 2.9 | 3.2 | 5.8 | 8.5 | 10.8 | 13.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HTH-OYN | S | 17.7 | 0 |  |  |  | 1.2 | 1.6 | 1.9 | 2.4 | 2.8 | 3.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HTH-OYN | W | 35.4 | 0 |  |  |  | 1.5 | 1.8 | 2.2 | 2.6 | 3.1 | 3.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-CRO | S | 91.4 | 0.66667 |  |  |  | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-CRO | W | 91.4 | 0 |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHP-KYM | S | 84.6 | 0.99 |  |  |  | 100 | 106.6 | 107.2 | 108.4 | 109.7 | 110.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHP-KYM | W | 106.3 | 0.99091 |  |  |  | 99 | 102.4 | 103.4 | 104.3 | 105.3 | 105.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HCP-WBE | S | 109.7 | 0.87719 |  |  |  | 11.4 | 20.9 | 29.2 | 35.6 | 43.4 | 49.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HCP-WBE | W | 134.9 | 0.86726 |  |  |  | 11.3 | 16.8 | 24.4 | 27.4 | 32 | 36.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-KYM1 | S | 79.4 | 0.90807 |  |  |  | 53.3 | 59 | 59.9 | 61.6 | 63.1 | 64.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-KYM1 | W | 90.3 | 0.89503 |  |  |  | 54.3 | 56.3 | 58.1 | 59.5 | 61 | 62 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-KYM2 | S | 79.4 | 0.90545 |  |  |  | 55 | 60.8 | 61.8 | 63.5 | 65.1 | 66.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-KYM2 | W | 90.3 | 0.89464 |  |  |  | 56 | 58.1 | 60 | 61.4 | 63 | 64 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
YSW-BMH | S | 36.6 | 0.89408 |  |  |  | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
YSW-BMH | W | 37.2 | 0.89408 |  |  |  | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-TNA1 | S | 109.7 | 0.92925 |  |  |  | 21.2 | 20.5 | 17.7 | 13.6 | 13.3 | 13.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-TNA1 | W | 134.9 | 0.92925 |  |  |  | 21.2 | 13.4 | 14.1 | 13.4 | 13.4 | 14.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WPD-TQY1 | S | 107 | 0.125 |  |  |  | 3.2 | 6.2 | 7.1 | 9.3 | 11.5 | 13.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WPD-TQY1 | W | 108.6 | 0.13636 |  |  |  | 2.2 | 2.6 | 3.4 | 4.5 | 5.3 | 6.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KYM-ECA2 | S | 45.7 | 0.95062 |  |  |  | 8.1 | 12.7 | 14.4 | 16.3 | 18.1 | 19.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KYM-ECA2 | W | 53.2 | 0.95062 |  |  |  | 8.1 | 9.4 | 11 | 12.5 | 13.6 | 14.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-AWT | S | 109.7 | 0.90769 |  |  |  | 13 | 26.8 | 34.6 | 39.8 | 47.6 | 53.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-AWT | W | 134.9 | 0.90769 |  |  |  | 13 | 20.7 | 28 | 31.7 | 36.8 | 41.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KYM-ECA1 | S | 45.7 | 0.95062 |  |  |  | 8.1 | 12.8 | 14.4 | 16.3 | 18.1 | 19.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KYM-ECA1 | W | 52.6 | 0.95062 |  |  |  | 8.1 | 9.4 | 11 | 12.5 | 13.7 | 14.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KGTS-GSF | S | 48.6 | 0.97849 |  |  |  | 55.8 | 57.8 | 58.3 | 59 | 59.7 | 60.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KGTS-GSF | W | 52.6 | 0.97909 |  |  |  | 57.4 | 59.7 | 60.4 | 61 | 61.6 | 62.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GLE-DDL1 | S | 74.3 | 0.85075 |  |  |  | 6.7 | 14.9 | 18.6 | 24.5 | 30.2 | 35.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GLE-DDL1 | W | 86.9 | 0.85455 |  |  |  | 5.5 | 7.8 | 11.4 | 15.1 | 18.2 | 21.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GLE-DDL2 | S | 74.3 | 0.85075 |  |  |  | 6.7 | 14.9 | 18.5 | 24.4 | 30.1 | 34.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GLE-DDL2 | W | 86.9 | 0.85455 |  |  |  | 5.5 | 7.8 | 11.4 | 15.1 | 18.1 | 21 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GCY-GL | S | 109.7 | 0.98969 |  |  |  | 9.7 | 9.8 | 8.7 | 6.5 | 4.3 | 4.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GCY-GL | W | 134.9 | 0.98969 |  |  |  | 9.7 | 9.6 | 8.6 | 6.5 | 4.9 | 3.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GSF-SHL | S | 76.6 | 0.97059 |  |  |  | 6.8 | 9.3 | 9.9 | 10.6 | 11.3 | 11.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GSF-SHL | W | 89.2 | 0.9881 |  |  |  | 8.4 | 11.4 | 12 | 12.7 | 13.3 | 13.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
YSF-HTH | S | 17.7 | 0.74 |  |  |  | 5 | 4.4 | 4.5 | 4.4 | 4.4 | 4.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
YSF-HTH | W | 35.4 | 0.75472 |  |  |  | 5.3 | 6.2 | 6.4 | 6.5 | 6.2 | 6.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KRT-PLD2/YWF | S | 29.7 | 0.82095 |  |  |  | 29.6 | 32.3 | 33.6 | 35.9 | 37.7 | 39.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KRT-PLD2/YWF | W | 29.7 | 0.80198 |  |  |  | 30.3 | 32.3 | 34.2 | 35.4 | 36.3 | 38 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CTN-CBW | S | 98.9 | 0.91163 |  |  |  | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CTN-CBW | W | 106.3 | 0.91628 |  |  |  | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-HCP | S | 109.7 | 0.85841 |  |  |  | 11.3 | 20.4 | 28.7 | 35 | 42.7 | 48.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-HCP | W | 134.9 | 0.86486 |  |  |  | 11.1 | 16.3 | 23.9 | 26.8 | 31.4 | 35.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KRT-WBL | S | 46.9 | 0.87543 |  |  |  | 28.9 | 32.1 | 33.2 | 34.8 | 36.1 | 37.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KRT-WBL | W | 47.4 | 0.84444 |  |  |  | 31.5 | 31.7 | 31.8 | 31.7 | 31.5 | 31.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-SCI | S | 90.8 | 0 |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-SCI | W | 116 | 0.73494 |  |  |  | 8.3 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SBY-GSB2 | S | 76.6 | 0.65854 |  |  |  | 4.1 | 14.6 | 22.2 | 28.1 | 33.8 | 38.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SBY-GSB2 | W | 89.2 | 0.63415 |  |  |  | 4.1 | 12 | 16.5 | 20.7 | 24.1 | 27.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-WNS | S | 91.4 | 0.84023 |  |  |  | 140.2 | 143 | 145.3 | 147.2 | 150.4 | 153.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-WNS | W | 91.4 | 0.84917 |  |  |  | 132.6 | 132.4 | 133.6 | 134.8 | 136.2 | 137.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-YSF | S | 84.6 | 0.95139 |  |  |  | 86.4 | 85.8 | 85.8 | 85.7 | 85.6 | 85.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-YSF | W | 106.3 | 0.9504 |  |  |  | 86.7 | 87.8 | 88 | 88.1 | 88.2 | 88.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-SU1 | S | 109.7 | 0.99248 |  |  |  | 13.3 | 8.8 | 7.4 | 5.2 | 2 | 2.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-SU1 | W | 133.7 | 0.99248 |  |  |  | 13.3 | 15.8 | 14 | 12.5 | 9.8 | 7.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-BCG | S | 109.7 | 0.90071 |  |  |  | 56.4 | 58.1 | 60.2 | 62.4 | 64.5 | 66.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-BCG | W | 134.9 | 0.91529 |  |  |  | 54.3 | 56.3 | 57.9 | 60.2 | 62.1 | 64.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WPD-TQY2 | S | 107 | 0.125 |  |  |  | 3.2 | 6.2 | 7.1 | 9.3 | 11.5 | 13.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WPD-TQY2 | W | 108.6 | 0.13636 |  |  |  | 2.2 | 2.7 | 3.5 | 4.5 | 5.3 | 6.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-LVN | S | 109.7 | 0.99115 |  |  |  | 11.3 | 14.3 | 16.3 | 14.9 | 14.5 | 17.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-LVN | W | 134.9 | 0.9902 |  |  |  | 10.2 | 19.2 | 18.7 | 17.1 | 16.3 | 16.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GB | S | 135.5 | 1 |  |  |  | 18 | 15 | 15.3 | 11.4 | 7.4 | 5.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GB | W | 142.3 | 1 |  |  |  | 18 | 18 | 16.8 | 12.9 | 9.6 | 7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
COB-CDN | S | 49.2 | 0.92219 |  |  |  | 34.7 | 34.2 | 33.4 | 32.8 | 31.8 | 30.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
COB-CDN | W | 57.2 | 0.90657 |  |  |  | 28.9 | 32.2 | 32.4 | 33.5 | 34.5 | 35.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KSF-RVL | S | 84.6 | 0.86957 |  |  |  | 4.6 | 7.4 | 6.6 | 4.9 | 5 | 5.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KSF-RVL | W | 106.3 | 0.89583 |  |  |  | 4.8 | 6.5 | 4.6 | 4.5 | 4.8 | 4.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BCG-WIN | S | 91.4 | 0.88536 |  |  |  | 97.7 | 95.7 | 94.5 | 93.7 | 92.9 | 92.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BCG-WIN | W | 91.4 | 0.89914 |  |  |  | 93.2 | 95.5 | 95.1 | 96 | 96.8 | 98.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CPL-AL | S | 91.4 | 0.55357 |  |  |  | 5.6 | 6.3 | 6.1 | 5.7 | 8.3 | 10.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CPL-AL | W | 91.4 | 0.60606 |  |  |  | 6.6 | 5.8 | 5.5 | 7.9 | 11 | 11.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SBY-GSB1 | S | 51.4 | 0.64286 |  |  |  | 4.2 | 14.7 | 22.2 | 28.1 | 33.7 | 38.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SBY-GSB1 | W | 69.7 | 0.61905 |  |  |  | 4.2 | 12.1 | 16.6 | 20.7 | 24.1 | 27.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-SRC | S | 109.7 | 0.99708 |  |  |  | 34.3 | 12.7 | 12.1 | 11.9 | 11.6 | 10.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-SRC | W | 134.9 | 0.99708 |  |  |  | 34.3 | 16.2 | 16.1 | 16.2 | 15.1 | 13.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-TYA | S | 88 | 0.60656 |  |  |  | 6.1 | 6.3 | 6.2 | 7 | 12.3 | 16 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-TYA | W | 112 | 0.28378 |  |  |  | 7.4 | 5.8 | 5.6 | 9.8 | 13.2 | 13.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BCG-WPD | S | 91.4 | 0.89455 |  |  |  | 55 | 53.7 | 53.3 | 52.3 | 51.3 | 50.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BCG-WPD | W | 91.4 | 0.90737 |  |  |  | 52.9 | 55.5 | 54.8 | 54.7 | 54.7 | 55 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BATS-YSW/BGL | S | 36.6 | 0.83389 |  |  |  | 30.1 | 30.2 | 30.1 | 30.2 | 30.3 | 30.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BATS-YSW/BGL | W | 37.1 | 0.82566 |  |  |  | 30.4 | 30.1 | 30.1 | 30.1 | 30.1 | 30.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAS1 | S | 83.5 | 1 |  |  |  | 6.7 | 7.3 | 13.3 | 16.2 | 17.2 | 21 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAS1 | W | 102.9 | 1 |  |  |  | 6.7 | 4.1 | 10.1 | 7.7 | 13.2 | 16.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-HKT | S | 135.5 | 0.89922 |  |  |  | 12.9 | 26.5 | 28.4 | 26.1 | 48.8 | 65.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-HKT | W | 142.3 | 0.89922 |  |  |  | 12.9 | 18.9 | 15.3 | 37.7 | 57 | 78.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SSE1 | S | 89.7 | 1 |  |  |  | 12.6 | 9.5 | 8.3 | 5.5 | 2.6 | 1.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SSE1 | W | 94.3 | 1 |  |  |  | 12.6 | 15 | 12.4 | 9.8 | 7.5 | 5.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-NSF | S | 98.3 | 0.83962 |  |  |  | 159 | 161.5 | 163.7 | 165.7 | 169 | 171.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-NSF | W | 114.3 | 0.84808 |  |  |  | 151.4 | 151.1 | 152 | 153.5 | 154.6 | 155.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-KWF | S | 44 | 0.71505 |  |  |  | 37.2 | 38.4 | 38.7 | 39.2 | 39.7 | 40.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-KWF | W | 43.4 | 0.71351 |  |  |  | 37 | 38.2 | 38.4 | 38.7 | 39 | 39.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SA2 | S | 108 | 0.5 |  |  |  | 6 | 9.4 | 13.6 | 20.1 | 27.2 | 33.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SA2 | W | 122.3 | 0.5 |  |  |  | 6 | 5.8 | 9.7 | 15 | 20.2 | 25.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
NRB-HTN | S | 52.6 | 0.99194 |  |  |  | 62 | 62 | 62 | 62 | 62 | 62 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
NRB-HTN | W | 53.2 | 0.99194 |  |  |  | 62 | 62 | 62 | 62 | 62 | 62 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GSB-WND2 | S | 46.3 | 0.68421 |  |  |  | 1.9 | 6.7 | 11 | 13.2 | 15.3 | 17 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GSB-WND2 | W | 49.7 | 0.68421 |  |  |  | 1.9 | 6.5 | 8.3 | 9.8 | 11 | 12.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KGTS-CHA | S | 31.4 | 1 |  |  |  | 0.6 | 36.9 | 37.5 | 38.3 | 39.3 | 40.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KGTS-CHA | W | 43.4 | 1 |  |  |  | 0.6 | 28.9 | 29.5 | 30.3 | 31.1 | 31.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GSB-WND1 | S | 109.7 | 0.65 |  |  |  | 2 | 6.7 | 11.1 | 13.3 | 15.4 | 17.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GSB-WND1 | W | 114.3 | 0.65 |  |  |  | 2 | 6.6 | 8.3 | 9.8 | 11.1 | 12.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SSE2 | S | 89.4 | 1 |  |  |  | 12.6 | 9.6 | 8.3 | 5.5 | 2.6 | 1.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SSE2 | W | 100.6 | 1 |  |  |  | 12.6 | 15 | 12.4 | 9.8 | 7.5 | 5.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF1 | S | 87.5 | 1 |  |  |  | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF1 | W | 87.5 | 1 |  |  |  | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MDA-BNG | S | 104 | 0.45833 |  |  |  | 2.4 | 2.6 | 2.8 | 3.2 | 3.6 | 3.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MDA-BNG | W | 114.3 | 0.65 |  |  |  | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GLE2 | S | 109.7 | 0.48387 |  |  |  | 6.2 | 14.6 | 20.6 | 28.5 | 36.2 | 42.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GLE2 | W | 133.7 | 0.070175 |  |  |  | 5.7 | 7.4 | 11.7 | 17.1 | 21.7 | 26.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GLE1 | S | 109.7 | 0.4918 |  |  |  | 6.1 | 14.7 | 20.7 | 28.6 | 36.4 | 43 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GLE1 | W | 133.7 | 0.071429 |  |  |  | 5.6 | 7.3 | 11.7 | 17.1 | 21.8 | 26.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MGW-CLC | S | 74.3 | 0.99398 |  |  |  | 66.4 | 66.4 | 66.4 | 66.4 | 66.3 | 66.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MGW-CLC | W | 86.9 | 0.9955 |  |  |  | 66.6 | 67.2 | 67.7 | 68.2 | 68.6 | 69 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAS2/BGF | S | 93.2 | 0.98507 |  |  |  | 6.7 | 7.2 | 13.2 | 16.1 | 17.1 | 20.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAS2/BGF | W | 94.9 | 0.98507 |  |  |  | 6.7 | 4.1 | 10.1 | 7.7 | 13.2 | 16.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
STN-MNA | S | 48.6 | 0.4375 |  |  |  | 4.8 | 5.9 | 5.6 | 7.4 | 9.3 | 11.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
STN-MNA | W | 52.6 | 0.43182 |  |  |  | 4.4 | 4.2 | 4.9 | 5.9 | 7 | 8.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-KRT2 | S | 97.2 | 0.89958 |  |  |  | 23.9 | 26.3 | 27.7 | 29.6 | 31.2 | 32.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-KRT2 | W | 116 | 0.90175 |  |  |  | 28.5 | 28.4 | 28.8 | 28.6 | 28.5 | 28.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-KRT1 | S | 44 | 0.63636 |  |  |  | 18.7 | 20.6 | 21.6 | 23.1 | 24.4 | 25.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-KRT1 | W | 44.6 | 0.64574 |  |  |  | 22.3 | 22.3 | 22.5 | 22.4 | 22.3 | 22.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-WPD | S | 108 | 0.90231 |  |  |  | 56.3 | 58.1 | 60.2 | 62.5 | 64.8 | 66.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-WPD | W | 135.5 | 0.91682 |  |  |  | 54.1 | 56 | 57.9 | 60.2 | 62.2 | 64.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BGO-EHK | S | 48.6 | 0.95455 |  |  |  | 4.4 | 2 | 3.5 | 6.9 | 10.3 | 13 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BGO-EHK | W | 49.2 | 0.95455 |  |  |  | 4.4 | 2.9 | 3.1 | 5.3 | 7.2 | 9.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WNS-NKA | S | 91.4 | 0.8392 |  |  |  | 119.4 | 120.4 | 121.2 | 122.1 | 122.9 | 124.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WNS-NKA | W | 91.4 | 0.84007 |  |  |  | 116.3 | 115.4 | 115.4 | 115.2 | 115.8 | 116.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-STN | S | 91.4 | 0.41379 |  |  |  | 8.7 | 10.4 | 10.3 | 13.1 | 16.8 | 20.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-STN | W | 91.4 | 0.41558 |  |  |  | 7.7 | 8.1 | 8.7 | 10.2 | 11.9 | 13.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-SU2 | S | 109.7 | 0.99248 |  |  |  | 13.3 | 8.8 | 7.4 | 5.2 | 2 | 2.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-SU2 | W | 133.7 | 0.99248 |  |  |  | 13.3 | 15.8 | 14 | 12.5 | 9.8 | 7.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RVL-BSP | S | 84.6 | 0.76923 |  |  |  | 5.2 | 8 | 7.3 | 6.9 | 5.7 | 6.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RVL-BSP | W | 106.3 | 0.76786 |  |  |  | 5.6 | 7.4 | 6.2 | 6.1 | 6.3 | 6.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WIN-MGW | S | 98.3 | 0.97046 |  |  |  | 94.8 | 93.9 | 93.8 | 93.9 | 94.1 | 94.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WIN-MGW | W | 99.5 | 0.9587 |  |  |  | 92 | 93.6 | 92.8 | 93.3 | 93.7 | 94.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-MNA | S | 88 | 0.4186 |  |  |  | 8.6 | 10.4 | 10.3 | 13.1 | 16.8 | 20.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-MNA | W | 114.4 | 0.42105 |  |  |  | 7.6 | 8 | 8.7 | 10.1 | 11.9 | 13.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-SCI | S | 97.2 | 0 |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-SCI | W | 125.7 | 0 |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-MLN2 | S | 109.7 | 0.87368 |  |  |  | 9.5 | 26.6 | 27.2 | 30.8 | 33.7 | 30 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-MLN2 | W | 134.9 | 0.87368 |  |  |  | 9.5 | 11.6 | 14.2 | 15.7 | 9.3 | 10.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CDN-CLC | S | 74.3 | 0.88341 |  |  |  | 66.9 | 66.9 | 66.7 | 66.7 | 66.6 | 66.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CDN-CLC | W | 86.9 | 0.88551 |  |  |  | 55.9 | 60.7 | 59.7 | 62.1 | 63.7 | 65.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-COB | S | 109.7 | 0.95208 |  |  |  | 31.3 | 29.2 | 28.4 | 27.7 | 26.7 | 25.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-COB | W | 116 | 0.92884 |  |  |  | 26.7 | 29.2 | 29.3 | 30.5 | 31.5 | 32.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF3 | S | 87.5 | 1 |  |  |  | 1.7 | 1.7 | 1.7 | 1.7 | 1.8 | 1.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF3 | W | 87.5 | 1 |  |  |  | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BSP-BBD | S | 65.2 | 0.071429 |  |  |  | 1.4 | 5.6 | 5.5 | 5.5 | 5.6 | 5.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BSP-BBD | W | 67.4 | 0.071429 |  |  |  | 1.4 | 3.8 | 3.8 | 3.8 | 3.9 | 3.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-LVN | S | 109.7 | 0.83962 |  |  |  | 10.6 | 7.9 | 9.6 | 10.5 | 13.4 | 16.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-LVN | W | 122.3 | 0.82787 |  |  |  | 12.2 | 11.4 | 11.8 | 13 | 14.3 | 14.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-FNS | S | 88 | 0.99708 |  |  |  | 34.3 | 12.7 | 12.1 | 11.9 | 11.6 | 10 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-FNS | W | 112 | 0.99708 |  |  |  | 34.3 | 16.2 | 16.1 | 16.2 | 15.1 | 13.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-MLN1 | S | 109.7 | 0.87368 |  |  |  | 9.5 | 26.6 | 27.2 | 30.7 | 33.6 | 30 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-MLN1 | W | 134.9 | 0.87368 |  |  |  | 9.5 | 11.6 | 14.2 | 15.7 | 9.3 | 10.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-TRG2 | S | 91.5 | 0.54023 |  |  |  | 17.4 | 16.2 | 18.6 | 21.8 | 24.8 | 27.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-TRG2 | W | 91.5 | 0.76585 |  |  |  | 20.5 | 20.4 | 20.6 | 20.5 | 20.5 | 20.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-TRG1 | S | 91.5 | 0.54335 |  |  |  | 17.3 | 16.2 | 18.6 | 21.8 | 24.8 | 27.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-TRG1 | W | 91.5 | 0.76585 |  |  |  | 20.5 | 20.4 | 20.6 | 20.5 | 20.5 | 20.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-MBN | S | 97.2 | 0.55556 |  |  |  | 2.7 | 3.3 | 3.9 | 5.1 | 6.2 | 7.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-MBN | W | 114.3 | 0.4 |  |  |  | 2 | 1.3 | 1.6 | 2.1 | 2.7 | 3.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-KSF | S | 84.6 | 0.93361 |  |  |  | 96.4 | 99.4 | 98.5 | 96.6 | 96.8 | 97 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-KSF | W | 106.3 | 0.93368 |  |  |  | 96.5 | 98.3 | 96.3 | 96.2 | 96.4 | 96.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-BMH | S | 32.6 | 0.81379 |  |  |  | 29 | 29.1 | 29.2 | 29.3 | 29.3 | 29.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-BMH | W | 37.7 | 0.79054 |  |  |  | 29.6 | 29.2 | 28.4 | 27.6 | 26.8 | 26.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
AC-CPL | S | 102.9 | 0.53571 |  |  |  | 5.6 | 12.3 | 12.9 | 13.8 | 15.1 | 15.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
AC-CPL | W | 108 | 0.2766 |  |  |  | 4.7 | 12.5 | 13 | 14.1 | 14.7 | 14.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FNS-SRC | S | 109.7 | 0.99346 |  |  |  | 30.6 | 10.9 | 10.7 | 10.7 | 10.8 | 10.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FNS-SRC | W | 125.7 | 0.99349 |  |  |  | 30.7 | 11.9 | 11.8 | 11.8 | 11.9 | 11.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WETS-BSP | S | 84.6 | 0.93668 |  |  |  | 91.6 | 88.5 | 87.7 | 86.2 | 85.9 | 86.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WETS-BSP | W | 106.3 | 0.94396 |  |  |  | 91 | 93.3 | 91.4 | 91.4 | 91.6 | 91.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -

## ZSS Aug Sum
Zone Substation | Season | Station N Export Rating (MVA) | Station N-1 Export Rating (MVA) | Station Nameplate Rating (MVA) | Station Power Factor at Minimum Demand | Embedded Generation Capacity (MVA) | Load Transfer Capability (MVA) | Generation Headroom (MVA) | Hours load is > 95% of Minimum Demand (Hrs) | Actual Minimum Demand (MVA) | 50% POE |  |  |  |  | % 50% POE load below N-1 Export Rating | 50% POE
[11 empty] | Forecast Minimum Demand (MVA) | [5 empty] | Energy at Risk (MWh) |  |  |  |  | Expected Energy at Risk (MWh) |  |  |  |  | Hours at Risk (Hrs)
[5 empty] | 2024 | 2024 | 2025 | 2024 | 2024 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029
AC | S | -40 | -20 | 40 | 0.23 | 0.481 | 0 | 19.519 | 0.25 | 0.4 | -1.27 | -1.26 | -1.27 | -1.28 | -1.29 | -
AC | W | -40 | -20 | 40 | 0.23 | 0.481 | 0 | 19.519 | 0.25 | 0.5 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | -
AL | S | -30 | 0 | 30 | 0.82 | 12.6295 | 0 | 0 | 0 | -0.91 | -0.3 | -0.78 | -1.68 | -2.64 | -3.44 | 100%
AL | W | -30 | 0 | 30 | 0.82 | 12.6295 | 0 | 0 | 0 | 2.63 | 2.23 | 1.48 | 0.79 | 0.3 | -0.62 | -
ART | S | -20 | -10 | 20 | 0.89 | 14.1862 | 2.2863 | 0 | 3.5 | -6.09 | -6.31 | -7.22 | -8.45 | -9.81 | -10.99 | -
ART | W | -20 | -10 | 20 | 0.89 | 14.1862 | 2.2863 | 0 | 3.5 | -1.82 | -5.18 | -6.09 | -7.14 | -8.07 | -8.95 | -
BAN | S | -120 | -80 | 120 | 0.89 | 44.3748 | 8.3831 | 35.6252 | 0 | -5.97 | -1.89 | -1.55 | -4.62 | -10.14 | -14.64 | -
BAN | W | -120 | -80 | 120 | 0.89 | 44.3748 | 8.3831 | 35.6252 | 0 | 12.96 | 12.61 | 9.09 | 3.56 | -1.43 | -4.27 | -
BAS | S | -99 | -66 | 99 | 1 | 54.4501 | 9.7168 | 11.5499 | 0.68 | -11.39 | -7.29 | -13.35 | -16.32 | -17.32 | -21.21 | -
BAS | W | -99 | -66 | 99 | 1 | 54.4501 | 9.7168 | 11.5499 | 0.68 | 3.87 | -4.03 | -10.12 | -7.67 | -13.28 | -16.58 | -
BBD | S | -66 | -33 | 66 | 0.07 | 1.0402 | 0 | 31.9598 | 2.15 | -1.78 | -5.5 | -5.46 | -5.47 | -5.5 | -5.52 | -
BBD | W | -66 | -33 | 66 | 0.07 | 1.0402 | 0 | 31.9598 | 2.15 | -0.35 | -3.76 | -3.76 | -3.78 | -3.81 | -3.8 | -
BGO | S | -66 | -33 | 66 | 0.27 | 17.7292 | 13.1463 | 15.2708 | 0 | 0.87 | 1.83 | -2.95 | -5.51 | -8.32 | -10.74 | -
BGO | W | -66 | -33 | 66 | 0.27 | 17.7292 | 13.1463 | 15.2708 | 0 | 4.44 | -1.83 | -3.13 | -5.28 | -7.23 | -9.15 | -
BMH | S | -27 | -13.5 | 26 | 0.93 | 14.8598 | 3.0484 | 0 | 0.23 | -3.79 | -4.48 | -5.88 | -8.43 | -10.96 | -13.05 | -
BMH | W | -27 | -13.5 | 26 | 0.93 | 14.8598 | 3.0484 | 0 | 0.23 | 1.64 | -2.42 | -3.82 | -5.68 | -7.36 | -9.02 | -
CDN | S | -20 | -10 | 20 | 0.81 | 5.6786 | 0 | 4.3214 | 0.8 | -2.87 | -2.5 | -3.21 | -4.05 | -4.88 | -5.61 | -
CDN | W | -20 | -10 | 20 | 0.81 | 5.6786 | 0 | 4.3214 | 0.8 | -1.42 | -1.78 | -2.28 | -2.82 | -3.32 | -3.8 | -
CHA | S | -27 | -13.5 | 26 | 0.97 | 8.1803 | 0 | 5.3197 | 5.75 | -27.12 | -39.21 | -39.82 | -40.7 | -41.79 | -42.6 | 190.4%
CHA | W | -27 | -13.5 | 26 | 0.97 | 8.1803 | 0 | 5.3197 | 5.75 | -0.7 | -30.51 | -31.19 | -32.02 | -32.92 | -33.41 | 126%
CHM | S | -33 | 0 | 33 | 0.34 | 1.3729 | 0 | 0 | 0.83 | -0.56 | -0.69 | -0.84 | -1.06 | -1.28 | -1.46 | 100%
CHM | W | -33 | 0 | 33 | 0.34 | 1.3729 | 0 | 0 | 0.83 | 0.21 | -0.64 | -0.79 | -0.96 | -1.12 | -1.27 | 100%
CLC | S | -79 | -46 | 79 | 0.99 | 12.7479 | 0 | 33.2521 | 0 | 5.71 | 6.79 | 6.09 | 6.58 | 4.58 | 2.88 | -
CLC | W | -79 | -46 | 79 | 0.99 | 12.7479 | 0 | 33.2521 | 0 | 11.16 | 6.66 | 8.31 | 6.6 | 5.17 | 3.74 | -
CME | S | -40.5 | -27 | 39 | 0.97 | 18.4119 | 0 | 8.5881 | 1.96 | -13.55 | -14.25 | -15.91 | -17.69 | -19.35 | -20.55 | -
CME | W | -40.5 | -27 | 39 | 0.97 | 18.4119 | 0 | 8.5881 | 1.96 | -11.52 | -12.24 | -13.89 | -15.31 | -16.49 | -17.52 | -
CMN | S | -66 | -33 | 66 | 0.97 | 29.0396 | 0 | 3.9604 | 0.64 | -4.65 | -12.11 | -11.33 | -14.34 | -17.21 | -19.67 | -
CMN | W | -66 | -33 | 66 | 0.97 | 29.0396 | 0 | 3.9604 | 0.64 | -0.93 | -6.09 | -7.57 | -10.03 | -12.11 | -13.99 | -
COB | S | -26 | -10 | 31 | 0.33 | 1.1122 | 2.1339 | 8.8878 | 0.97 | -5.99 | -6.23 | -6.22 | -6.22 | -6.22 | -6.22 | -
COB | W | -26 | -10 | 31 | 0.33 | 1.1122 | 2.1339 | 8.8878 | 0.97 | -5.68 | -6.27 | -6.26 | -6.25 | -6.25 | -6.25 | -
CRO | S | -60 | -27 | 60 | 0.86 | 5.4569 | 11.0124 | 21.5431 | 0 | 3.92 | 2.94 | 2.98 | 2.95 | 2.94 | 2.96 | -
CRO | W | -60 | -27 | 60 | 0.86 | 5.4569 | 11.0124 | 21.5431 | 0 | 6.79 | 3.49 | 3.44 | 3.41 | 3.36 | 3.28 | -
CTN | S | -39.5 | -26 | 41 | 0.88 | 17.2207 | 0 | 8.7793 | 4.57 | -7.36 | -6.36 | -7.76 | -9.36 | -10.93 | -12.23 | -
CTN | W | -39.5 | -26 | 41 | 0.88 | 17.2207 | 0 | 8.7793 | 4.57 | -5.21 | -6.51 | -7.79 | -9.09 | -10.22 | -11.32 | -
DDL | S | -66 | -33 | 66 | 0.99 | 40.3392 | 4.5726 | 0 | 0.83 | -14.89 | -16.94 | -21.15 | -27.89 | -34.38 | -39.83 | -
DDL | W | -66 | -33 | 66 | 0.99 | 40.3392 | 4.5726 | 0 | 0.83 | -7.4 | -10.6 | -15.73 | -20.98 | -25.25 | -29.27 | -
DLF | S | -66 | -33 | 66 | 0.96 | 0.34125 | 0 | 32.6587 | 0 | 4.14 | 3.88 | 4.07 | 4.19 | 4.33 | 4.45 | -
DLF | W | -66 | -33 | 66 | 0.96 | 0.34125 | 0 | 32.6587 | 0 | 4.63 | 4.57 | 4.79 | 4.95 | 5.12 | 5.28 | -
ECA | S | -40.5 | -27 | 39 | 0.97 | 19.879 | 4.7631 | 7.121 | 1.38 | -12.22 | -13.17 | -14.9 | -16.95 | -18.97 | -20.65 | -
ECA | W | -40.5 | -27 | 39 | 0.97 | 19.879 | 4.7631 | 7.121 | 1.38 | -9.35 | -9.67 | -11.31 | -12.86 | -14.12 | -15.21 | -
EHK | S | -54 | -27 | 54 | 0.85 | 23.4658 | 20.9578 | 3.5342 | 0 | -9.19 | -2.11 | -3.57 | -6.89 | -10.33 | -13.08 | -
EHK | W | -54 | -27 | 54 | 0.85 | 23.4658 | 20.9578 | 3.5342 | 0 | -3.74 | 2.96 | -2.01 | -3.77 | -5.94 | -7.96 | -
FNS | S | -99 | -66 | 99 | 0.35 | 15.1917 | 0 | 50.8083 | 0 | 0.47 | 1.97 | 1.75 | 1.69 | -1.68 | -2.54 | -
FNS | W | -99 | -66 | 99 | 0.35 | 15.1917 | 0 | 50.8083 | 0 | 4.05 | 4.3 | 4.3 | 4.39 | 3.22 | 2.04 | -
GB | S | -37.5 | -25 | 36 | 0.92 | 1.9222 | 0 | 23.0778 | 0 | 2.68 | 2.51 | 2.44 | 2.37 | 2.3 | 2.25 | -
GB | W | -37.5 | -25 | 36 | 0.92 | 1.9222 | 0 | 23.0778 | 0 | 3.61 | 2.74 | 2.69 | 2.65 | 2.6 | 2.54 | -
GCY | S | -66 | -33 | 66 | 1 | 11.3272 | 16.3852 | 21.6728 | 0 | 9.62 | 9.81 | 8.74 | 6.51 | 4.34 | 2.91 | -
GCY | W | -66 | -33 | 66 | 1 | 11.3272 | 16.3852 | 21.6728 | 0 | 9.36 | 9.65 | 8.32 | 6.5 | 4.95 | 3.64 | -
GHP | S | -66 | -33 | 66 | 0.91 | 18.9423 | 0 | 14.0577 | 0.59 | -2.17 | -2.85 | -8.07 | -10.35 | -12.46 | -14.13 | -
GHP | W | -66 | -33 | 66 | 0.91 | 18.9423 | 0 | 14.0577 | 0.59 | 1.79 | -5.01 | -6.79 | -8.5 | -9.87 | -11.1 | -
GL | S | -80 | -40 | 80 | 0.87 | 18.5026 | 14.4895 | 21.4974 | 0 | 2.24 | 3.45 | 4.42 | 3.17 | -2.87 | -4.26 | -
GL | W | -80 | -40 | 80 | 0.87 | 18.5026 | 14.4895 | 21.4974 | 0 | 4.91 | 5.83 | 5.92 | 4.03 | 2.89 | -2.84 | -
GLE | S | -79.5 | -46.5 | 79 | 0.49 | 23.7374 | 6.0968 | 22.7626 | 0 | -1.97 | 3.31 | -4.02 | -7.04 | -10.39 | -13.34 | -
GLE | W | -79.5 | -46.5 | 79 | 0.49 | 23.7374 | 6.0968 | 22.7626 | 0 | 4.96 | 4.71 | 3.16 | -3.17 | -4.3 | -5.79 | -
GSB | S | -66 | -33 | 66 | 0.9 | 18.1573 | 0 | 14.8427 | 1.33 | -5.35 | -7.42 | -10.38 | -14.22 | -17.89 | -20.77 | -
GSB | W | -66 | -33 | 66 | 0.9 | 18.1573 | 0 | 14.8427 | 1.33 | -1.56 | -5 | -7.97 | -10.79 | -13.16 | -15.35 | -
HSM | S | -40.5 | -27 | 39 | 0.84 | 20.6709 | 3.3914 | 6.3291 | 0.12 | -4.29 | -3.57 | -6.24 | -9.5 | -12.72 | -15.52 | -
HSM | W | -40.5 | -27 | 39 | 0.84 | 20.6709 | 3.3914 | 6.3291 | 0.12 | -2.92 | -3.19 | -5.84 | -8.58 | -10.95 | -13.3 | -
HTN | S | -39.5 | -26 | 39 | 0 | 10.833 | 0 | 15.167 | 0 |  | 1.82 | -1.16 | -3.28 | -5.7 | -7.87 | -
HTN | W | -39.5 | -26 | 39 | 0 | 10.833 | 0 | 15.167 | 0 | 2.93 | 2.19 | 0.96 | -2.15 | -3.82 | -5.59 | -
KRT | S | -40.5 | -27 | 39 | 0.88 | 8.9893 | 3.1627 | 18.0107 | 0 | 4.05 | 4.49 | 3.24 | 2.28 | 1.95 | -2.16 | -
KRT | W | -40.5 | -27 | 39 | 0.88 | 8.9893 | 3.1627 | 18.0107 | 0 | 6.34 | 5.44 | 4.48 | 3.6 | 2.93 | 2.35 | -
KYM | S | -40.5 | -27 | 39 | 0.4 | 12.9152 | 0 | 14.0848 | 0.61 | -4.3 | -3.07 | -4.2 | -5.49 | -6.69 | -7.66 | -
KYM | W | -40.5 | -27 | 39 | 0.4 | 12.9152 | 0 | 14.0848 | 0.61 | -5.09 | -2.87 | -3.66 | -4.5 | -5.25 | -5.97 | -
LV | S | -99 | -66 | 99 | 0.98 | 64.4246 | 15.7755 | 1.5754 | 0.8 | -26.66 | -27.32 | -35.39 | -40.75 | -48.61 | -54.51 | -
LV | W | -99 | -66 | 99 | 0.98 | 64.4246 | 15.7755 | 1.5754 | 0.8 | -13.07 | -21.08 | -28.6 | -32.36 | -37.69 | -42.26 | -
LVN | S | -99 | -66 | 129 | 0.92 | 13.257 | 4.9537 | 52.743 | 0 | 16.98 | 20.11 | 24.2 | 23.91 | 23.59 | 23.44 | -
LVN | W | -99 | -66 | 129 | 0.92 | 13.257 | 4.9537 | 52.743 | 0 | 20.61 | 29.13 | 29.1 | 28.98 | 28.9 | 28.72 | -
MBN | S | -59 | -27 | 59 | 0.95 | 19.9415 | 13.1463 | 7.0585 | 0.4 | -4.95 | -4.88 | -6.12 | -8.09 | -9.81 | -11.08 | -
MBN | W | -59 | -27 | 59 | 0.95 | 19.9415 | 13.1463 | 7.0585 | 0.4 | -3.65 | -3.83 | -5.45 | -6.86 | -7.91 | -8.87 | -
MDA | S | -66 | -33 | 66 | 0.75 | 20.3504 | 16.9568 | 12.6496 | 0 | -2.81 | 3.14 | 0.94 | -2.12 | -4.99 | -7.31 | -
MDA | W | -66 | -33 | 66 | 0.75 | 20.3504 | 16.9568 | 12.6496 | 0 | 1.38 | 3.42 | 0.8 | -1.69 | -3.72 | -5.59 | -
MLN | S | -99 | -66 | 99 | 0.98 | 55.7824 | 10.7075 | 10.2176 | 1.47 | -22.97 | -27.25 | -27.87 | -31.57 | -34.54 | -30.77 | -
MLN | W | -99 | -66 | 99 | 0.98 | 55.7824 | 10.7075 | 10.2176 | 1.47 | -9.49 | -11.67 | -14.42 | -15.94 | -9.26 | -10.64 | -
MNA | S | -66 | -33 | 66 | 0.62 | 18.4025 | 10.6694 | 14.5975 | 0 | -5.01 | -4.66 | -5.57 | -7.33 | -9.3 | -11.07 | -
MNA | W | -66 | -33 | 66 | 0.62 | 18.4025 | 10.6694 | 14.5975 | 0 | -4.76 | -4.58 | -5.26 | -6.44 | -7.56 | -8.79 | -
MRO | S | -27 | -13.5 | 26 | 0.87 | 13.5952 | 2.9341 | 0 | 0.79 | -6.99 | -5.16 | -7.02 | -9.11 | -11.13 | -12.89 | -
MRO | W | -27 | -13.5 | 26 | 0.87 | 13.5952 | 2.9341 | 0 | 0.79 | -5.37 | -3.62 | -5.45 | -7.24 | -8.74 | -10.08 | -
NHL | S | -20 | -10 | 20 | 0.88 | 4.3923 | 0 | 5.6077 | 8.55 | -6.74 | -8.74 | -9.05 | -9.71 | -10.42 | -11.02 | -
NHL | W | -20 | -10 | 20 | 0.88 | 4.3923 | 0 | 5.6077 | 8.55 | -5.46 | -8.98 | -9.24 | -9.62 | -10.06 | -10.43 | -
NKA | S | -39.5 | -26 | 39 | 0.96 | 23.1854 | 1.9815 | 2.8146 | 1.28 | -12.06 | -13.19 | -14.19 | -14.53 | -15.93 | -17.17 | -
NKA | W | -39.5 | -26 | 39 | 0.96 | 23.1854 | 1.9815 | 2.8146 | 1.28 | -9.11 | -12.39 | -12.41 | -13.41 | -14.45 | -15.37 | -
OYN | S | -27 | -13.5 | 26 | 0.78 | 3.5341 | 0 | 9.9659 | 0.89 | -0.94 | -1.79 | -2.34 | -3.03 | -3.72 | -4.3 | -
OYN | W | -27 | -13.5 | 26 | 0.78 | 3.5341 | 0 | 9.9659 | 0.89 | -1.07 | -1.57 | -2.03 | -2.57 | -3.1 | -3.62 | -
PLD | S | -32 | -16 | 32 | 0.63 | 14.1384 | 0 | 1.8616 | 0 | -1.8 | -0.79 | -2.23 | -4.05 | -5.94 | -7.6 | -
PLD | W | -32 | -16 | 32 | 0.63 | 14.1384 | 0 | 1.8616 | 0 | 1.83 | -0.59 | -2.09 | -3.67 | -5.03 | -6.38 | -
RVL | S | -19.5 | -13 | 37 | 0.94 | 5.4815 | 5.1061 | 7.5185 | 6.7 | -8.79 | -8.11 | -7.1 | -4.99 | -5.14 | -5.4 | -
RVL | W | -19.5 | -13 | 37 | 0.94 | 5.4815 | 5.1061 | 7.5185 | 6.7 | -4.96 | -6.72 | -4.55 | -4.5 | -4.72 | -4.89 | -
SA | S | -93 | -60 | 93 | 0.85 | 38.9298 | 3.5819 | 21.0702 | 0.72 | -8.24 | -9.48 | -13.74 | -20.4 | -27.59 | -33.84 | -
SA | W | -93 | -60 | 93 | 0.85 | 38.9298 | 3.5819 | 21.0702 | 0.72 | -5.11 | -5.86 | -9.84 | -15.23 | -20.43 | -25.56 | -
SHL | S | -40.5 | -27 | 39 | 1 | 44.9393 | 2.7817 | 0 | 3 | -18.05 | -16.88 | -17.98 | -19.35 | -20.76 | -21.84 | -
SHL | W | -40.5 | -27 | 39 | 1 | 44.9393 | 2.7817 | 0 | 3 | -12.17 | -16.53 | -17.57 | -18.59 | -19.55 | -20.35 | -
SHN | S | -66 | -33 | 66 | 0.99 | 18.8331 | 0 | 14.1669 | 0.79 | -7.97 | -3.62 | -5.03 | -6.22 | -7.28 | -8.03 | -
SHN | W | -66 | -33 | 66 | 0.99 | 18.8331 | 0 | 14.1669 | 0.79 | -7 | 1.59 | -4.57 | -5.64 | -6.44 | -7.09 | -
SHP | S | -66 | -33 | 66 | 0.92 | 13.4153 | 0 | 19.5847 | 4.01 | -28.05 | -31.18 | -31.98 | -33.17 | -34.46 | -35.55 | -
SHP | W | -66 | -33 | 66 | 0.92 | 13.4153 | 0 | 19.5847 | 4.01 | -26.63 | -28.28 | -29.14 | -30.3 | -31.17 | -31.82 | -
SSE | S | -99 | -66 | 99 | 1 | 20.3397 | 0 | 45.6603 | 0 | 5.02 | 9.53 | 8.32 | 5.45 | 2.55 | -1.53 | -
SSE | W | -99 | -66 | 99 | 1 | 20.3397 | 0 | 45.6603 | 0 | 12.57 | 14.96 | 12.41 | 9.81 | 7.54 | 5.32 | -
STL | S | -27 | -13.5 | 26 | 0.16 | 6.6493 | 4.0772 | 6.8507 | 0 | 4.55 | 4.74 | 4.17 | 3.41 | 2.95 | -2.97 | -
STL | W | -27 | -13.5 | 26 | 0.16 | 6.6493 | 4.0772 | 6.8507 | 0 | 4.9 | 5.1 | 4.54 | 4 | 3.54 | 3.15 | -
STN | S | -79 | -46 | 79 | 0.98 | 19.3432 | 0 | 26.6568 | 0.24 | -4.02 | -6.64 | -5.65 | -6.68 | -8.5 | -10.3 | -
STN | W | -79 | -46 | 79 | 0.98 | 19.3432 | 0 | 26.6568 | 0.24 | -4.45 | 5.6 | -5.6 | -5.98 | -6.81 | -7.82 | -
SU | S | -99 | -66 | 99 | 0.61 | 32.1099 | 9.7549 | 33.8901 | 0 | 3.25 | 8.78 | 7.4 | 5.21 | 1.85 | -2.5 | -
SU | W | -99 | -66 | 99 | 0.61 | 32.1099 | 9.7549 | 33.8901 | 0 | 13.25 | 15.8 | 13.96 | 12.45 | 9.81 | 7.36 | -
TNA | S | -99 | -66 | 99 | 0.86 | 65.2379 | 36.962 | 0.76208 | 0.62 | -28.89 | -21.23 | -18.3 | 13.98 | 13.73 | -13.71 | -
TNA | W | -99 | -66 | 99 | 0.86 | 65.2379 | 36.962 | 0.76208 | 0.62 | -21.66 | -13.81 | 14.5 | 13.78 | -13.83 | -14.57 | -
TQY | S | -66 | -33 | 66 | 0.9 | 26.9586 | 0 | 6.0414 | 1 | -6.37 | -8 | -9.24 | -12.14 | -15.1 | -17.44 | -
TQY | W | -66 | -33 | 66 | 0.9 | 26.9586 | 0 | 6.0414 | 1 | -4.03 | -4.93 | -6.55 | -8.66 | -10.28 | -12.01 | -
TRG | S | -46.5 | -13.5 | 46 | 0.98 | 14.8627 | 5.1442 | 0 | 1.6 | -5.33 | -5.01 | -6.06 | -7.19 | -8.26 | -9.13 | -
TRG | W | -46.5 | -13.5 | 46 | 0.98 | 14.8627 | 5.1442 | 0 | 1.6 | -6.01 | -4.21 | -5.03 | -5.85 | -6.56 | -7.22 | -
WBE | S | -99 | -66 | 99 | 0.89 | 65.516 | 8.7642 | 0.48401 | 0.47 | -21.49 | -21.32 | -29.84 | -36.38 | -44.27 | -50.11 | -
WBE | W | -99 | -66 | 99 | 0.89 | 65.516 | 8.7642 | 0.48401 | 0.47 | -11.59 | -17.4 | -25.27 | -28.34 | -33.16 | -37.73 | -
WBL | S | -79.5 | -46.5 | 79 | 0.98 | 13.8094 | 8.7642 | 32.6906 | 0 | 10.79 | 12.43 | 10.49 | 8.21 | 6.09 | 4.58 | -
WBL | W | -79.5 | -46.5 | 79 | 0.98 | 13.8094 | 8.7642 | 32.6906 | 0 | 12.09 | 12.87 | 11.07 | 9.19 | 7.55 | 5.98 | -
WIN | S | -20.5 | -7 | 20 | 0.43 | 16.3808 | 0 | 0 | 1.29 | -4.14 | -4.16 | -4.77 | -5.6 | -6.48 | -7.15 | -
WIN | W | -20.5 | -7 | 20 | 0.43 | 16.3808 | 0 | 0 | 1.29 | -3.92 | -4.01 | -4.47 | -5.02 | -5.57 | -6.14 | -
WMN | S | -46.5 | -13.5 | 46 | 0.42 | 1.7882 | 5.3347 | 11.7118 | 1.91 | -3.42 | -6.08 | -6.09 | -6.14 | -6.22 | -6.31 | -
WMN | W | -46.5 | -13.5 | 46 | 0.42 | 1.7882 | 5.3347 | 11.7118 | 1.91 | -1.41 | -3.99 | -4 | -4.03 | -4.07 | -4.08 | -
WND | S | -66 | -33 | 66 | 0.99 | 17.8521 | 1.1432 | 15.1479 | 2.63 | -6.69 | -7.63 | -12.8 | -15.4 | -17.89 | -19.95 | -
WND | W | -66 | -33 | 66 | 0.99 | 17.8521 | 1.1432 | 15.1479 | 2.63 | -2.01 | -7.31 | -9.4 | -11.13 | -12.62 | -14.02 | -
WPD | S | -79.5 | -46.5 | 81 | 0.96 | 24.2982 | 2.2863 | 22.2018 | 1.21 | -8.7 | -9.63 | -12.23 | -15.7 | -19.15 | -21.97 | -
WPD | W | -79.5 | -46.5 | 81 | 0.96 | 24.2982 | 2.2863 | 22.2018 | 1.21 | -3.67 | -5.94 | -8.24 | -10.7 | -12.73 | -14.53 | -