## Intro
CitiPower 2025 Distribution System Limitation Template
This Distribution Systems Limitations template is intended to make the Distribution Annual Planning Report (DAPR) limitation data more accessible and usable. Any information provided in this System Limitations template should be read in conjunction with the CitiPower 2025 DAPR. It should also be noted that the information in this template and the DAPR are based on high-level risk assessments produced for the DAPR. As such the numbers are indicative and subject to change. Therefore the information in this template should not be used to make investment decisions, and should only be used to assist in discussions with CitiPower. Finalised data will be produced in a detailed risk assessment conducted at the RIT-D or business case stage. However CitiPower invites interested parties to submit their proposals or to engage in joint planning with CitiPower as early as possible in order to defer or avoid the proposed augmentation. CitiPower also publishes its own Network Limitation maps in order to assist with the visualisation of the limitation data presented within this template and the DAPR. The data in this template will be updated annually and will be published along with the DAPR. We welcome any feedback to improve the content or usability of this template.

## Citipower Limitations
Owner | Asset Code | Asset Name | Project Name | Network Element | Voltage level (kV) | Rating | [5 empty] | Nameplate Rating | Location |  |  |  | Residential customers affected |  | Business Case | [7 empty] | Demand Reduction required to defer investment by 1 year |  | Emergency Generation |  | Load Transfer capability (MVA) | Power Factor | 10% POE | [14 empty] | 50% POE | [14 empty] | Weighted Expected Energy at Risk (MWh)
[6 empty] | Summer |  |  | Winter |  |  |  | Start |  | End |  |  |  | Constraint Primary Driver | Investment Description | Preferred network investment |  |  |  | Proposed Timing | Annual Deferral Value | [6 empty] | Forecast Maximum Demand (MVA) |  |  |  |  | Maximum Load at risk (MVA) (N-1) |  |  |  |  | Maximum Load at risk (MVA) (N-2) |  |  |  |  | Forecast Maximum Demand (MVA) |  |  |  |  | Maximum Load at risk (MVA) (N-1) |  |  |  |  | Maximum Load at risk (MVA) (N-2)
[6 empty] | N Rating (MVA) | N-1 Rating (MVA) | N-2 Rating (MVA) | N Rating (MVA) | N-1 Rating (MVA) | N-2 Rating (MVA) |  | Longitude | Latitude | Longitude | Latitude | Count | Percent |  |  | capital cost ($) | cost accuracy plus | cost accuracy minus | Operating cost ($) |  |  | (MW) | (MVA) | (MW) | (MVA) |  |  | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030
CitiPower | BK | Brunswick zone substation | Offload BK to WB | zss | 22/6.6 | 27.2 | 27.2 | - | 28.6 | 28.6 | - | 23 | 144.9724 | -37.7569 | 144.9724 | -37.7569 | 7341 | 89.21% | reliability capacity | Citipower's preferred network option is to offload BK to WB and convert 6.6kV feeders to 11kV. See the DAPR report for more details. | 35309095.9809 | 30% | 30% | 353090.9598 | 2027/28 | 1505357.7431 | NA | NA | 0 | 0 | 0 | 0.99448 | 18.68 | 19.17 | 23.3243 | 25.2353 | 27.3609 | 0 | 0 | 0 | 0 | 0.16093 | - | - | - | - | - | 17.24 | 17.68 | 22.3025 | 24.1297 | 26.1622 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | 0 | 0 | 0 | 0 | 0.32599
CitiPower | WB | West Brunswick zone substation | Offload BK to WB | zss | 66/6.6 | 52.7 | 31.8 | - | 52.7 | 31.8 | - | 52.7 | 144.9553 | -37.7684 | 144.9553 | -37.7684 | 16613 | 91.06% | reliability capacity | Citipower's preferred network option is to offload BK to WB and convert 6.6kV feeders to 11kV. See the DAPR report for more details. | 27384095.9809 | 30% | 30% | 273840.9598 | 2027/28 | 1167485.5948 | 33.4036 | 33.546 | 0 | 0 | 0 | 0.99575 | 42.1 | 44.17 | 68.02 | 70.29 | 72.36 | 10.3 | 12.37 | 36.22 | 38.49 | 40.56 | - | - | - | - | - | 40.54 | 42.53 | 64.2 | 66.3 | 68.33 | 8.74 | 10.73 | 32.4 | 34.5 | 36.53 | - | - | - | - | - | 0.069597 | 0.21382 | 0.46367 | 1.0257 | 2.1094
CitiPower | F | Fitzroy ZSS offload to CW | Offload F to CW | zss | 22/6.6 | 30.2 | 13.5 | - | 35.2 | 15.3 | - | 20 | 144.9896 | -37.7873 | 144.9896 | -37.7873 | 7872 | 91.25% | capacity | Citipower's preferred network option is to offload F to CW and convert 6.6kV feeders to 11kV. See the DAPR report for more details. | 26633702.8192 | 30% | 30% | 266337.0282 | 2026/27 | 1135493.5507 | NA | NA | 0 | 0 | NA | 0.99753 | 18.59 | 19.17 | 22.2876 | 24.151 | 26.1829 | 5.09 | 5.67 | 8.7876 | 10.651 | 12.6829 | - | - | - | - | - | 17.65 | 18.21 | 21.1906 | 22.9624 | 24.8942 | 4.15 | 4.71 | 7.6906 | 9.4624 | 11.3942 | - | - | - | - | - | 1.2134 | 3.1368 | 6.8428 | 12.9075 | 21.1578
CitiPower | CW | Collingwood zone substation | CW new 3rd transformer | zss | 66/11 | 65.3 | 34.4 | - | 73.4 | 38.2 | - | 54 | 144.9872 | -37.7981 | 144.9872 | -37.7981 | 7664 | 78.65% | capacity | Citipower's preferred network option is to establish a third transformer at CW. See the DAPR report for more details. | 9214921.6062 | 30% | 30% | 92149.2161 | 2030/31 | 392866.2914 | 18.1515 | 18.281 | 0 | 0 | 10.1 | 0.99292 | 29.52 | 51.93 | 53.19 | 54.62 | 55.95 | 0 | 17.53 | 18.79 | 20.22 | 21.55 | - | - | - | - | - | 27.48 | 47.16 | 48.46 | 49.93 | 51.28 | 0 | 12.76 | 14.06 | 15.53 | 16.88 | - | - | - | - | - | 1.2134 | 3.1368 | 6.8428 | 12.9075 | 21.1578
CitiPower | BQ | Bouveries/ Queens zone substation | Bouverie Queensberry supply area | zss | 66/11 | 132.3 | 64.9 | - | 147.3 | 72.3 | - | 110 | 144.9613 | -37.8052 | 144.9613 | -37.8052 | 17335 | 87.08% | capacity | Citipower's preferred network option is to establish a third transformer at BQ. See the DAPR report for more details. | 20034069.16 | 30% | 30% | 200340.6916 | 2027/28 | 854126.686 | 25.3504 | 25.637 | 0 | 0 | 6.5 | 0.98882 | 95.77 | 97.17 | 96.27 | 95.18 | 93.79 | 30.87 | 32.27 | 31.37 | 30.28 | 28.89 | - | - | - | - | - | 87.29 | 88.81 | 88.08 | 87 | 85.71 | 22.39 | 23.91 | 23.18 | 22.1 | 20.81 | - | - | - | - | - | 1.4831 | 1.8929 | 1.6546 | 137.5673 | 143.2341
CitiPower | VM | Victoria Market zone substation | Bouverie Queensberry supply area | zss | 66/11 | 90.96 | 57.88 | - | 110.1 | 70.22 | - | 84 | 144.9536 | -37.8085 | 144.9536 | -37.8085 | 7953 | 81.64% | capacity | Citipower's preferred network option is to establish a third transformer at BQ. See the DAPR report for more details. | 20034069.16 | 30% | 30% | 200340.6916 | 2027/28 | 854126.686 | 13.2877 | 13.438 | 0 | 0 | 8.9 | 0.98882 | 71.61 | 74.54 | 75.49 | 76.39 | 76.47 | 13.73 | 16.66 | 17.61 | 18.51 | 18.59 | - | - | - | - | - | 65.64 | 68.61 | 69.53 | 70.29 | 70.82 | 7.76 | 10.73 | 11.65 | 12.41 | 12.94 | - | - | - | - | - | 0.077433 | 0.11216 | 0.14589 | 0.17732 | 0.21665
CitiPower | E | Fishermans Bend zone substation | Fishermans Bend modernisation | zss | 66/6.6 | 10.9 | 0 | - | 12.1 | 0 | - | 13.5 | 144.9226 | -37.8243 | 144.9226 | -37.8243 | 0 | 0% | capacity | Citipower's preferred network option is to offload E to WG and convert 6.6kV feeders to 11kV. See the DAPR report for more details. | 4977723.2807 | 30% | 30% | 49777.2328 | 2028/29 | 212218.8087 | 2.565 | 2.565 | 0 | 0 | 0 | 1 | 2.77 | 3 | 3.19 | 3.37 | 3.54 | 2.77 | 3 | 3.19 | 3.37 | 3.54 | - | - | - | - | - | 1.81 | 1.97 | 2.1 | 2.22 | 2.33 | 1.81 | 1.97 | 2.1 | 2.22 | 2.33 | - | - | - | - | - | 74.1481 | 79.4845 | 84.5968 | 89.304 | 93.8325
CitiPower | JA | Little Bourke Street zone substation | J rebuild | zss | 66/11 | 203.5 | 127.8 | - | 202.7 | 127.4 | - | 165 | 144.9534 | -37.8157 | 144.9534 | -37.8157 | 6235 | 65.5% | CBD Security | Citipower's preferred network option is to rebuild J zone substation. See the DAPR report for more details. | 37738348 | 30% | 30% | 377383.48 | 2030/31 | 1608925.7682 | 27.028 | 27.028 | 0 | 0 | 70.3 | 0.99084 | 148.9 | 156.38 | 160.31 | 163.7 | 166.7 | 21.1 | 28.58 | 32.51 | 35.9 | 38.9 | - | - | - | - | - | 133.87 | 140.43 | 143.92 | 147.03 | 149.74 | 6.07 | 12.63 | 16.12 | 19.23 | 21.94 | - | - | - | - | - | 0.035706 | 0.39496 | 0.94339 | 1.8106 | 2.9344
CitiPower | JA | Little Bourke Street zone substation | New feeders from MG to JA | zss | 66/12 | 203.5 | 127.8 | - | 202.7 | 127.4 | - | 165 | 144.9534 | -37.8157 | 144.9534 | -37.8157 | 6235 | 65.5% | CBD Security | Citipower's preferred network option is to establish new feeders from MG zone substation to JA zone substation. See the DAPR report for more details. | 19022643 | 30% | 30% | 190226.43 | 2027/28 | 811005.8369 | 21.037 | 21.037 | 0 | 0 | 70.3 | 0.99084 | 148.9 | 156.38 | 160.31 | 163.7 | 166.7 | 21.1 | 28.58 | 32.51 | 35.9 | 38.9 | - | - | - | - | - | 133.87 | 140.43 | 143.92 | 147.03 | 149.74 | 6.07 | 12.63 | 16.12 | 19.23 | 21.94 | - | - | - | - | - | 0.035706 | 0.39496 | 0.94339 | 1.8106 | 2.9344
CitiPower | WA023 | Heffernan Lane feeder 23 | WA023 feeder | feeder | 11 | 2.9531 | 2.9531 | - | 2.9531 | 2.9531 | - | - | 144.968 | -37.8047 | 144.968 | -37.8047 | 559 | 76.89% | capacity | CitiPower's preferred network option is to uprate WA023. See the DAPR report for more details | 2231515 | 30% | 30% | 22315.15 | 2026/27 | 95137.7624 | 1.2843 | 1.2843 | 0 | 0 | - | 0.99998 | 4.2887 | 4.4301 | 4.413 | 4.3899 | 4.361 | 1.3356 | 1.4769 | 1.4599 | 1.4368 | 1.4079 | - | - | - | - | - | 4.0171 | 4.1549 | 4.1392 | 4.1176 | 4.0912 | 1.0639 | 1.2018 | 1.186 | 1.1644 | 1.1381 | - | - | - | - | - | 111.1111 | 127.3452 | 122.6487 | 115.1319 | 109.4246
CitiPower | SK001 | St Kilda feeder 1 | SK001 feeder | feeder | 11 | 5 | 5 | - | 5 | 5 | - | - | 144.9832 | -37.8648 | 144.9832 | -37.8648 | 1627 | 87.01% | capacity | CitiPower's preferred network option is to uprate SK001. See the DAPR report for more details | 950835 | 30% | 30% | 9508.35 | 2027/28 | 40537.6232 | 0.62232 | 0.62232 | 0 | 0 | - | 0.99144 | 5.3631 | 5.9179 | 5.9458 | 5.9219 | 5.8936 | 0.36308 | 0.91795 | 0.94576 | 0.92192 | 0.89362 | - | - | - | - | - | 4.8944 | 5.4543 | 5.4837 | 5.4408 | 5.5097 | 0 | 0.4543 | 0.48371 | 0.4408 | 0.50966 | - | - | - | - | - | 0.084457 | 0.3363 | 0.79667 | 1.5278 | 2.798
CitiPower | BQ017 | Bouveries/ Queens feeder 17 | BQ017 feeder | feeder | 11 | 10.5742 | 10.5742 | - | 10.5742 | 10.5742 | - | - | 144.9433 | -37.7926 | 144.9433 | -37.7926 | 4511 | 92.19% | capacity | Citipower's preferred network option is to construct a new feeder from BQ. See the DAPR report for more details. | 4451651 | 30% | 30% | 44516.51 | 2027/28 | 189790.3958 | 0.99764 | 0.99764 | 0 | 0 | - | 0.99958 | 13.5371 | 13.686 | 13.8996 | 14.0095 | 14.0467 | 2.963 | 3.1118 | 3.3255 | 3.4353 | 3.4726 | - | - | - | - | - | 8.8938 | 9.029 | 9.2153 | 9.3117 | 9.3834 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | 332.4071 | 455.3351 | 551.7453 | 634.6816 | 665.2169
CitiPower | WB011 | West Brunswick feeder 11 | WB011 feeder | feeder | 6.6 | 4.1 | 4.1 | - | 4.1 | 4.1 | - | - | 144.9447 | -37.7612 | 144.9447 | -37.7612 | 1641 | 96.42% | capacity | Citipower's preferred network option is to uprate feeder WB011. See the DAPR report for more details. | 288083 | 30% | 30% | 2880.83 | 2026/27 | 12282.047 | 0.81062 | 0.81062 | 0 | 0 | - | 0.99707 | 4.6865 | 5.1686 | 5.1899 | 5.2005 | 5.2439 | 0.58649 | 1.0686 | 1.0899 | 1.1005 | 1.1439 | - | - | - | - | - | 4.5675 | 4.8001 | 4.9161 | 5.0214 | 5.1229 | 0.46748 | 0.70006 | 0.81611 | 0.92145 | 1.0229 | - | - | - | - | - | 1.7366 | 4.1402 | 5.0501 | 5.9651 | 6.4135
CitiPower | AR | Armadale #2 Transformer Replacement | Armadale #2 Transformer Replacement | transformer | 66/11 | 56 | 28 | 0 | 56 | 28 | 0 | 30 | 145.0192 | -37.8555 | 145.0192 | -37.8555 | 12091 | 90.34% | asset condition | Citipower’s preferred network option is to replace the #2 transformer AR. See the DAPR report for more details. | 7111651.9396 | 30% | 30% | 71116.5194 | 2029 | 303196.1033 | 6.5 | 6.5641 | 0 | 0 | 5.8 | 0.99023 | 38.03 | 39.18 | 39.21 | 39.14 | 39.28 | 4.23 | 5.38 | 5.41 | 5.34 | 5.48 | 32.23 | 33.38 | 33.41 | 33.34 | 33.48 | 34.83 | 35.98 | 35.96 | 35.78 | 35.75 | 1.03 | 2.18 | 2.16 | 1.98 | 1.95 | 29.03 | 30.18 | 30.16 | 29.98 | 29.95 | 20.5622 | 22.3915 | 22.9968 | 23.4656 | 24.1423
CitiPower | NC | Northcote #1 Transformer Replacement | Northcote #1 Transformer Replacement | transformer | 66/11 | 70 | 35 | 0 | 70 | 35 | 0 | 30 | 145.0033 | -37.771 | 145.0033 | -37.771 | 17757 | 92.3% | asset condition | Citipower’s preferred network option is to replace the #1 transformer NC. See the DAPR report for more details. | 8410434.1047 | 30% | 30% | 84104.341 | 2027 | 358568.0049 | 7.3 | 7.3357 | 0 | 0 | 0 | 0.99514 | 37.27 | 38.04 | 38.73 | 39.24 | 39.77 | 2.27 | 3.04 | 3.73 | 4.24 | 4.77 | 37.27 | 38.04 | 38.73 | 39.24 | 39.77 | 34.07 | 34.8 | 35.38 | 35.93 | 36.36 | 0 | 0 | 0.38 | 0.93 | 1.36 | 34.07 | 34.8 | 35.38 | 35.93 | 36.36 | 20.6631 | 21.7556 | 22.8187 | 23.84 | 24.8624
CitiPower | B | Collingwood (B) 11kV Switchboard Replacement | Collingwood (B) 11kV Switchboard Replacement | switchboard | 11 | 68.6 | 34.3 | 0 | 68.6 | 34.3 | 0 | N/A | 144.9913 | -37.8068 | 144.9913 | -37.8068 | 5207 | 75.26% | asset condition | Citipower’s preferred network option is to replace the 11kV switchboard at B. See the DAPR report for more details. | 17534252.2411 | 30% | 30% | 175342.5224 | 2028 | 747550.2175 | N/A | N/A | 0 | 0 | 0 | 0.97516 | 40.24 | 41.08 | 41.68 | 42.1 | 42.23 | 5.94 | 6.78 | 7.38 | 7.8 | 7.93 | 40.24 | 41.08 | 41.68 | 42.1 | 42.23 | 36.13 | 36.98 | 37.52 | 37.9 | 38.03 | 1.83 | 2.68 | 3.22 | 3.6 | 3.73 | 36.13 | 36.98 | 37.52 | 37.9 | 38.03 | N/A | N/A | N/A | N/A | N/A
CitiPower | AR | Armadale 11kV Switchboard Replacement | Armadale 11kV Switchboard Replacement | switchboard | 11 | 56 | 28 | 0 | 56 | 28 | 0 | N/A | 145.0192 | -37.8555 | 145.0192 | -37.8555 | 12091 | 90.34% | asset condition | Citipower’s preferred network option is to replace the 11kV switchboard at AR. See the DAPR report for more details. | 8605270.7945 | 30% | 30% | 86052.7079 | 2027 | 366874.6158 | 5.4 | 5.4533 | 0 | 0 | 5.8 | 0.99023 | 38.03 | 39.18 | 39.21 | 39.14 | 39.28 | 4.23 | 5.38 | 5.41 | 5.34 | 5.48 | 32.23 | 33.38 | 33.41 | 33.34 | 33.48 | 34.83 | 35.98 | 35.96 | 35.78 | 35.75 | 1.03 | 2.18 | 2.16 | 1.98 | 1.95 | 29.03 | 30.18 | 30.16 | 29.98 | 29.95 | 7.8193 | 8.2784 | 8.2801 | 8.2328 | 8.2552
CitiPower | NC | Northcote 11kV Switchboard Replacement | Northcote 11kV Switchboard Replacement | switchboard | 11 | 70 | 35 | 0 | 70 | 35 | 0 | N/A | 145.0033 | -37.771 | 145.0033 | -37.771 | 17757 | 92.3% | asset condition | Citipower’s preferred network option is to replace the 11kV switchboard at NC. See the DAPR report for more details. | 8011488.3292 | 30% | 30% | 80114.8833 | 2029 | 341559.4666 | 7.1 | 7.1347 | 0 | 0 | 0 | 0.99514 | 37.27 | 38.04 | 38.73 | 39.24 | 39.77 | 2.27 | 3.04 | 3.73 | 4.24 | 4.77 | 37.27 | 38.04 | 38.73 | 39.24 | 39.77 | 34.07 | 34.8 | 35.38 | 35.93 | 36.36 | 0 | 0 | 0.38 | 0.93 | 1.36 | 34.07 | 34.8 | 35.38 | 35.93 | 36.36 | 12.5522 | 12.841 | 13.0925 | 13.3028 | 13.4983
CitiPower | R | Richmond 22kV Switchboard Retirement | Richmond 22kV Switchboard Retirement | switchboard | 22 | 49.9 | 33.2667 | 16.6333 | 49.9 | 32.9 | 16.6333 | N/A | 144.994 | -37.8325 | 144.994 | -37.8325 | 4710 | 72.55% | asset condition | Citipower’s preferred network option is to retire the 22kV switchboard at R. See the DAPR report for more details. | 2988080.3083 | 30% | 30% | 29880.8031 | 2026 | 127392.948 | N/A | N/A | 0 | 0 | 7.3 | 0.99346 | 47.09 | 56.71 | 57.6 | 57.37 | 56.85 | 6.5233 | 16.1433 | 17.0333 | 16.8033 | 16.2833 | 23.1567 | 32.7767 | 33.6667 | 33.4367 | 32.9167 | 43.92 | 50.78 | 51.3 | 50.86 | 50.16 | 3.3533 | 10.2133 | 10.7333 | 10.2933 | 9.5933 | 19.9867 | 26.8467 | 27.3667 | 26.9267 | 26.2267 | 1.1119 | 1.6279 | 1.6864 | 1.661 | 1.6136
CitiPower | RD | Riversdale 11kV Switchboard Replacement | Riversdale 11kV Switchboard Replacement | switchboard | 11 | 61 | 30.5 | 0 | 61 | 30.5 | 0 | N/A | 145.0869 | -37.8426 | 145.0869 | -37.8426 | 10918 | 92.25% | asset condition | Citipower’s preferred network option is to replace the 11kV switchboard at RD. See the DAPR report for more details. | 8014884.7805 | 30% | 30% | 80148.8478 | 2028 | 341704.2699 | 1.5 | 1.5199 | 0 | 0 | 8.4 | 0.98692 | 42.84 | 43.22 | 43.46 | 43.56 | 43.49 | 3.94 | 4.32 | 4.56 | 4.66 | 4.59 | 34.44 | 34.82 | 35.06 | 35.16 | 35.09 | 38.4 | 38.74 | 39.03 | 39.18 | 39.12 | 0 | 0 | 0.13 | 0.28 | 0.22 | 30 | 30.34 | 30.63 | 30.78 | 30.72 | 6.6196 | 6.7875 | 6.9105 | 6.9686 | 6.9384

## Sub-T Aug Sum
Sub transmission line | Season | Line N Import Rating (MVA) | Line Power Factor at Maximum Demand | Embedded Generation Capacity (MVA) | Load Transfer Capability (MVA) | Hours load is > 95% of Maximum Demand (Hrs) | Actual Maximum Demand (MVA) | 50% POE |  |  |  |  | 50% POE load above N Import Rating (%) | 50% POE load above N Import Rating (MVA) | 50% POE
[8 empty] | Forecast Maximum Demand (MVA) | [6 empty] | Energy at Risk (MWh) |  |  |  |  | Hours at Risk (Hrs)
|  |  | 2025 | 2025 | 2026 | 2025 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2026 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030
RTS-RP124 | S | 7.6 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-RP124 | W | 7.6 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF1 | S | 87.5 | 0.97107 | 0.34125 | - | - | 24.2 | 28.2 | 29 | 29.7 | 30.5 | 30.9 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF1 | W | 87.5 | 0.98077 | 0.34125 | - | - | 20.8 | 24.2 | 24.7 | 25.5 | 25.8 | 26.2 | - | - | - | - | - | - | - | - | - | - | - | -
VM-LQ3 | S | 76.6 | 0.88235 | 3.2968 | - | - | 39.1 | 52.7 | 57.5 | 58.2 | 60.5 | 60.2 | - | - | - | - | - | - | - | - | - | - | - | -
VM-LQ3 | W | 86.9 | 0.9697 | 3.2968 | - | - | 23.1 | 37.9 | 39.2 | 41 | 41.5 | 42.4 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-WG | S | 88 | 0.94126 | 25.3788 | - | - | 71.5 | 97.1 | 106.2 | 112.9 | 116.9 | 120.8 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-WG | W | 112 | 0.97043 | 25.3788 | - | - | 57.5 | 88.1 | 94.6 | 99.7 | 102.7 | 106 | - | - | - | - | - | - | - | - | - | - | - | -
VM-WA2 | S | 37.7 | 0.94444 | 3.238 | - | - | 19.8 | 24 | 25.7 | 25 | 25.1 | 25.2 | - | - | - | - | - | - | - | - | - | - | - | -
VM-WA2 | W | 40 | 0.992 | 3.238 | - | - | 12.5 | 16.6 | 16.9 | 16.7 | 17.1 | 17.2 | - | - | - | - | - | - | - | - | - | - | - | -
FB-WG | S | 89.7 | 0.97194 | 26.2954 | - | - | 39.2 | 59.9 | 64.6 | 68 | 69.5 | 70.7 | - | - | - | - | - | - | - | - | - | - | - | -
FB-WG | W | 94.3 | 0.97846 | 26.2954 | - | - | 32.5 | 51.2 | 54.6 | 56.8 | 57.9 | 59.1 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-FR3 | S | 82.3 | 0.98813 | 0.70444 | - | - | 33.7 | 40.5 | 42.6 | 42.7 | 42.4 | 42.1 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-FR3 | W | 87.4 | 1 | 0.70444 | - | - | 23.5 | 30.6 | 31.5 | 31.4 | 31.7 | 31.4 | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-HB | S | 117.2 | 0.909 | 0 | - | - | 97.8 | 118.9 | 119.5 | 120.4 | 120.6 | 120.2 | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-HB | W | 126.3 | 0.97406 | 0 | - | - | 77.1 | 96.3 | 99.6 | 103.4 | 107.8 | 111.5 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BQ3 | S | 139.7 | 0.96861 | 27.6844 | - | - | 92.4 | 102.3 | 105.8 | 105.2 | 105.4 | 105.4 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BQ3 | W | 149.2 | 0.98688 | 27.6844 | - | - | 76.2 | 88 | 88.6 | 88.9 | 89.3 | 89.3 | - | - | - | - | - | - | - | - | - | - | - | -
B-NR | S | 85.7 | 0.95 | 20.0224 | - | - | 62 | 66.9 | 69.3 | 89.4 | 91.4 | 92.2 | - | - | - | - | - | - | - | - | - | - | - | -
B-NR | W | 91.4 | 0.97436 | 20.0224 | - | - | 54.6 | 60 | 85.5 | 87.8 | 90.3 | 92.1 | - | - | - | - | - | - | - | - | - | - | - | -
B-CW | S | 85.7 | 0.94321 | 12.509 | 10.25 | 9.65 | 89.8 | 97.9 | 99.8 | 102.4 | 103.1 | 103.7 | 12.46% | 12.2 | 127.8077 | 145.2661 | 172.1785 | 197.782 | 227.1929 | 9.0495 | 11.0604 | 11.5632 | 11.8984 | 12.2432
B-CW | W | 91.4 | 0.97392 | 12.509 | - | - | 76.7 | 87.2 | 89.2 | 92 | 94.2 | 96.3 | - | - | - | - | - | - | - | - | - | - | - | -
BQ-WP3 | S | 84 | 0.97449 | 27.7553 | - | - | 39.2 | 45.4 | 47.4 | 46.3 | 45.7 | 45.2 | - | - | - | - | - | - | - | - | - | - | - | -
BQ-WP3 | W | 91.5 | 1 | 27.7553 | - | - | 26.9 | 34.7 | 34.7 | 34.3 | 34.2 | 33.8 | - | - | - | - | - | - | - | - | - | - | - | -
BQ-WP2 | S | 84 | 0.97449 | 27.7553 | - | - | 39.2 | 45.4 | 47.4 | 46.3 | 45.7 | 45.2 | - | - | - | - | - | - | - | - | - | - | - | -
BQ-WP2 | W | 91.5 | 1 | 27.7553 | - | - | 26.9 | 34.7 | 34.7 | 34.3 | 34.2 | 33.8 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-FR1 | S | 82.3 | 0.99107 | 0.70444 | - | - | 33.6 | 40.5 | 42.6 | 42.6 | 42.2 | 41.9 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-FR1 | W | 87.4 | 1 | 0.70444 | - | - | 23.5 | 30.5 | 31.5 | 31.4 | 31.7 | 31.4 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BK194 | S | 10.3 | 0.96703 | 4.4363 | - | - | 9.1 | 9.2 | 9.4 | 1.9 | 1.8 | 1.8 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BK194 | W | 10.3 | 0.94318 | 4.4363 | - | - | 8.8 | 9.2 | 9.6 | 1.8 | 1.8 | 1.8 | - | - | - | - | - | - | - | - | - | - | - | -
TK-BC | S | 91.5 | 0.97718 | 7.6426 | - | - | 70.1 | 87.3 | 93.1 | 95.8 | 95.6 | 95.5 | - | - | - | - | - | - | - | - | - | - | - | -
TK-BC | W | 91.5 | 0.98805 | 7.6426 | - | - | 58.6 | 73.4 | 79.8 | 82.8 | 86.9 | 89.5 | - | - | - | - | - | - | - | - | - | - | - | -
SB-SO | S | 109.7 | 0.97403 | 8.8701 | - | - | 38.5 | 54.1 | 60.3 | 60.8 | 61.1 | 61.3 | - | - | - | - | - | - | - | - | - | - | - | -
SB-SO | W | 121.7 | 0.99265 | 8.8701 | - | - | 27.2 | 43.4 | 45.9 | 46.2 | 46.2 | 46.9 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BK187 | S | 10.3 | 0.92784 | 4.4363 | - | - | 9.7 | 9.7 | 9.8 | 1.5 | 1.3 | 1.8 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BK187 | W | 10.3 | 0.94318 | 4.4363 | - | - | 8.8 | 9.8 | 10 | 1.6 | 1.3 | 1.6 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-FR2 | S | 82.3 | 0.98824 | 0.70444 | - | - | 34 | 40.7 | 42.8 | 43 | 42.6 | 42.3 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-FR2 | W | 87.4 | 1 | 0.70444 | - | - | 23.6 | 30.8 | 31.7 | 31.5 | 31.8 | 31.5 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-SB | S | 117.7 | 0.95961 | 7.9439 | - | - | 71.8 | 92.2 | 99.4 | 101.1 | 102.3 | 102.9 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-SB | W | 130.3 | 0.988 | 7.9439 | - | - | 50 | 73 | 76.6 | 78.3 | 79 | 80.6 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-RP123 | S | 11.4 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-RP123 | W | 11.4 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
FR-WP3 | S | 81.7 | 0.98519 | 0.77534 | - | - | 13.5 | 15.6 | 15.8 | 15.8 | 15.9 | 15.9 | - | - | - | - | - | - | - | - | - | - | - | -
FR-WP3 | W | 88 | 1 | 0.77534 | - | - | 9.4 | 11.3 | 11.5 | 11.7 | 11.9 | 11.9 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BQ1 | S | 159.9 | 0.96834 | 27.6844 | - | - | 97.9 | 108.5 | 112.2 | 111.5 | 111.7 | 111.7 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BQ1 | W | 170.6 | 0.98637 | 27.6844 | - | - | 80.7 | 93.2 | 93.9 | 94.2 | 94.6 | 94.6 | - | - | - | - | - | - | - | - | - | - | - | -
VM-BQ1 | S | 162.3 | 0.95228 | 30.512 | - | - | 48.2 | 57 | 60.4 | 60.5 | 61.3 | 61.7 | - | - | - | - | - | - | - | - | - | - | - | -
VM-BQ1 | W | 173.8 | 0.98343 | 30.512 | - | - | 36.2 | 46.4 | 47.1 | 47.8 | 48.6 | 48.9 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-VM1 | S | 159.9 | 0.96916 | 2.8276 | - | - | 84.3 | 94.2 | 97.7 | 97.2 | 97.5 | 97.5 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-VM1 | W | 170.6 | 0.98837 | 2.8276 | - | - | 68.8 | 80.3 | 81.1 | 81.4 | 81.9 | 82 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-R136 | S | 21.5 | 0.97462 | 1.9347 | 8.0021 | 7.1 | 19.7 | 29.8 | 35.1 | 35.6 | 35.3 | 34.6 | 27.85% | 8.3 | 198.3369 | 775.1195 | 874.0928 | 832.5662 | 723.2958 | 92.75 | 279.25 | 312.5 | 304 | 275
RTS-R136 | W | 24.7 | 0.98837 | 1.9347 | 8.0021 | 7.1 | 17.2 | 28.8 | 30.5 | 30.9 | 31 | 30.9 | 14.24% | 4.1 | 198.3369 | 775.1195 | 874.0928 | 832.5662 | 723.2958 | 92.75 | 279.25 | 312.5 | 304 | 275
FBTS-SO | S | 109.2 | 0.95961 | 0.9262 | - | - | 71.8 | 92.3 | 100.1 | 101.5 | 102.3 | 103.2 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-SO | W | 125.7 | 0.988 | 0.9262 | - | - | 50 | 73 | 76.6 | 78.3 | 79 | 80.6 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-K | S | 90.3 | 0.95994 | 0 | - | - | 62.4 | 65.4 | 65.8 | 65.7 | 65.4 | 64.9 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-K | W | 104.6 | 0.98708 | 0 | - | - | 61.9 | 68 | 69.6 | 72 | 74 | 76.1 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-EW | S | 85.7 | 0.98447 | 0 | - | - | 51.5 | 63.3 | 66.4 | 66.5 | 67.5 | 68.2 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-EW | W | 101.7 | 0.99433 | 0 | - | - | 52.9 | 65.8 | 69 | 70.9 | 73.5 | 75.8 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-F179 | S | 12 | 0.98089 | 4.6517 | NA | 1.34 | 15.7 | 15.5 | 15.8 | 2.8 | 2.8 | 2.8 | 22.58% | 3.5 | 1.0173 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | -
BTS-F179 | W | 12.6 | 0.98148 | 4.6517 | NA | 1.34 | 16.2 | 18.3 | 18.9 | 2.9 | 2.8 | 2.8 | 31.15% | 5.7 | 1.0173 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | -
FR-WP1 | S | 78.3 | 0.98639 | 0.77534 | - | - | 14.7 | 17.7 | 18.7 | 18.9 | 19 | 18.9 | - | - | - | - | - | - | - | - | - | - | - | -
FR-WP1 | W | 84.6 | 1 | 0.77534 | - | - | 10.4 | 14 | 14.4 | 14.5 | 14.5 | 14.6 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-TK/BC | S | 135.5 | 0.98489 | 0 | - | - | 66.2 | 81.5 | 87 | 89.3 | 89.2 | 89.5 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-TK/BC | W | 137.2 | 0.99045 | 0 | - | - | 73.3 | 91.4 | 97.6 | 101 | 104.2 | 108 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-CW | S | 135.5 | 0.93052 | 3.4105 | - | - | 120.9 | 132.4 | 136 | 159.6 | 162.1 | 163.8 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-CW | W | 142.3 | 0.96635 | 3.4105 | - | - | 104 | 118.8 | 146.2 | 151.7 | 156.1 | 160.3 | - | - | - | - | - | - | - | - | - | - | - | -
VM-WA3 | S | 37.7 | 0.97297 | 3.238 | - | - | 18.5 | 20.6 | 21.1 | 21.5 | 21.6 | 21.6 | - | - | - | - | - | - | - | - | - | - | - | -
VM-WA3 | W | 40 | 1 | 3.238 | - | - | 12.1 | 15.5 | 15.8 | 16.2 | 16 | 16.1 | - | - | - | - | - | - | - | - | - | - | - | -
DLF5-TP53 | S | 12.6 | 0.95652 | 0.34125 | - | - | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | - | - | - | - | - | - | - | - | - | - | - | -
DLF5-TP53 | W | 13.1 | 0.95652 | 0.34125 | - | - | 6.9 | 6.9 | 7 | 6.9 | 6.9 | 6.9 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-PM | S | 66.3 | 0.96026 | 2.3792 | - | - | 15.1 | 18.3 | 18.8 | 18.8 | 18.9 | 19.1 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-PM | W | 86.3 | 0.97037 | 2.3792 | - | - | 13.5 | 16.9 | 17.1 | 17.4 | 17.9 | 18.4 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-WP | S | 125.7 | 0.96997 | 0.0709 | - | - | 89.9 | 100.1 | 103.7 | 102.9 | 102.9 | 102.7 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-WP | W | 137.2 | 0.989 | 0.0709 | - | - | 72.7 | 84.9 | 85.5 | 85.6 | 85.9 | 85.8 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-C186 | S | 9.9 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-C186 | W | 11.2 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
VM-WA1 | S | 37.7 | 0.9433 | 3.238 | - | - | 19.4 | 23.5 | 25.2 | 24.5 | 24.6 | 24.7 | - | - | - | - | - | - | - | - | - | - | - | -
VM-WA1 | W | 40 | 0.9918 | 3.238 | - | - | 12.2 | 16.3 | 16.5 | 16.3 | 16.8 | 16.9 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-C196 | S | 9.9 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-C196 | W | 11.2 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
FR-WP2 | S | 80 | 0.99275 | 0.77534 | - | - | 13.8 | 15.8 | 16.1 | 16.2 | 16.2 | 16.3 | - | - | - | - | - | - | - | - | - | - | - | -
FR-WP2 | W | 85.7 | 1 | 0.77534 | - | - | 9.5 | 11.6 | 11.7 | 11.8 | 12 | 12.1 | - | - | - | - | - | - | - | - | - | - | - | -
HB-Q | S | 95.5 | 0.91954 | 9.1666 | - | - | 87 | 85.6 | 85.7 | 86 | 86.1 | 85.7 | - | - | - | - | - | - | - | - | - | - | - | -
HB-Q | W | 108.6 | 0.97778 | 9.1666 | - | - | 63 | 70.1 | 72 | 74.5 | 77.7 | 80.2 | - | - | - | - | - | - | - | - | - | - | - | -
MG-AP | S | 91.5 | 0.95359 | 19.0045 | - | - | 47.4 | 53.9 | 55.7 | 56.5 | 57.5 | 57.6 | - | - | - | - | - | - | - | - | - | - | - | -
MG-AP | W | 91.5 | 0.98442 | 19.0045 | - | - | 38.5 | 48.8 | 50.7 | 52.7 | 54.3 | 56 | - | - | - | - | - | - | - | - | - | - | - | -
JA-WP | S | 47.4 | 0 | 4.6152 | - | - | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | - | - | - | - | - | - | - | - | - | - | - | -
JA-WP | W | 57.2 | 0 | 4.6152 | - | - | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | - | - | - | - | - | - | - | - | - | - | - | -
SK-EW | S | 86.3 | 0.97523 | 7.9699 | - | - | 32.3 | 43.1 | 45.6 | 45.5 | 46.1 | 46.6 | - | - | - | - | - | - | - | - | - | - | - | -
SK-EW | W | 91.5 | 0.99023 | 7.9699 | - | - | 30.7 | 40.8 | 42.9 | 43.7 | 45.3 | 47 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-VM3 | S | 120 | 0.93874 | 2.8276 | - | - | 50.6 | 62.8 | 66.5 | 68.3 | 70 | 71.4 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-VM3 | W | 129.7 | 0.97879 | 2.8276 | - | - | 33 | 47.4 | 49.1 | 50.6 | 51.8 | 53.2 | - | - | - | - | - | - | - | - | - | - | - | -
VM-LQ1 | S | 76.6 | 0.97605 | 3.2968 | - | - | 33.4 | 42.3 | 44.5 | 45.2 | 45.4 | 46.8 | - | - | - | - | - | - | - | - | - | - | - | -
VM-LQ1 | W | 86.9 | 0.9693 | 3.2968 | - | - | 22.8 | 32.3 | 33.5 | 33.6 | 34.1 | 34.9 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF3 | S | 87.5 | 0.96708 | 0.34125 | - | - | 24.3 | 28.2 | 29 | 29.8 | 30.6 | 31 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF3 | W | 87.5 | 0.98077 | 0.34125 | - | - | 20.8 | 24.2 | 24.7 | 25.5 | 25.8 | 26.3 | - | - | - | - | - | - | - | - | - | - | - | -
K-CL | S | 91.5 | 0.95714 | 7.4494 | - | - | 49 | 51.5 | 51.7 | 51.6 | 51.2 | 50.8 | - | - | - | - | - | - | - | - | - | - | - | -
K-CL | W | 105.7 | 0.99125 | 7.4494 | - | - | 34.3 | 37.4 | 38.5 | 39.8 | 41.2 | 42.6 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-R134 | S | 19.1 | 0.98276 | 1.9347 | - | - | 11.6 | 17.6 | 20.7 | 21 | 20.8 | 20.5 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-R134 | W | 20.7 | 0.9902 | 1.9347 | - | - | 10.2 | 17 | 18 | 18.2 | 18.3 | 18.2 | - | - | - | - | - | - | - | - | - | - | - | -
WP-MP3 | S | 83.9 | 0.9505 | 3.1674 | - | - | 40.4 | 47.4 | 48.9 | 48.2 | 47.6 | 47.1 | - | - | - | - | - | - | - | - | - | - | - | -
WP-MP3 | W | 91.5 | 0.9854 | 3.1674 | - | - | 27.4 | 35.4 | 35.8 | 35.4 | 35 | 34.6 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-F182 | S | 12 | 1 | 4.6517 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-F182 | W | 12.6 | 1 | 4.6517 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-JA1 | S | 145.2 | 0.9249 | 4.5443 | - | - | 71.9 | 88.9 | 94.2 | 96.9 | 99.5 | 101.6 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-JA1 | W | 153.2 | 0.97831 | 4.5443 | - | - | 46.1 | 66.8 | 69.1 | 71.4 | 73 | 74.8 | - | - | - | - | - | - | - | - | - | - | - | -
E-PM | S | 74.3 | 0.93007 | 2.5972 | - | - | 14.3 | 17.2 | 17.6 | 17.4 | 17.4 | 17.4 | - | - | - | - | - | - | - | - | - | - | - | -
E-PM | W | 91.5 | 0.96094 | 2.5972 | - | - | 12.8 | 16.3 | 16.5 | 16.8 | 17.2 | 17.7 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-AP | S | 101.7 | 0.95536 | 6.1117 | - | - | 78.4 | 92 | 97.5 | 98.7 | 98.6 | 98.8 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-AP | W | 109.7 | 0.98089 | 6.1117 | - | - | 62.8 | 79.3 | 83.8 | 85.7 | 87.8 | 89.4 | - | - | - | - | - | - | - | - | - | - | - | -
L-Q | S | 95.4 | 0.90126 | 22.87 | - | - | 47.6 | 66.9 | 67.7 | 67.9 | 68 | 67.8 | - | - | - | - | - | - | - | - | - | - | - | -
L-Q | W | 108.6 | 0.99533 | 22.87 | - | - | 42.8 | 56.6 | 58.5 | 60.6 | 62.6 | 64.5 | - | - | - | - | - | - | - | - | - | - | - | -
DLF64-TP278 | S | 12.6 | 0.95652 | 0.34125 | - | - | 6.9 | 6.9 | 6.9 | 6.9 | 6.8 | 6.9 | - | - | - | - | - | - | - | - | - | - | - | -
DLF64-TP278 | W | 13.1 | 0.97101 | 0.34125 | - | - | 6.9 | 6.8 | 6.9 | 6.9 | 6.9 | 6.9 | - | - | - | - | - | - | - | - | - | - | - | -
WP-MP2 | S | 80 | 0.94815 | 3.1674 | - | - | 40.5 | 47.5 | 49 | 48.4 | 47.7 | 47.2 | - | - | - | - | - | - | - | - | - | - | - | -
WP-MP2 | W | 85.7 | 0.9854 | 3.1674 | - | - | 27.4 | 35.6 | 35.9 | 35.5 | 35.1 | 34.7 | - | - | - | - | - | - | - | - | - | - | - | -
VM-BQ3 | S | 125.7 | 0.95228 | 30.512 | - | - | 48.2 | 57 | 60.4 | 60.5 | 61.3 | 61.7 | - | - | - | - | - | - | - | - | - | - | - | -
VM-BQ3 | W | 128 | 0.98343 | 30.512 | - | - | 36.2 | 46.4 | 47.1 | 47.8 | 48.6 | 48.9 | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-L | S | 106.9 | 0.93135 | 13.7034 | 15.2611 | 2.09 | 97.6 | 121 | 122.2 | 122.5 | 122.8 | 122.4 | 11.65% | 14.1 | 206.894 | 217.9836 | 245.5312 | 277.5494 | 313.7429 | 23.3503 | 23.7994 | 25.1465 | 26.4936 | 27.9129
TSTS-L | W | 108.6 | 0.97927 | 13.7034 | - | - | 77.2 | 97.5 | 101 | 105.7 | 110 | 114.1 | - | - | - | - | - | - | - | - | - | - | - | -
WP-MP1 | S | 78.3 | 0.94815 | 3.1674 | - | - | 40.5 | 47.4 | 48.9 | 48.3 | 47.6 | 47.1 | - | - | - | - | - | - | - | - | - | - | - | -
WP-MP1 | W | 84.6 | 0.9854 | 3.1674 | - | - | 27.4 | 35.5 | 35.8 | 35.4 | 35 | 34.6 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-JA3 | S | 114.9 | 0.94504 | 4.5443 | - | - | 65.5 | 80.4 | 84.9 | 87.3 | 89.3 | 90.9 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-JA3 | W | 121.2 | 0.98601 | 4.5443 | - | - | 42.9 | 60.8 | 63 | 65.1 | 66.7 | 68.5 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-R135 | S | 21.5 | 0.96985 | 1.9347 | 8.0021 | 7.1 | 19.9 | 30 | 35.4 | 35.9 | 35.5 | 34.9 | 28.33% | 8.5 | 212.3154 | 827.466 | 931.8424 | 872.9945 | 775.1414 | 100 | 297.25 | 333 | 320.75 | 294.25
RTS-R135 | W | 24.7 | 0.98844 | 1.9347 | 8.0021 | 7.1 | 17.3 | 29 | 30.7 | 31.1 | 31.2 | 31.1 | 14.83% | 4.3 | 212.3154 | 827.466 | 931.8424 | 872.9945 | 775.1414 | 100 | 297.25 | 333 | 320.75 | 294.25
JA-LQ2 | S | 76.6 | 0.88462 | 5.0134 | - | - | 39 | 52.7 | 57.6 | 58.2 | 60.5 | 60.1 | - | - | - | - | - | - | - | - | - | - | - | -
JA-LQ2 | W | 86.9 | 0.96943 | 5.0134 | - | - | 22.9 | 37.8 | 39.1 | 40.9 | 41.4 | 42.3 | - | - | - | - | - | - | - | - | - | - | - | -
RD-EB | S | 65.2 | 0.99081 | 9.9144 | - | - | 54.4 | 53.6 | 54.5 | 54.7 | 54.7 | 54.7 | - | - | - | - | - | - | - | - | - | - | - | -
RD-EB | W | 77.2 | 1 | 9.9144 | - | - | 42.5 | 44.8 | 46.6 | 48.3 | 50.5 | 52.6 | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-RD | S | 80 | 0.98063 | 9.9144 | - | - | 67.1 | 67.1 | 68.2 | 68.5 | 68.5 | 68.5 | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-RD | W | 97.2 | 0.99231 | 9.9144 | - | - | 65 | 71 | 74.1 | 77.2 | 81.1 | 84.8 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-AR | S | 94.3 | 0.96266 | 4.1576 | - | - | 72.3 | 90.5 | 97.1 | 98.4 | 99.2 | 99 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-AR | W | 123.5 | 0.97822 | 4.1576 | - | - | 59.7 | 76.1 | 82.8 | 86.4 | 89.6 | 93.3 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-VM2 | S | 144 | 0.94603 | 2.8276 | - | - | 31.5 | 39.2 | 41.5 | 42.7 | 43.5 | 44.4 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-VM2 | W | 155.5 | 0.98529 | 2.8276 | - | - | 20.4 | 29.5 | 30.6 | 31.5 | 32.3 | 33.1 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-FB | S | 88 | 0.94522 | 0.91664 | - | - | 71.2 | 96.9 | 106 | 112.9 | 116.7 | 120.5 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-FB | W | 112 | 0.97203 | 0.91664 | - | - | 57.2 | 87.7 | 94.2 | 99.2 | 102.8 | 106.1 | - | - | - | - | - | - | - | - | - | - | - | -
BC-AR | S | 84.6 | 0.95663 | 7.9721 | - | - | 41.5 | 52.3 | 57 | 58.4 | 59.1 | 59 | - | - | - | - | - | - | - | - | - | - | - | -
BC-AR | W | 91.4 | 0.97345 | 7.9721 | - | - | 33.9 | 43.8 | 48.4 | 50.5 | 52.2 | 53.9 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-RP125 | S | 9 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-RP125 | W | 9.7 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-MG | S | 100.6 | 0.95547 | 12.8928 | - | - | 78.6 | 92.1 | 97 | 98.2 | 98.9 | 98.3 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-MG | W | 115.5 | 0.98246 | 12.8928 | - | - | 62.7 | 79.4 | 83.8 | 86.1 | 87.7 | 89.4 | - | - | - | - | - | - | - | - | - | - | - | -
VM-JA | S | 91.5 | 0.95828 | 7.3719 | - | - | 81.5 | 98.8 | 104.2 | 107.2 | 109.9 | 112.4 | - | - | - | - | - | - | - | - | - | - | - | -
VM-JA | W | 98.3 | 0.99257 | 7.3719 | - | - | 53.8 | 75.1 | 77.8 | 80.4 | 82.7 | 84.9 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BK185 | S | 10.5 | 1 | 4.4363 | - | - | 8.3 | 8.3 | 8.4 | 2.2 | 2.2 | 2.3 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BK185 | W | 10.5 | 1 | 4.4363 | - | - | 7.7 | 8.5 | 8.6 | 2.2 | 2.2 | 2.2 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-SK | S | 83.5 | 0.99022 | 7.9699 | - | - | 51.1 | 62.4 | 65.5 | 66.1 | 66.6 | 67.3 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-SK | W | 93.2 | 0.99811 | 7.9699 | - | - | 52.8 | 64.9 | 68 | 69.9 | 72.4 | 74.9 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-C191 | S | 9.9 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-C191 | W | 11.2 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-VM1 | S | 130.3 | 0.97156 | 2.8276 | - | - | 42.2 | 52.6 | 55.6 | 57.2 | 58.4 | 59.5 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-VM1 | W | 164.6 | 0.99634 | 2.8276 | - | - | 27.3 | 39.6 | 41 | 42.3 | 43.3 | 44.4 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-NR | S | 135.5 | 0.92456 | 10.9239 | - | - | 119.3 | 130.2 | 133.2 | 158.6 | 161.7 | 162.8 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-NR | W | 137.2 | 0.96101 | 10.9239 | - | - | 102.6 | 116.6 | 146.5 | 152.5 | 157.5 | 160.9 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-F189 | S | 14.1 | 0.98089 | 4.6517 | - | - | 15.7 | 15.4 | 15.7 | 3.2 | 3.2 | 3.3 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-F189 | W | 14.8 | 0.9875 | 4.6517 | NA | 1.34 | 16 | 18.3 | 18.9 | 3.1 | 3.1 | 3.1 | 19.13% | 3.5 | 1.057 | 0 | 0 | 0 | 0 | 2.0779 | 0 | 0 | 0 | 0
RTS-TK | S | 116.6 | 0.98904 | 3.8281 | - | - | 36.5 | 45.1 | 47.9 | 49.1 | 49 | 49.1 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-TK | W | 122.3 | 0.99738 | 3.8281 | - | - | 38.2 | 47.8 | 51.3 | 52.9 | 55.4 | 56.7 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-E | S | 66.3 | 0.93548 | 0.218 | - | - | 15.5 | 18.9 | 19.4 | 19.3 | 19.4 | 19.6 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-E | W | 86.3 | 0.96377 | 0.218 | - | - | 13.8 | 17.3 | 17.6 | 17.9 | 18.5 | 19 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-CL | S | 117.2 | 0.96314 | 7.4494 | - | - | 62.4 | 65.4 | 65.8 | 65.7 | 65.4 | 64.8 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-CL | W | 126.3 | 0.98708 | 7.4494 | - | - | 61.9 | 68 | 69.8 | 72.1 | 74.1 | 76.3 | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-EB | S | 94.9 | 0.98483 | 0 | - | - | 65.9 | 66.3 | 66.8 | 67.1 | 67.7 | 67.7 | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-EB | W | 101.7 | 0.99226 | 0 | - | - | 64.6 | 70.5 | 73.1 | 76.9 | 80.3 | 83.9 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-NC/WB | S | 74.305 | 1 | 25.6935 | - | - | 0 | 72.65 | 75.5 | 95.17 | 96.02 | 96.45 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-NC/WB | W | 93.167 | 1 | 25.6935 | - | - | 0 | 75.1 | 78.61 | 102.06 | 105.96 | 109.74 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-NC | S | 74.305 | 1 | 15.3119 | - | - | 36.9 | 34.17 | 34.9 | 35.48 | 36.04 | 36.48 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-NC | W | 97.1681 | 1 | 15.3119 | - | - | 55.1 | 34.56 | 36.08 | 37.86 | 39.66 | 41.41 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-WB | S | 74.305 | 1 | 10.3816 | - | - | 27.5 | 38.48 | 40.6 | 59.69 | 59.98 | 59.97 | - | - | - | - | - | - | - | - | - | - | - | -
BTS-WB | W | 97.1681 | 1 | 10.3816 | - | - | 0 | 40.54 | 42.53 | 64.2 | 66.3 | 68.33 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-DA1 | S | 71.4471 | 0.96 | 3.7136 | - | - | 20.5 | 41.5 | 46.07 | 50.34 | 51.77 | 50.97 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-DA1 | W | 87.4512 | 0.96 | 3.7136 | - | - | 11.8 | 35.37 | 40.11 | 43.61 | 43.82 | 43.14 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-DA2 | S | 71.4471 | 0.98 | 3.7136 | - | - | 20.1 | 41.5 | 46.07 | 50.34 | 51.77 | 50.97 | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-DA2 | W | 87.4512 | 0.98 | 3.7136 | - | - | 11.9 | 35.37 | 40.11 | 43.61 | 43.82 | 43.14 | - | - | - | - | - | - | - | - | - | - | - | -

## ZSS Aug Sum
Zone Substation | Season | Station N Import Rating (MVA) | Station N-1 Import Rating (MVA) | Station Nameplate Rating (MVA) | Station Power Factor at Maximum Demand | Embedded Generation Capacity (MVA) | Load Transfer Capability (MVA) | Hours load is > 95% of Maximum Demand (Hrs) | Actual Maximum Demand (MVA) | 10% POE |  |  |  |  | 50% POE |  |  |  |  | 50% POE load above N-1 Import Rating (%) | 50% POE load above N-1 Import Rating (MVA) | 10% POE | [14 empty] | 50% POE | [14 empty] | Weighted POE
[10 empty] | Forecast Maximum Demand (MVA) |  |  |  |  | Forecast Maximum Demand (MVA) | [6 empty] | Energy at Risk (MWh) |  |  |  |  | Expected Energy at Risk (MWh) |  |  |  |  | Hours at Risk (Hrs) |  |  |  |  | Energy at Risk (MWh) |  |  |  |  | Expected Energy at Risk (MWh) |  |  |  |  | Hours at Risk (Hrs) |  |  |  |  | Energy at Risk (MWh) |  |  |  |  | Expected Energy at Risk (MWh)
[5 empty] | 2025 | 2025 | 2026 | 2025 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2026 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030
AP | summer | 70 | 70 | 87 | 0.98831 | 6.1117 | 22.0629 | 10.1026 | 45.3604 | 54.86 | 56.82 | 57.49 | 58.15 | 58.52 | 51.09 | 52.88 | 53.64 | 54.23 | 54.65 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AP | winter | 71.3 | 71.3 | 87 | 2025: 0.99829; 2025: 6.1117; 2026: 22.0629; 2025: 1.7797; 2025: 38.0951; Forecast Maximum Demand (MVA) 2026: 48.57; Forecast Maximum Demand (MVA) 2027: 50.4; Forecast Maximum Demand (MVA) 2028: 52.2; Forecast Maximum Demand (MVA) 2029: 53.93; Forecast Maximum Demand (MVA) 2030: 55.59; Forecast Maximum Demand (MVA) 2026: 46.73; Forecast Maximum Demand (MVA) 2027: 48.45; Forecast Maximum Demand (MVA) 2028: 50.19; Forecast Maximum Demand (MVA) 2029: 51.8; Forecast Maximum Demand (MVA) 2030: 53.33; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
AR | summer | 61.8 | 32.9 | 60 | 0.99023 | 4.1576 | 9.5263 | 2.7641 | 33.0564 | 38.54 | 39.73 | 39.76 | 39.69 | 39.84 | 35.23 | 36.42 | 36.4 | 36.21 | 36.19 | 0.070821 | 2.33 | 49.43 | 91.04 | 84.18 | 76.07 | 82.81 | 0.04 | 0.08 | 0.08 | 0.07 | 0.07 | 34 | 50 | 45 | 39.5 | 44.5 | 3.39 | 11.99 | 10.86 | 8.7 | 9.06 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 3.5 | 11.5 | 11 | 10 | 10 | 17.202 | 35.705 | 32.856 | 28.911 | 31.185 | 0.012 | 0.031 | 0.031 | 0.028 | 0.028
AR | winter | 67.4 | 35.8 | 60 | 2025: 0.99901; 2025: 4.1576; 2026: 9.5263; 2025: 1.3987; 2025: 28.862; Forecast Maximum Demand (MVA) 2026: 33.77; Forecast Maximum Demand (MVA) 2027: 35.2; Forecast Maximum Demand (MVA) 2028: 36.42; Forecast Maximum Demand (MVA) 2029: 37.9; Forecast Maximum Demand (MVA) 2030: 39.49; Forecast Maximum Demand (MVA) 2026: 32; Forecast Maximum Demand (MVA) 2027: 33.4; Forecast Maximum Demand (MVA) 2028: 34.6; Forecast Maximum Demand (MVA) 2029: 35.99; Forecast Maximum Demand (MVA) 2030: 37.56; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
B | summer | 69.4 | 29 | 54 | 0.97516 | 9.0985 | 13.2201 | 7.1093 | 34.2985 | 41.23 | 42.12 | 42.74 | 43.18 | 43.31 | 36.96 | 37.84 | 38.41 | 38.8 | 38.94 | 0.27448 | 7.96 | 903.29 | 1133.62 | 1334.23 | 1438.34 | 1611.04 | 0.91 | 1.14 | 1.34 | 1.44 | 1.62 | 255 | 304.5 | 359 | 385 | 417 | 281.43 | 391.38 | 480.11 | 525.37 | 601.12 | 0.28 | 0.39 | 0.48 | 0.53 | 0.6 | 120 | 143.5 | 168 | 176.5 | 197 | 467.988 | 614.052 | 736.346 | 799.261 | 904.096 | 0.469 | 0.615 | 0.738 | 0.803 | 0.906
B | winter | 75.7 | 32.2 | 54 | 2025: 0.99084; 2025: 9.0985; 2026: 13.2201; 2025: 6.4826; 2025: 29.3319; Forecast Maximum Demand (MVA) 2026: 34.61; Forecast Maximum Demand (MVA) 2027: 35.26; Forecast Maximum Demand (MVA) 2028: 36.03; Forecast Maximum Demand (MVA) 2029: 36.6; Forecast Maximum Demand (MVA) 2030: 36.85; Forecast Maximum Demand (MVA) 2026: 31.92; Forecast Maximum Demand (MVA) 2027: 32.45; Forecast Maximum Demand (MVA) 2028: 33.21; Forecast Maximum Demand (MVA) 2029: 33.69; Forecast Maximum Demand (MVA) 2030: 33.97; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
BC | summer | 109.6 | 71.6 | 87 | 0.99423 | 3.8145 | 10.3455 | 3.1249 | 41.5935 | 61.53 | 65.55 | 67.26 | 67.2 | 67.15 | 48.27 | 52.25 | 54 | 54.21 | 54.2 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BC | winter | 123.8 | 70.6 | 87 | 2025: 0.99927; 2025: 3.8145; 2026: 10.3455; 2025: 1.6947; 2025: 39.1151; Forecast Maximum Demand (MVA) 2026: 48.11; Forecast Maximum Demand (MVA) 2027: 52.74; Forecast Maximum Demand (MVA) 2028: 54.66; Forecast Maximum Demand (MVA) 2029: 56.35; Forecast Maximum Demand (MVA) 2030: 58; Forecast Maximum Demand (MVA) 2026: 45.47; Forecast Maximum Demand (MVA) 2027: 50; Forecast Maximum Demand (MVA) 2028: 52.02; Forecast Maximum Demand (MVA) 2029: 53.68; Forecast Maximum Demand (MVA) 2030: 55.29; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
BK | summer | 27.2 | 27.2 | 23 | 0.99448 | 4.4363 | 0 | 2.275 | 16.9033 | 18.59 | 19.03 | 20.5195 | 21.7966 | 23.2901 | 16.95 | 17.26 | 19.0652 | 20.2518 | 21.6394 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BK | winter | 28.6 | 28.6 | 23 | 2025: 0.99877; 2025: 4.4363; 2026: 0; 2025: 1.7739; 2025: 15.8595; Forecast Maximum Demand (MVA) 2026: 18.68; Forecast Maximum Demand (MVA) 2027: 19.17; Forecast Maximum Demand (MVA) 2028: 23.3243; Forecast Maximum Demand (MVA) 2029: 25.2353; Forecast Maximum Demand (MVA) 2030: 27.3609; Forecast Maximum Demand (MVA) 2026: 17.24; Forecast Maximum Demand (MVA) 2027: 17.68; Forecast Maximum Demand (MVA) 2028: 22.3025; Forecast Maximum Demand (MVA) 2029: 24.1297; Forecast Maximum Demand (MVA) 2030: 26.1622; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
BQ | summer | 132.3 | 64.9 | 110 | 0.98882 | 27.6844 | 7.9449 | 12.7076 | 77.1524 | 95.77 | 97.17 | 96.27 | 95.18 | 93.79 | 87.29 | 88.81 | 88.08 | 87 | 85.71 | 0.34499 | 22.39 | 6178.5601 | 7754.3301 | 7264.8599 | 5964.0801 | 5053.6699 | 2.97 | 3.73 | 3.49 | 2.87 | 2.43 | 791.5 | 996.5 | 944.5 | 812 | 695.5 | 2586.5701 | 3340.99 | 3124.9299 | 2434.6799 | 2027.24 | 1.24 | 1.61 | 1.5 | 1.17 | 0.97 | 369 | 485 | 472 | 366 | 318 | 3664.1671 | 4664.992 | 4366.9089 | 3493.5 | 2935.169 | 1.759 | 2.246 | 2.097 | 1.68 | 1.408
BQ | winter | 147.3 | 72.3 | 110 | 2025: 0.99811; 2025: 27.6844; 2026: 7.9449; 2025: 3.3999; 2025: 64.9726; Forecast Maximum Demand (MVA) 2026: 83.77; Forecast Maximum Demand (MVA) 2027: 84.25; Forecast Maximum Demand (MVA) 2028: 84.43; Forecast Maximum Demand (MVA) 2029: 84.38; Forecast Maximum Demand (MVA) 2030: 84.69; Forecast Maximum Demand (MVA) 2026: 79.35; Forecast Maximum Demand (MVA) 2027: 79.85; Forecast Maximum Demand (MVA) 2028: 79.94; Forecast Maximum Demand (MVA) 2029: 79.81; Forecast Maximum Demand (MVA) 2030: 79.68; Forecast Maximum Demand (MVA) 2026: 0.09751; Forecast Maximum Demand (MVA) 2026: 7.05
CL | summer | 106.5 | 71.7 | 87 | 0.98815 | 7.4494 | 1.2384 | 4.9085 | 47.4862 | 52.7 | 53 | 52.94 | 52.75 | 52.52 | 49.72 | 50.03 | 49.83 | 49.59 | 49.22 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CL | winter | 120.2 | 70.7 | 87 | 2025: 0.99919; 2025: 7.4494; 2026: 1.2384; 2025: 2.1609; 2025: 36.7665; Forecast Maximum Demand (MVA) 2026: 41.42; Forecast Maximum Demand (MVA) 2027: 42.36; Forecast Maximum Demand (MVA) 2028: 43.57; Forecast Maximum Demand (MVA) 2029: 44.74; Forecast Maximum Demand (MVA) 2030: 46; Forecast Maximum Demand (MVA) 2026: 39.64; Forecast Maximum Demand (MVA) 2027: 40.64; Forecast Maximum Demand (MVA) 2028: 41.91; Forecast Maximum Demand (MVA) 2029: 43.13; Forecast Maximum Demand (MVA) 2030: 44.41; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
CW | summer | 65.3 | 34.4 | 54 | 0.99292 | 3.4105 | 10 | 8.2771 | 25.222 | 29.22 | 30.59 | 49.34 | 50.11 | 50.82 | 27.48 | 28.69 | 45.33 | 46.06 | 46.76 | - | - | 0 | 131.65 | 1637.03 | 1819.3 | 2189.3799 | 0 | 0.12 | 1.52 | 1.69 | 2.04 | 0 | 48 | 516 | 563.5 | 641.5 | 0 | 29.43 | 528.3 | 606.34 | 769.07 | 0 | 0.03 | 0.49 | 0.56 | 0.72 | 0 | 9.5 | 174.5 | 190 | 233.5 | 0 | 60.096 | 860.919 | 970.228 | 1195.163 | 0 | 0.057 | 0.799 | 0.899 | 1.116
CW | winter | 73.4 | 38.2 | 54 | 2025: 0.99871; 2025: 3.4105; 2026: 0.7621; 2025: 6.3184; 2025: 24.1813; Forecast Maximum Demand (MVA) 2026: 29.52; Forecast Maximum Demand (MVA) 2027: 51.93; Forecast Maximum Demand (MVA) 2028: 53.19; Forecast Maximum Demand (MVA) 2029: 54.62; Forecast Maximum Demand (MVA) 2030: 55.95; Forecast Maximum Demand (MVA) 2026: 26.21; Forecast Maximum Demand (MVA) 2027: 47.16; Forecast Maximum Demand (MVA) 2028: 48.46; Forecast Maximum Demand (MVA) 2029: 49.93; Forecast Maximum Demand (MVA) 2030: 51.28; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
DA | summer | 60.96 | 30.48 | 54 | 0.95893 | 3.7136 | 16.1977 | 3.2879 | 31.3641 | 44.94 | 49.69 | 54.06 | 55.65 | 54.88 | 41.5 | 46.07 | 50.34 | 51.77 | 50.97 | 0.36155 | 11.02 | 1922.25 | 5911.2202 | 13979.3701 | 17114.5801 | 15071.0195 | 2.59 | 20.06 | 166.99 | 275.82 | 221.55 | 615.5 | 1736.5 | 3453.5 | 3757 | 3449 | 736.99 | 2379.1599 | 6175.4302 | 8340.3896 | 7221.8999 | 0.99 | 3.2 | 28.66 | 61.42 | 40.65 | 262 | 735 | 1640 | 2042.5 | 1829 | 1092.568 | 3438.778 | 8516.6122 | 10972.6468 | 9576.6358 | 1.47 | 8.258 | 70.159 | 125.74 | 94.92
DA | winter | 60.96 | 30.48 | 54 | 2025: 0.96944; 2025: 3.7136; 2026: 16.1977; 2025: 2.1406; 2025: 24.5136; Forecast Maximum Demand (MVA) 2026: 44.6; Forecast Maximum Demand (MVA) 2027: 49.42; Forecast Maximum Demand (MVA) 2028: 52.73; Forecast Maximum Demand (MVA) 2029: 52.81; Forecast Maximum Demand (MVA) 2030: 52.23; Forecast Maximum Demand (MVA) 2026: 35.37; Forecast Maximum Demand (MVA) 2027: 40.11; Forecast Maximum Demand (MVA) 2028: 43.61; Forecast Maximum Demand (MVA) 2029: 43.82; Forecast Maximum Demand (MVA) 2030: 43.14; Forecast Maximum Demand (MVA) 2026: 0.16043; Forecast Maximum Demand (MVA) 2026: 4.89
DLF | summer | 86.5 | 42 | 66 | 0.99648 | 0.34125 | 0 | 11.4249 | 14.6249 | 19.1 | 19.97 | 20.67 | 21.3 | 21.85 | 18.18 | 19.03 | 19.7 | 20.32 | 20.84 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DLF | winter | 99.3 | 49.3 | 66 | 2025: 0.99983; 2025: 0.34125; 2026: 0; 2025: 7.4762; 2025: 11.4198; Forecast Maximum Demand (MVA) 2026: 15.24; Forecast Maximum Demand (MVA) 2027: 15.81; Forecast Maximum Demand (MVA) 2028: 16.39; Forecast Maximum Demand (MVA) 2029: 16.88; Forecast Maximum Demand (MVA) 2030: 17.33; Forecast Maximum Demand (MVA) 2026: 14.59; Forecast Maximum Demand (MVA) 2027: 15.14; Forecast Maximum Demand (MVA) 2028: 15.69; Forecast Maximum Demand (MVA) 2029: 16.17; Forecast Maximum Demand (MVA) 2030: 16.59; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
E | summer | 10.9 | 0 | 13.5 | 1 | 0.218 | 2.9951 | 1.7474 | 1.2667 | 2.77 | 3 | 3.19 | 3.37 | 3.54 | 1.81 | 1.97 | 2.1 | 2.22 | 2.33 | 1 | 1.81 | 6522.25 | 7023.2598 | 7492.98 | 7885.5 | 8293.1904 | 21.16 | 22.79 | 24.31 | 25.58 | 26.91 | 8760 | 8760 | 8760 | 8760 | 8760 | 4326.2798 | 4653.71 | 4952.3999 | 5217.0601 | 5486.1099 | 14.04 | 15.1 | 16.07 | 16.93 | 17.8 | 8749.5 | 8748.5 | 8748.5 | 8748.5 | 8748.5 | 4985.0708 | 5364.5749 | 5714.5739 | 6017.592 | 6328.234 | 16.176 | 17.407 | 18.542 | 19.525 | 20.533
E | winter | 12.1 | 0 | 13.5 | 2025: 1; 2025: 0.218; 2026: 2.9951; 2025: 1.4193; 2025: 1.4823; Forecast Maximum Demand (MVA) 2026: 1.92; Forecast Maximum Demand (MVA) 2027: 2.06; Forecast Maximum Demand (MVA) 2028: 2.19; Forecast Maximum Demand (MVA) 2029: 2.31; Forecast Maximum Demand (MVA) 2030: 2.42; Forecast Maximum Demand (MVA) 2026: 1.77; Forecast Maximum Demand (MVA) 2027: 1.89; Forecast Maximum Demand (MVA) 2028: 2.01; Forecast Maximum Demand (MVA) 2029: 2.12; Forecast Maximum Demand (MVA) 2030: 2.22; Forecast Maximum Demand (MVA) 2026: 1; Forecast Maximum Demand (MVA) 2026: 1.77
F | summer | 30.2 | 13.5 | 20 | 0.99753 | 4.6517 | 2.3092 | 2.3948 | 15.1975 | 16.41 | 16.73 | 18.9452 | 20.438 | 22.0844 | 14.92 | 15.22 | 17.3027 | 18.666 | 20.1697 | 0.10519 | 1.42 | 53.17 | 72.85 | 0 | 0 | 0 | 0.05 | 0.06 | 0 | 0 | 0 | 54 | 65 | 0 | 0 | 0 | 9.83 | 15.4 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0 | 0 | 15 | 20 | 0 | 0 | 0 | 22.832 | 32.635 | 0 | 0 | 0 | 0.022 | 0.025 | 0 | 0 | 0
F | winter | 35.2 | 15.3 | 20 | 2025: 0.99903; 2025: 4.6517; 2026: 2.3092; 2025: 1.333; 2025: 15.5652; Forecast Maximum Demand (MVA) 2026: 18.59; Forecast Maximum Demand (MVA) 2027: 19.17; Forecast Maximum Demand (MVA) 2028: 22.2876; Forecast Maximum Demand (MVA) 2029: 24.151; Forecast Maximum Demand (MVA) 2030: 26.1829; Forecast Maximum Demand (MVA) 2026: 17.65; Forecast Maximum Demand (MVA) 2027: 18.21; Forecast Maximum Demand (MVA) 2028: 21.1906; Forecast Maximum Demand (MVA) 2029: 22.9624; Forecast Maximum Demand (MVA) 2030: 24.8942; Forecast Maximum Demand (MVA) 2026: 0.15359; Forecast Maximum Demand (MVA) 2026: 2.35
FB | summer | 113.7 | 63.7 | 90 | 0.96867 | 0.91664 | 3.5628 | 5.9769 | 30.1995 | 35.76 | 39.3 | 41.79 | 44.1 | 46.18 | 33.66 | 37.08 | 39.48 | 41.65 | 43.61 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FB | winter | 125.4 | 62 | 90 | 2025: 0.99437; 2025: 0.91664; 2026: 3.5628; 2025: 4.4946; 2025: 24.7358; Forecast Maximum Demand (MVA) 2026: 37.03; Forecast Maximum Demand (MVA) 2027: 39.67; Forecast Maximum Demand (MVA) 2028: 42.05; Forecast Maximum Demand (MVA) 2029: 44.24; Forecast Maximum Demand (MVA) 2030: 46.24; Forecast Maximum Demand (MVA) 2026: 34.66; Forecast Maximum Demand (MVA) 2027: 37.15; Forecast Maximum Demand (MVA) 2028: 39.4; Forecast Maximum Demand (MVA) 2029: 41.43; Forecast Maximum Demand (MVA) 2030: 43.3; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
FR | summer | 109.6 | 61.3 | 90 | 0.97489 | 0.70444 | 0 | 6.2181 | 40.4626 | 53.08 | 57.92 | 57.74 | 56.99 | 56.14 | 48.43 | 52.11 | 51.76 | 51.1 | 50.32 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FR | winter | 122.2 | 72.1 | 90 | 2025: 0.99147; 2025: 0.70444; 2026: 0; 2025: 6.7402; 2025: 28.6778; Forecast Maximum Demand (MVA) 2026: 40.78; Forecast Maximum Demand (MVA) 2027: 43.5; Forecast Maximum Demand (MVA) 2028: 43; Forecast Maximum Demand (MVA) 2029: 42.44; Forecast Maximum Demand (MVA) 2030: 41.8; Forecast Maximum Demand (MVA) 2026: 37.45; Forecast Maximum Demand (MVA) 2027: 39.35; Forecast Maximum Demand (MVA) 2028: 38.93; Forecast Maximum Demand (MVA) 2029: 38.51; Forecast Maximum Demand (MVA) 2030: 38.05; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
JA | summer | 203.5 | 127.8 | 165 | 0.99084 | 4.5443 | 59.8822 | 7.6842 | 106.9353 | 148.9 | 156.38 | 160.31 | 163.7 | 166.7 | 133.87 | 140.43 | 143.92 | 147.03 | 149.74 | 0.047496 | 6.07 | 312.3 | 790.08 | 1140.85 | 1413.0699 | 1847.79 | 0.39 | 1 | 1.44 | 1.78 | 2.33 | 48 | 96 | 114.5 | 127 | 148.5 | 11.06 | 67.91 | 152.67 | 255.76 | 375.32 | 0.01 | 0.09 | 0.19 | 0.32 | 0.47 | 4.5 | 20 | 34 | 43 | 59 | 101.432 | 284.561 | 449.124 | 602.953 | 817.061 | 0.124 | 0.363 | 0.565 | 0.758 | 1.028
JA | winter | 202.7 | 127.4 | 165 | 2025: 0.99981; 2025: 4.5443; 2026: 59.8822; 2025: 7.5457; 2025: 73.7776; Forecast Maximum Demand (MVA) 2026: 108.44; Forecast Maximum Demand (MVA) 2027: 111.81; Forecast Maximum Demand (MVA) 2028: 114.99; Forecast Maximum Demand (MVA) 2029: 117.84; Forecast Maximum Demand (MVA) 2030: 120.31; Forecast Maximum Demand (MVA) 2026: 99.73; Forecast Maximum Demand (MVA) 2027: 102.98; Forecast Maximum Demand (MVA) 2028: 105.86; Forecast Maximum Demand (MVA) 2029: 108.41; Forecast Maximum Demand (MVA) 2030: 110.69; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
L | summer | 76.6 | 32.1 | 60 | 0.98442 | 13.7034 | 16.4043 | 2.1279 | 45.7192 | 47.61 | 47.54 | 47.85 | 47.85 | 47.86 | 43.49 | 43.67 | 43.8 | 43.93 | 43.81 | 0.35483 | 11.39 | 525.04 | 524.05 | 584.01 | 612.17 | 742.02 | 0.51 | 0.51 | 0.57 | 0.6 | 0.72 | 117 | 114.5 | 134 | 146.5 | 181 | 229.92 | 241.13 | 257.17 | 271.41 | 314.9 | 0.22 | 0.23 | 0.25 | 0.26 | 0.31 | 68.5 | 68.5 | 71 | 76.5 | 91 | 318.456 | 326.006 | 355.222 | 373.638 | 443.036 | 0.307 | 0.314 | 0.346 | 0.362 | 0.433
L | winter | 87.6 | 36.4 | 60 | 2025: 0.99926; 2025: 13.7034; 2026: 16.4043; 2025: 1.2648; 2025: 32.0439; Forecast Maximum Demand (MVA) 2026: 36.42; Forecast Maximum Demand (MVA) 2027: 37.46; Forecast Maximum Demand (MVA) 2028: 39.03; Forecast Maximum Demand (MVA) 2029: 40.54; Forecast Maximum Demand (MVA) 2030: 42.21; Forecast Maximum Demand (MVA) 2026: 34.51; Forecast Maximum Demand (MVA) 2027: 35.64; Forecast Maximum Demand (MVA) 2028: 37.19; Forecast Maximum Demand (MVA) 2029: 38.77; Forecast Maximum Demand (MVA) 2030: 40.34; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
LQ | summer | 131.8 | 131.8 | 180 | 0.98272 | 0.46918 | 21.5294 | 5.6013 | 67.1982 | 90.8 | 95.31 | 97.21 | 98.81 | 100.08 | 85.82 | 90.38 | 92.19 | 93.76 | 95.01 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LQ | winter | 142.2 | 142.2 | 180 | 2025: 0.9908; 2025: 0.46918; 2026: 21.5294; 2025: 5.9885; 2025: 46.8948; Forecast Maximum Demand (MVA) 2026: 75.95; Forecast Maximum Demand (MVA) 2027: 78.85; Forecast Maximum Demand (MVA) 2028: 80.37; Forecast Maximum Demand (MVA) 2029: 81.75; Forecast Maximum Demand (MVA) 2030: 82.84; Forecast Maximum Demand (MVA) 2026: 69.9; Forecast Maximum Demand (MVA) 2027: 72.15; Forecast Maximum Demand (MVA) 2028: 73.64; Forecast Maximum Demand (MVA) 2029: 74.97; Forecast Maximum Demand (MVA) 2030: 76.1; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
MG | summer | 64.3 | 64.3 | 87 | 0.98517 | 12.8928 | 9.6787 | 10.245 | 30.5631 | 40.03 | 42.24 | 42.44 | 41.98 | 41.46 | 37.16 | 39.96 | 40.31 | 39.9 | 39.43 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MG | winter | 75 | 75 | 87 | 2025: 0.9964; 2025: 12.8928; 2026: 9.6787; 2025: 3.2119; 2025: 23.9996; Forecast Maximum Demand (MVA) 2026: 30.97; Forecast Maximum Demand (MVA) 2027: 33.2; Forecast Maximum Demand (MVA) 2028: 33.35; Forecast Maximum Demand (MVA) 2029: 33.44; Forecast Maximum Demand (MVA) 2030: 33.46; Forecast Maximum Demand (MVA) 2026: 30.09; Forecast Maximum Demand (MVA) 2027: 32.45; Forecast Maximum Demand (MVA) 2028: 32.56; Forecast Maximum Demand (MVA) 2029: 32.59; Forecast Maximum Demand (MVA) 2030: 32.58; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
MP | summer | 202.3 | 124 | 165 | 0.98588 | 3.0965 | 0 | 8.2059 | 77.7107 | 94.13 | 96.11 | 95.06 | 93.81 | 92.7 | 86.75 | 88.84 | 87.85 | 86.57 | 85.65 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MP | winter | 201.5 | 123.4 | 165 | 2025: 0.9972; 2025: 3.0965; 2026: 0; 2025: 8.9891; 2025: 55.8464; Forecast Maximum Demand (MVA) 2026: 72.45; Forecast Maximum Demand (MVA) 2027: 73.39; Forecast Maximum Demand (MVA) 2028: 72.47; Forecast Maximum Demand (MVA) 2029: 71.44; Forecast Maximum Demand (MVA) 2030: 70.85; Forecast Maximum Demand (MVA) 2026: 66.11; Forecast Maximum Demand (MVA) 2027: 66.6; Forecast Maximum Demand (MVA) 2028: 65.9; Forecast Maximum Demand (MVA) 2029: 65.17; Forecast Maximum Demand (MVA) 2030: 64.7; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
NC | summer | 72.8 | 31.9 | 60 | 0.99514 | 15.3119 | 0 | 3.2787 | 37.1673 | 37.39 | 38.17 | 38.86 | 39.38 | 39.92 | 34.17 | 34.9 | 35.48 | 36.04 | 36.48 | 0.07116 | 2.27 | 55.2 | 89.14 | 133.48 | 162.6 | 220.17 | 0.05 | 0.07 | 0.11 | 0.13 | 0.18 | 33.5 | 42 | 54.5 | 60.5 | 79.5 | 4.35 | 10.58 | 19.74 | 30.28 | 44.06 | 0 | 0.01 | 0.02 | 0.02 | 0.04 | 4.5 | 10.5 | 14.5 | 20.5 | 28.5 | 19.605 | 34.148 | 53.862 | 69.976 | 96.893 | 0.015 | 0.028 | 0.047 | 0.053 | 0.082
NC | winter | 83.7 | 40.2 | 60 | 2025: 0.99915; 2025: 15.3119; 2026: 0; 2025: 1.2833; 2025: 32.3608; Forecast Maximum Demand (MVA) 2026: 37.49; Forecast Maximum Demand (MVA) 2027: 39.11; Forecast Maximum Demand (MVA) 2028: 41.03; Forecast Maximum Demand (MVA) 2029: 42.94; Forecast Maximum Demand (MVA) 2030: 44.77; Forecast Maximum Demand (MVA) 2026: 34.56; Forecast Maximum Demand (MVA) 2027: 36.08; Forecast Maximum Demand (MVA) 2028: 37.86; Forecast Maximum Demand (MVA) 2029: 39.66; Forecast Maximum Demand (MVA) 2030: 41.41; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
NR | summer | 97.1 | 65.2 | 83 | 0.9867 | 10.9239 | 4.001 | 5.4827 | 52.7245 | 61.06 | 61.56 | 62.88 | 63.7 | 64 | 57.69 | 58.13 | 59.43 | 60.13 | 60.39 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NR | winter | 106.6 | 71.7 | 83 | 2025: 0.99769; 2025: 10.9239; 2026: 4.001; 2025: 1.8674; 2025: 45.0341; Forecast Maximum Demand (MVA) 2026: 54.03; Forecast Maximum Demand (MVA) 2027: 55.27; Forecast Maximum Demand (MVA) 2028: 57.45; Forecast Maximum Demand (MVA) 2029: 59.34; Forecast Maximum Demand (MVA) 2030: 61.06; Forecast Maximum Demand (MVA) 2026: 51.23; Forecast Maximum Demand (MVA) 2027: 52.29; Forecast Maximum Demand (MVA) 2028: 54.17; Forecast Maximum Demand (MVA) 2029: 55.87; Forecast Maximum Demand (MVA) 2030: 57.38; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
PM | summer | 34.8 | 17.4 | 27 | 0.96734 | 2.3792 | 5.7386 | 9.1784 | 13.7939 | 18.18 | 18.48 | 18.33 | 18.36 | 18.44 | 16.31 | 16.62 | 16.46 | 16.46 | 16.53 | - | - | 0 | 0.15 | 0.01 | 0.03 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 0.5 | 0.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.045 | 0.003 | 0.009 | 0.027 | 0 | 0 | 0 | 0 | 0
PM | winter | 39.4 | 19.7 | 27 | 2025: 0.98363; 2025: 2.3792; 2026: 5.7386; 2025: 2.0783; 2025: 12.4877; Forecast Maximum Demand (MVA) 2026: 16.5; Forecast Maximum Demand (MVA) 2027: 16.68; Forecast Maximum Demand (MVA) 2028: 16.95; Forecast Maximum Demand (MVA) 2029: 17.37; Forecast Maximum Demand (MVA) 2030: 17.72; Forecast Maximum Demand (MVA) 2026: 15.5; Forecast Maximum Demand (MVA) 2027: 15.67; Forecast Maximum Demand (MVA) 2028: 15.9; Forecast Maximum Demand (MVA) 2029: 16.3; Forecast Maximum Demand (MVA) 2030: 16.66; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
Q | summer | 54.4 | 27.2 | 60 | 0.99173 | 9.1666 | 6.0016 | 1.5913 | 35.9741 | 40.36 | 40.56 | 40.69 | 40.63 | 40.57 | 36.93 | 37.11 | 37.07 | 37.09 | 36.91 | 0.35772 | 9.73 | 516.5 | 503.22 | 518.72 | 515.18 | 571.56 | 0.53 | 0.51 | 0.53 | 0.53 | 0.58 | 141 | 128 | 134 | 139 | 152 | 217.02 | 214.69 | 214.58 | 215.47 | 226.28 | 0.22 | 0.22 | 0.22 | 0.22 | 0.23 | 75 | 72.5 | 73.5 | 69.5 | 75.5 | 306.864 | 301.249 | 305.822 | 305.383 | 329.864 | 0.313 | 0.307 | 0.313 | 0.313 | 0.335
Q | winter | 54.4 | 31.5 | 60 | 2025: 0.99932; 2025: 9.1666; 2026: 6.0016; 2025: 1.2539; 2025: 29.2834; Forecast Maximum Demand (MVA) 2026: 33.31; Forecast Maximum Demand (MVA) 2027: 34.08; Forecast Maximum Demand (MVA) 2028: 35.17; Forecast Maximum Demand (MVA) 2029: 36.25; Forecast Maximum Demand (MVA) 2030: 37.38; Forecast Maximum Demand (MVA) 2026: 31.88; Forecast Maximum Demand (MVA) 2027: 32.53; Forecast Maximum Demand (MVA) 2028: 33.5; Forecast Maximum Demand (MVA) 2029: 34.53; Forecast Maximum Demand (MVA) 2030: 35.57; Forecast Maximum Demand (MVA) 2026: 0.012063; Forecast Maximum Demand (MVA) 2026: 0.38
R | summer | 49.9 | 30.1 | 40 | 0.99346 | 1.9347 | 13.5105 | 7.2189 | 30.0634 | 47.67 | 57.52 | 58.43 | 58.2 | 57.67 | 44.43 | 51.45 | 51.98 | 51.53 | 50.82 | 0.47608 | 14.33 | 2717.2 | 16118.5898 | 17691.5 | 16844.1309 | 15902.0195 | 2.92 | 132.4 | 183.13 | 159.21 | 133.28 | 640 | 2452 | 2564.5 | 2522 | 2461 | 1526 | 8493.9902 | 9264.6396 | 8372.29 | 7519.7998 | 1.64 | 10.2 | 12.28 | 10.27 | 8.31 | 392.5 | 1797 | 1907 | 1802 | 1658.5 | 1883.36 | 10781.3701 | 11792.6978 | 10913.8423 | 10034.4657 | 2.024 | 46.86 | 63.535 | 54.952 | 45.801
R | winter | 58.9 | 36 | 40 | 2025: 0.99852; 2025: 1.9347; 2026: 13.5105; 2025: 9.4091; 2025: 24.9602; Forecast Maximum Demand (MVA) 2026: 43.11; Forecast Maximum Demand (MVA) 2027: 45.87; Forecast Maximum Demand (MVA) 2028: 46.27; Forecast Maximum Demand (MVA) 2029: 46.03; Forecast Maximum Demand (MVA) 2030: 45.88; Forecast Maximum Demand (MVA) 2026: 40.18; Forecast Maximum Demand (MVA) 2027: 42.54; Forecast Maximum Demand (MVA) 2028: 43.11; Forecast Maximum Demand (MVA) 2029: 43.14; Forecast Maximum Demand (MVA) 2030: 43.1; Forecast Maximum Demand (MVA) 2026: 0.11611; Forecast Maximum Demand (MVA) 2026: 4.18
RD | summer | 54.4 | 24.9 | 60 | 0.98692 | 9.9144 | 6.7637 | 1.0393 | 40.6046 | 43.66 | 44.06 | 44.3 | 44.41 | 44.34 | 39.03 | 39.39 | 39.69 | 39.85 | 39.78 | 0.56747 | 14.13 | 1074.52 | 1259.79 | 1479.89 | 1749.05 | 2101.9299 | 0.85 | 0.99 | 1.17 | 1.38 | 1.66 | 230.5 | 278.5 | 330.5 | 414.5 | 508 | 474.8 | 545.25 | 630.42 | 719.05 | 839.02 | 0.37 | 0.43 | 0.5 | 0.57 | 0.66 | 114.5 | 137.5 | 157 | 186.5 | 222 | 654.716 | 759.612 | 885.261 | 1028.05 | 1217.893 | 0.514 | 0.598 | 0.701 | 0.813 | 0.96
RD | winter | 54.4 | 28.7 | 60 | 2025: 0.99924; 2025: 9.9144; 2026: 6.7637; 2025: 1.0671; 2025: 27.5742; Forecast Maximum Demand (MVA) 2026: 31.17; Forecast Maximum Demand (MVA) 2027: 32.31; Forecast Maximum Demand (MVA) 2028: 33.81; Forecast Maximum Demand (MVA) 2029: 35.32; Forecast Maximum Demand (MVA) 2030: 36.82; Forecast Maximum Demand (MVA) 2026: 29.22; Forecast Maximum Demand (MVA) 2027: 30.34; Forecast Maximum Demand (MVA) 2028: 31.77; Forecast Maximum Demand (MVA) 2029: 33.23; Forecast Maximum Demand (MVA) 2030: 34.62; Forecast Maximum Demand (MVA) 2026: 0.018118; Forecast Maximum Demand (MVA) 2026: 0.52
SB | summer | 137.8 | 59.7 | 110 | 0.99123 | 7.9439 | 0 | 8.8935 | 38.8035 | 56.2 | 61.2 | 62.39 | 63.39 | 64.18 | 50.96 | 55.94 | 57.03 | 57.91 | 58.61 | - | - | 0 | 0 | 3.26 | 8.45 | 15.6 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 5 | 6.5 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.978 | 2.535 | 4.68 | 0 | 0 | 0 | 0 | 0.003
SB | winter | 151 | 63.6 | 110 | 2025: 0.9988; 2025: 7.9439; 2026: 0; 2025: 6.9248; 2025: 27.7532; Forecast Maximum Demand (MVA) 2026: 44.32; Forecast Maximum Demand (MVA) 2027: 47.13; Forecast Maximum Demand (MVA) 2028: 48.12; Forecast Maximum Demand (MVA) 2029: 48.83; Forecast Maximum Demand (MVA) 2030: 49.52; Forecast Maximum Demand (MVA) 2026: 42.02; Forecast Maximum Demand (MVA) 2027: 44.52; Forecast Maximum Demand (MVA) 2028: 45.48; Forecast Maximum Demand (MVA) 2029: 46.31; Forecast Maximum Demand (MVA) 2030: 46.98; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
SK | summer | 105.4 | 63.2 | 87 | 0.9895 | 7.9699 | 0 | 7.956 | 43.1955 | 54.77 | 57.25 | 57.46 | 57.89 | 58.56 | 51.54 | 54.07 | 54.37 | 54.7 | 55.34 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SK | winter | 116.6 | 72.9 | 87 | 2025: 0.99867; 2025: 7.9699; 2026: 0; 2025: 3.2477; 2025: 35.8096; Forecast Maximum Demand (MVA) 2026: 43.76; Forecast Maximum Demand (MVA) 2027: 45.77; Forecast Maximum Demand (MVA) 2028: 46.5; Forecast Maximum Demand (MVA) 2029: 48.03; Forecast Maximum Demand (MVA) 2030: 49.6; Forecast Maximum Demand (MVA) 2026: 41.99; Forecast Maximum Demand (MVA) 2027: 44.02; Forecast Maximum Demand (MVA) 2028: 44.7; Forecast Maximum Demand (MVA) 2029: 46.34; Forecast Maximum Demand (MVA) 2030: 47.88; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
SO | summer | 63.7 | 63.7 | 87 | 0.97887 | 0.9262 | 0 | 9.7725 | 31.4614 | 38.05 | 39.11 | 39.88 | 40.57 | 41.05 | 35.28 | 36.28 | 37.03 | 37.71 | 38.18 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SO | winter | 71.7 | 71.7 | 87 | 2025: 0.99409; 2025: 0.9262; 2026: 0; 2025: 9.6031; 2025: 22.3186; Forecast Maximum Demand (MVA) 2026: 29.57; Forecast Maximum Demand (MVA) 2027: 30.49; Forecast Maximum Demand (MVA) 2028: 31.49; Forecast Maximum Demand (MVA) 2029: 32.4; Forecast Maximum Demand (MVA) 2030: 33.19; Forecast Maximum Demand (MVA) 2026: 28.1; Forecast Maximum Demand (MVA) 2027: 28.98; Forecast Maximum Demand (MVA) 2028: 29.94; Forecast Maximum Demand (MVA) 2029: 30.79; Forecast Maximum Demand (MVA) 2030: 31.59; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
TK | summer | 110.2 | 52.5 | 87 | 0.98303 | 3.8281 | 13.3939 | 7.7155 | 45.6073 | 59.42 | 61.37 | 62.01 | 62.41 | 62.53 | 54.63 | 57.09 | 57.61 | 57.94 | 58.04 | 0.040571 | 2.13 | 50.64 | 106.25 | 124.41 | 130.91 | 129.75 | 0.05 | 0.1 | 0.12 | 0.12 | 0.12 | 30.5 | 50 | 55 | 53 | 52.5 | 1.03 | 9.99 | 14.01 | 17.43 | 18.08 | 0 | 0.01 | 0.01 | 0.02 | 0.02 | 2 | 8 | 11.5 | 13.5 | 13 | 15.913 | 38.868 | 47.13 | 51.474 | 51.581 | 0.015 | 0.037 | 0.043 | 0.05 | 0.05
TK | winter | 124.6 | 54.7 | 87 | 2025: 0.99742; 2025: 3.8281; 2026: 13.3939; 2025: 1.9209; 2025: 39.0239; Forecast Maximum Demand (MVA) 2026: 49.3; Forecast Maximum Demand (MVA) 2027: 50.92; Forecast Maximum Demand (MVA) 2028: 52.41; Forecast Maximum Demand (MVA) 2029: 53.77; Forecast Maximum Demand (MVA) 2030: 54.99; Forecast Maximum Demand (MVA) 2026: 47.36; Forecast Maximum Demand (MVA) 2027: 48.9; Forecast Maximum Demand (MVA) 2028: 50.34; Forecast Maximum Demand (MVA) 2029: 51.68; Forecast Maximum Demand (MVA) 2030: 52.9; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
VM | summer | 90.96 | 57.88 | 84 | 0.98882 | 2.8276 | 16.3852 | 10.2387 | 56.121 | 71.61 | 74.54 | 75.49 | 76.39 | 76.47 | 65.64 | 68.61 | 69.53 | 70.29 | 70.82 | 0.13407 | 7.76 | 685.98 | 1182.36 | 1397.11 | 1542.1801 | 1699.33 | 0.68 | 1.17 | 1.38 | 1.52 | 1.68 | 157.5 | 227 | 256.5 | 277 | 297 | 121.44 | 339.07 | 440.94 | 511.85 | 624.01 | 0.12 | 0.34 | 0.44 | 0.51 | 0.62 | 51.5 | 109 | 125.5 | 132.5 | 154 | 290.802 | 592.057 | 727.791 | 820.949 | 946.606 | 0.288 | 0.589 | 0.722 | 0.813 | 0.938
VM | winter | 110.1 | 70.22 | 84 | 2025: 0.99783; 2025: 2.8276; 2026: 16.3852; 2025: 10.641; 2025: 46.9418; Forecast Maximum Demand (MVA) 2026: 61.49; Forecast Maximum Demand (MVA) 2027: 62.7; Forecast Maximum Demand (MVA) 2028: 63.79; Forecast Maximum Demand (MVA) 2029: 64.61; Forecast Maximum Demand (MVA) 2030: 65.2; Forecast Maximum Demand (MVA) 2026: 58.08; Forecast Maximum Demand (MVA) 2027: 59.16; Forecast Maximum Demand (MVA) 2028: 60.28; Forecast Maximum Demand (MVA) 2029: 61.09; Forecast Maximum Demand (MVA) 2030: 61.72; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
WA | summer | 67.1 | 67.1 | 84 | 0.97679 | 0.41042 | 2.3816 | 10.3416 | 36.5721 | 44.58 | 46.38 | 46.66 | 46.91 | 46.99 | 42.02 | 43.54 | 43.81 | 44.02 | 44.19 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WA | winter | 73.7 | 73.7 | 84 | 2025: 0.99551; 2025: 0.41042; 2026: 2.3816; 2025: 7.9087; 2025: 25.5078; Forecast Maximum Demand (MVA) 2026: 35.18; Forecast Maximum Demand (MVA) 2027: 35.59; Forecast Maximum Demand (MVA) 2028: 35.89; Forecast Maximum Demand (MVA) 2029: 36.22; Forecast Maximum Demand (MVA) 2030: 36.44; Forecast Maximum Demand (MVA) 2026: 33.13; Forecast Maximum Demand (MVA) 2027: 33.58; Forecast Maximum Demand (MVA) 2028: 33.92; Forecast Maximum Demand (MVA) 2029: 34.21; Forecast Maximum Demand (MVA) 2030: 34.44; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
WB | summer | 52.7 | 31.8 | 52.7 | 0.99575 | 10.3816 | 3.1551 | 2.7405 | 36.3209 | 40.77 | 43.07 | 64.59 | 64.97 | 64.95 | 38.48 | 40.6 | 59.69 | 59.98 | 59.97 | 0.21006 | 6.68 | 259.06 | 502.13 | 18973.6699 | 19117.1191 | 19469.3809 | 0.15 | 0.28 | 310.86 | 339.76 | 381.43 | 82.5 | 151.5 | 2906 | 2776.5 | 2693 | 126.4 | 269.03 | 11666.8496 | 11510.3398 | 11774.3701 | 0.07 | 0.15 | 90.42 | 105.22 | 120.25 | 53 | 88.5 | 2043 | 1934 | 1889.5 | 166.198 | 338.96 | 13858.8957 | 13792.3736 | 14082.8733 | 0.094 | 0.189 | 156.552 | 175.582 | 198.604
WB | winter | 52.7 | 31.8 | 52.7 | 2025: 0.99853; 2025: 10.3816; 2026: 3.1551; 2025: 1.4661; 2025: 35.1451; Forecast Maximum Demand (MVA) 2026: 42.1; Forecast Maximum Demand (MVA) 2027: 44.17; Forecast Maximum Demand (MVA) 2028: 68.02; Forecast Maximum Demand (MVA) 2029: 70.29; Forecast Maximum Demand (MVA) 2030: 72.36; Forecast Maximum Demand (MVA) 2026: 40.54; Forecast Maximum Demand (MVA) 2027: 42.53; Forecast Maximum Demand (MVA) 2028: 64.2; Forecast Maximum Demand (MVA) 2029: 66.3; Forecast Maximum Demand (MVA) 2030: 68.33; Forecast Maximum Demand (MVA) 2026: 0.27484; Forecast Maximum Demand (MVA) 2026: 8.74
WG | summer | 109.9 | 67.6 | 81 | 0.98961 | 25.3788 | 18.119 | 9.3931 | 41.263 | 60.57 | 63.9 | 66.25 | 68.44 | 70.41 | 55.11 | 58.24 | 60.39 | 62.39 | 64.23 | - | - | 0 | 0 | 0 | 0 | 4.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.263 | 0 | 0 | 0 | 0 | 0
WG | winter | 119 | 71.9 | 81 | 2025: 0.99179; 2025: 25.3788; 2026: 18.119; 2025: 8.0734; 2025: 33.1254; Forecast Maximum Demand (MVA) 2026: 52.66; Forecast Maximum Demand (MVA) 2027: 54.92; Forecast Maximum Demand (MVA) 2028: 56.9; Forecast Maximum Demand (MVA) 2029: 58.66; Forecast Maximum Demand (MVA) 2030: 60.33; Forecast Maximum Demand (MVA) 2026: 48.08; Forecast Maximum Demand (MVA) 2027: 50.01; Forecast Maximum Demand (MVA) 2028: 51.83; Forecast Maximum Demand (MVA) 2029: 53.5; Forecast Maximum Demand (MVA) 2030: 55.03; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
WP | summer | 143.3 | 71.7 | 110 | 0.98699 | 0.0709 | 0 | 7.61 | 27.5787 | 34.15 | 34.71 | 34.92 | 35.08 | 35.19 | 31.51 | 32.05 | 32.24 | 32.4 | 32.49 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WP | winter | 163.28 | 71.7 | 110 | 2025: 0.99708; 2025: 0.0709; 2026: 0; 2025: 5.7338; 2025: 22.3018; Forecast Maximum Demand (MVA) 2026: 25.15; Forecast Maximum Demand (MVA) 2027: 25.45; Forecast Maximum Demand (MVA) 2028: 25.77; Forecast Maximum Demand (MVA) 2029: 26.02; Forecast Maximum Demand (MVA) 2030: 26.26; Forecast Maximum Demand (MVA) 2026: 23.97; Forecast Maximum Demand (MVA) 2027: 24.2; Forecast Maximum Demand (MVA) 2028: 24.39; Forecast Maximum Demand (MVA) 2029: 24.55; Forecast Maximum Demand (MVA) 2030: 24.73; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -