## Intro
CitiPower 2025 Distribution System Limitation Template
This Distribution Systems Limitations template is intended to make the Distribution Annual Planning Report (DAPR) limitation data more accessible and usable. Any information provided in this System Limitations template should be read in conjunction with the CitiPower 2025 DAPR. It should also be noted that the information in this template and the DAPR are based on high-level risk assessments produced for the DAPR. As such the numbers are indicative and subject to change. Therefore the information in this template should not be used to make investment decisions, and should only be used to assist in discussions with CitiPower. Finalised data will be produced in a detailed risk assessment conducted at the RIT-D or business case stage. However CitiPower invites interested parties to submit their proposals or to engage in joint planning with CitiPower as early as possible in order to defer or avoid the proposed augmentation. CitiPower also publishes its own Network Limitation maps in order to assist with the visualisation of the limitation data presented within this template and the DAPR. The data in this template will be updated annually and will be published along with the DAPR. We welcome any feedback to improve the content or usability of this template.

## Citipower Limitations
Owner | Asset Name | Project Name | Asset Code | Network Element | Voltage level (kV) | Rating | [5 empty] | Nameplate Rating | Location |  |  |  | Residential customers affected |  | Business Case | [7 empty] | Demand Reduction required to defer investment by 1 year |  | Emergency Generation |  | Load Transfer capability (MVA) | Power Factor | 10% POE | [14 empty] | 50% POE | [14 empty] | Weighted Expected Energy at Risk (MWh)
[6 empty] | Summer |  |  | Winter |  |  |  | Start |  | End |  |  |  | Constraint Primary Driver | Investment Description | Preferred network investment |  |  |  | Proposed Timing | Annual Deferral Value | [6 empty] | Forecast Minimum Demand (MVA) |  |  |  |  | Maximum Load at risk (MVA) (N-1) |  |  |  |  | Maximum Load at risk (MVA) (N-2) |  |  |  |  | Forecast Minimum Demand (MVA) |  |  |  |  | Maximum Load at risk (MVA) (N-1) |  |  |  |  | Maximum Load at risk (MVA) (N-2)
[6 empty] | N Rating (MVA) | N-1 Rating (MVA) | N-2 Rating (MVA) | N Rating (MVA) | N-1 Rating (MVA) | N-2 Rating (MVA) |  | Longitude | Latitude | Longitude | Latitude | Count | Percent |  |  | capital cost ($) | cost accuracy plus | cost accuracy minus | Operating cost ($) |  |  | (MW) | (MVA) | (MW) | (MVA) |  |  | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030
Note on AD1: Lin, Tim: E.g. contracting backup generators in a hospital to become embedded generators during unuasually high peaks

## Sub-T Aug Sum
Sub transmission line | Season | Line N Import Rating (MVA) | Line Power Factor at Minimum Demand | Embedded Generation Capacity (MVA) | Load Transfer Capability (MVA) | Hours load is > 95% of Minimum Demand (Hrs) | Actual Minimum Demand (MVA) | 50% POE |  |  |  |  | 50% POE load above N Import Rating (%) | 50% POE load above N Import Rating (MVA) | 50% POE
[8 empty] | Forecast Minimum Demand (MVA) | [6 empty] | Energy at Risk (MWh) |  |  |  |  | Expected Energy at Risk (MWh) |  |  |  |  | Hours at Risk (Hrs)
|  |  | 2025 | 2025 | 2026 | 2025 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2026 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030
RTS-RP124 | S | 7.6 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-RP124 | W | 7.6 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF1 | S | 87.5 | 1 | 0.34125 | - | - | 13.2 | 13.7 | 14 | 14.1 | 14.3 | 14.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF1 | W | 87.5 | 1 | 0.34125 | - | - | 13.2 | 13.5 | 13.7 | 13.9 | 14 | 14.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-LQ3 | S | 76.6 | 1 | 3.2968 | - | - | 8.3 | 10.4 | 11.8 | 12 | 12.2 | 12.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-LQ3 | W | 86.9 | 1 | 3.2968 | - | - | 7.8 | 10.4 | 10.7 | 11.1 | 11.3 | 11.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-WG | S | 88 | 1 | 25.3788 | - | - | 18.2 | 25.4 | 28.4 | 30.7 | 31.6 | 32.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-WG | W | 112 | 1 | 25.3788 | - | - | 18.6 | 28 | 31.3 | 32.4 | 33.2 | 34.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-WA2 | S | 37.7 | 0.9322 | 3.238 | - | - | 5.9 | 5.4 | 5.8 | 5.9 | 5.9 | 5.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-WA2 | W | 40 | 0.92727 | 3.238 | - | - | 5.5 | 5.9 | 6 | 6 | 6.1 | 6.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FB-WG | S | 89.7 | 1 | 26.2954 | - | - | 9.8 | 14.2 | 15.7 | 17.1 | 17.1 | 16.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FB-WG | W | 94.3 | 0.97872 | 26.2954 | - | - | 9.4 | 16.1 | 18.1 | 18.5 | 18.5 | 18.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-FR3 | S | 82.3 | 0.85455 | 0.70444 | - | - | 11 | 8.3 | 9.4 | 9.5 | 9.4 | 9.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-FR3 | W | 87.4 | 0.84615 | 0.70444 | - | - | 10.4 | 9.7 | 10.3 | 10.2 | 10.2 | 10.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-HB | S | 117.2 | 0.97931 | 0 | - | - | 14.5 | 14.3 | 11.4 | 8.5 | 6.5 | 6.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-HB | W | 126.3 | 0.98507 | 0 | - | - | 20.1 | 21 | 18.8 | 16.1 | 13.5 | 11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BQ3 | S | 139.7 | 0.99807 | 27.6844 | - | - | 51.8 | 50.2 | 51.7 | 51.8 | 51.8 | 51.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BQ3 | W | 149.2 | 0.99613 | 27.6844 | - | - | 51.7 | 51.6 | 51.9 | 52 | 52.2 | 52.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
B-NR | S | 85.7 | 1 | 20.0224 | - | - | 15.9 | 15.4 | 16.5 | 19.4 | 19.6 | 19.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
B-NR | W | 91.4 | 0.99371 | 20.0224 | - | - | 15.9 | 16.2 | 19.7 | 19.6 | 19.7 | 19.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
B-CW | S | 85.7 | 1 | 12.509 | - | - | 23.3 | 24.3 | 25.4 | 26.1 | 26.5 | 26.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
B-CW | W | 91.4 | 1 | 12.509 | - | - | 23.2 | 25.4 | 26.3 | 26.8 | 27.3 | 27.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BQ-WP3 | S | 84 | 0.92593 | 27.7553 | - | - | 13.5 | 14.4 | 13.9 | 14 | 14.2 | 14.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BQ-WP3 | W | 91.5 | 0.92857 | 27.7553 | - | - | 14 | 14.1 | 14 | 14.1 | 14.2 | 14.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BQ-WP2 | S | 84 | 0.92593 | 27.7553 | - | - | 13.5 | 14.4 | 13.9 | 14 | 14.2 | 14.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BQ-WP2 | W | 91.5 | 0.92857 | 27.7553 | - | - | 14 | 14.1 | 14 | 14.1 | 14.2 | 14.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-FR1 | S | 82.3 | 0.85455 | 0.70444 | - | - | 11 | 8.3 | 9.4 | 9.5 | 9.4 | 9.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-FR1 | W | 87.4 | 0.84615 | 0.70444 | - | - | 10.4 | 9.7 | 10.3 | 10.2 | 10.2 | 10.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BK194 | S | 10.3 | 0.46875 | 4.4363 | - | - | 3.2 | 2.5 | 3 | 2.9 | 2.9 | 2.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BK194 | W | 10.3 | 0.81481 | 4.4363 | - | - | 2.7 | 3.5 | 3.5 | 2.9 | 2.9 | 2.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TK-BC | S | 91.5 | 1 | 7.6426 | - | - | 16.6 | 19.4 | 21.5 | 22.6 | 22.6 | 22.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TK-BC | W | 91.5 | 1 | 7.6426 | - | - | 16.8 | 21 | 23.1 | 23.7 | 23.9 | 24.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SB-SO | S | 109.7 | 1 | 8.8701 | - | - | 13.8 | 14.8 | 20.1 | 20.5 | 20.6 | 20.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SB-SO | W | 121.7 | 1 | 8.8701 | - | - | 13.6 | 19.5 | 20.7 | 20.6 | 20.7 | 21.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BK187 | S | 10.3 | 0.26923 | 4.4363 | - | - | 2.6 | 2.2 | 2.6 | 3.2 | 3.3 | 2.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BK187 | W | 10.3 | 0.66667 | 4.4363 | - | - | 2.4 | 2.9 | 2.9 | 3.3 | 3.3 | 3.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-FR2 | S | 82.3 | 0.85455 | 0.70444 | - | - | 11 | 8.3 | 9.4 | 9.5 | 9.4 | 9.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-FR2 | W | 87.4 | 0.84615 | 0.70444 | - | - | 10.4 | 9.8 | 10.3 | 10.2 | 10.2 | 10.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-SB | S | 117.7 | 1 | 7.9439 | - | - | 23 | 23.8 | 29.5 | 30.1 | 30.4 | 30.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-SB | W | 130.3 | 1 | 7.9439 | - | - | 22.9 | 29.5 | 31.1 | 31.4 | 31.8 | 32.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-RP123 | S | 11.4 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-RP123 | W | 11.4 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FR-WP3 | S | 81.7 | 0.97368 | 0.77534 | - | - | 3.8 | 2.2 | 2.2 | 2.3 | 2.3 | 2.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FR-WP3 | W | 88 | 0.97222 | 0.77534 | - | - | 3.6 | 2.2 | 2.2 | 2.3 | 2.3 | 2.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BQ1 | S | 159.9 | 0.99818 | 27.6844 | - | - | 54.9 | 53.2 | 54.8 | 54.9 | 54.9 | 55 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BQ1 | W | 170.6 | 0.99635 | 27.6844 | - | - | 54.8 | 54.7 | 55 | 55.2 | 55.3 | 55.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-BQ1 | S | 162.3 | 1 | 30.512 | - | - | 15.9 | 14.8 | 16.2 | 16.3 | 16.5 | 16.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-BQ1 | W | 173.8 | 1 | 30.512 | - | - | 16.3 | 16.1 | 16.4 | 16.7 | 16.9 | 17.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-VM1 | S | 159.9 | 1 | 2.8276 | - | - | 45 | 43.5 | 45 | 45.1 | 45.2 | 45.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-VM1 | W | 170.6 | 0.99778 | 2.8276 | - | - | 45 | 44.9 | 45.2 | 45.4 | 45.5 | 45.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-R136 | S | 21.5 | 0.91892 | 1.9347 | - | - | 3.7 | 5.3 | 7.6 | 7.8 | 7.7 | 7.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-R136 | W | 24.7 | 0.94595 | 1.9347 | - | - | 3.7 | 7.1 | 7.9 | 7.9 | 7.8 | 7.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-SO | S | 109.2 | 1 | 0.9262 | - | - | 23 | 23.8 | 29.5 | 30.1 | 30.4 | 30.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-SO | W | 125.7 | 1 | 0.9262 | - | - | 22.9 | 29.5 | 31.1 | 31.4 | 31.8 | 32.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-K | S | 90.3 | 0.99435 | 0 | - | - | 17.7 | 20.9 | 21 | 20.6 | 20.2 | 19.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-K | W | 104.6 | 0.99459 | 0 | - | - | 18.5 | 21.8 | 22.1 | 22.2 | 22.3 | 22.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-EW | S | 85.7 | 0.97076 | 0 | - | - | 17.1 | 21.2 | 22.5 | 22.9 | 23 | 23.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-EW | W | 101.7 | 0.98324 | 0 | - | - | 17.9 | 22.3 | 23.4 | 23.8 | 24.2 | 24.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-F179 | S | 12 | 0.38235 | 4.6517 | - | - | 3.4 | 3.4 | 3.3 | 3 | 3.1 | 3.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-F179 | W | 12.6 | 0.6 | 4.6517 | - | - | 3.5 | 3.9 | 4 | 3 | 3 | 3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FR-WP1 | S | 78.3 | 0.97619 | 0.77534 | - | - | 4.2 | 2.7 | 3.6 | 3.6 | 3.6 | 3.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FR-WP1 | W | 84.6 | 0.975 | 0.77534 | - | - | 4 | 2.8 | 3.1 | 3.1 | 3.1 | 3.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-TK/BC | S | 135.5 | 0.99095 | 0 | - | - | 22.1 | 25.6 | 28.1 | 28.9 | 29 | 29 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-TK/BC | W | 137.2 | 0.99119 | 0 | - | - | 22.7 | 27.8 | 29.8 | 30.4 | 30.7 | 31 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-CW | S | 135.5 | 0.9901 | 3.4105 | - | - | 30.3 | 30.9 | 32.5 | 35.9 | 36.4 | 36.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-CW | W | 142.3 | 0.99007 | 3.4105 | - | - | 30.2 | 32.5 | 36.6 | 36.9 | 37.4 | 37.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-WA3 | S | 37.7 | 0.9661 | 3.238 | - | - | 5.9 | 5.3 | 5.9 | 6 | 6 | 6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-WA3 | W | 40 | 0.96364 | 3.238 | - | - | 5.5 | 6 | 6.1 | 6.2 | 6.2 | 6.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLF5-TP53 | S | 12.6 | 0.95652 | 0.34125 | - | - | 6.9 | 6.9 | 7 | 6.9 | 6.9 | 6.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLF5-TP53 | W | 13.1 | 0.95714 | 0.34125 | - | - | 7 | 7 | 6.9 | 6.9 | 6.9 | 7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-PM | S | 66.3 | 1 | 2.3792 | - | - | 1.7 | 2.7 | 2.7 | 2.3 | 2.1 | 2.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-PM | W | 86.3 | 1 | 2.3792 | - | - | 3.1 | 4 | 3.8 | 3.5 | 3.5 | 3.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-WP | S | 125.7 | 0.9979 | 0.0709 | - | - | 47.6 | 45.7 | 47.3 | 47.3 | 47.3 | 47.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-WP | W | 137.2 | 0.99789 | 0.0709 | - | - | 47.3 | 47.1 | 47.5 | 47.6 | 47.7 | 47.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-C186 | S | 9.9 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-C186 | W | 11.2 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-WA1 | S | 37.7 | 0.93103 | 3.238 | - | - | 5.8 | 5.3 | 5.7 | 5.8 | 5.8 | 5.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-WA1 | W | 40 | 0.92593 | 3.238 | - | - | 5.4 | 5.8 | 5.9 | 5.9 | 6 | 6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-C196 | S | 9.9 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-C196 | W | 11.2 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FR-WP2 | S | 80 | 0.97436 | 0.77534 | - | - | 3.9 | 2.2 | 2.3 | 2.3 | 2.3 | 2.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FR-WP2 | W | 85.7 | 0.97297 | 0.77534 | - | - | 3.7 | 2.3 | 2.3 | 2.3 | 2.3 | 2.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HB-Q | S | 95.5 | 0.97531 | 9.1666 | - | - | 8.1 | 10.5 | 8.5 | 6.7 | 5.8 | 6.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HB-Q | W | 108.6 | 0.98507 | 9.1666 | - | - | 13.4 | 15.1 | 13.4 | 11.1 | 9.1 | 7.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MG-AP | S | 91.5 | 0.9823 | 19.0045 | - | - | 11.3 | 12.2 | 13.3 | 13.5 | 13.6 | 13.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MG-AP | W | 91.5 | 0.99138 | 19.0045 | - | - | 11.6 | 13.1 | 13.9 | 14 | 14.3 | 14.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
JA-WP | S | 47.4 | 0 | 4.6152 | - | - | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
JA-WP | W | 57.2 | 0 | 4.6152 | - | - | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SK-EW | S | 86.3 | 1 | 7.9699 | - | - | 11.7 | 15.9 | 17 | 17.3 | 17.4 | 17.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SK-EW | W | 91.5 | 1 | 7.9699 | - | - | 12.5 | 16.8 | 17.6 | 17.8 | 18.2 | 18.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-VM3 | S | 120 | 0.99242 | 2.8276 | - | - | 13.2 | 14.9 | 16.6 | 17 | 17.3 | 17.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-VM3 | W | 129.7 | 0.99231 | 2.8276 | - | - | 13 | 15.7 | 16.2 | 16.7 | 17.1 | 17.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-LQ1 | S | 76.6 | 0.96552 | 3.2968 | - | - | 8.7 | 10.6 | 11.8 | 12 | 12.6 | 12.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-LQ1 | W | 86.9 | 0.96386 | 3.2968 | - | - | 8.3 | 10.7 | 11.1 | 11.4 | 11.7 | 11.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF3 | S | 87.5 | 1 | 0.34125 | - | - | 13.2 | 13.7 | 14 | 14.2 | 14.3 | 14.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF3 | W | 87.5 | 1 | 0.34125 | - | - | 13.2 | 13.5 | 13.7 | 13.9 | 14 | 14.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
K-CL | S | 91.5 | 0.98198 | 7.4494 | - | - | 11.1 | 11.6 | 11.9 | 12 | 12 | 11.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
K-CL | W | 105.7 | 0.99123 | 7.4494 | - | - | 11.4 | 12.2 | 12.4 | 12.6 | 12.8 | 12.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-R134 | S | 19.1 | 0.90909 | 1.9347 | - | - | 2.2 | 3.2 | 4.5 | 4.6 | 4.5 | 4.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-R134 | W | 20.7 | 0.90909 | 1.9347 | - | - | 2.2 | 4.2 | 4.6 | 4.7 | 4.6 | 4.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WP-MP3 | S | 83.9 | 1 | 3.1674 | - | - | 11.3 | 9.7 | 10.6 | 10.6 | 10.4 | 10.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WP-MP3 | W | 91.5 | 1 | 3.1674 | - | - | 10.6 | 10.5 | 10.8 | 10.6 | 10.6 | 10.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-F182 | S | 12 | 1 | 4.6517 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-F182 | W | 12.6 | 1 | 4.6517 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-JA1 | S | 145.2 | 0.99465 | 4.5443 | - | - | 18.7 | 20.7 | 22.8 | 23.4 | 23.9 | 24.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-JA1 | W | 153.2 | 0.99459 | 4.5443 | - | - | 18.5 | 21.9 | 22.7 | 23.4 | 24 | 24.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
E-PM | S | 74.3 | 1 | 2.5972 | - | - | 1.7 | 2.6 | 2.7 | 2.3 | 2.1 | 2.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
E-PM | W | 91.5 | 1 | 2.5972 | - | - | 3.1 | 4 | 3.8 | 3.5 | 3.5 | 3.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-AP | S | 101.7 | 0.99535 | 6.1117 | - | - | 21.5 | 23.4 | 26.4 | 26.9 | 27 | 27.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-AP | W | 109.7 | 0.99528 | 6.1117 | - | - | 21.2 | 25.5 | 27.8 | 27.8 | 27.9 | 28.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
L-Q | S | 95.4 | 0.9717 | 22.87 | - | - | 10.6 | 9.3 | 7.7 | 5.9 | 4.3 | 3.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
L-Q | W | 108.6 | 0.97778 | 22.87 | - | - | 13.5 | 13.3 | 12.4 | 11 | 9.7 | 8.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLF64-TP278 | S | 12.6 | 0.97059 | 0.34125 | - | - | 6.8 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLF64-TP278 | W | 13.1 | 0.97101 | 0.34125 | - | - | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WP-MP2 | S | 80 | 1 | 3.1674 | - | - | 11.3 | 9.7 | 10.7 | 10.6 | 10.4 | 10.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WP-MP2 | W | 85.7 | 1 | 3.1674 | - | - | 10.6 | 10.5 | 10.8 | 10.6 | 10.6 | 10.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-BQ3 | S | 125.7 | 1 | 30.512 | - | - | 15.9 | 14.8 | 16.2 | 16.3 | 16.5 | 16.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-BQ3 | W | 128 | 1 | 30.512 | - | - | 16.3 | 16.1 | 16.4 | 16.7 | 16.9 | 17.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-L | S | 106.9 | 0.97931 | 13.7034 | - | - | 14.5 | 14.4 | 11.6 | 8.8 | 6.8 | 6.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-L | W | 108.6 | 0.98507 | 13.7034 | - | - | 20.1 | 21.1 | 18.9 | 16.2 | 13.7 | 11.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WP-MP1 | S | 78.3 | 1 | 3.1674 | - | - | 11.3 | 9.7 | 10.7 | 10.6 | 10.5 | 10.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WP-MP1 | W | 84.6 | 1 | 3.1674 | - | - | 10.6 | 10.5 | 10.8 | 10.6 | 10.6 | 10.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-JA3 | S | 114.9 | 0.99429 | 4.5443 | - | - | 17.5 | 19.4 | 21.5 | 22 | 22.4 | 22.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-JA3 | W | 121.2 | 0.99425 | 4.5443 | - | - | 17.4 | 20.6 | 21.4 | 21.9 | 22.4 | 22.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-R135 | S | 21.5 | 0.91892 | 1.9347 | - | - | 3.7 | 5.4 | 7.7 | 7.8 | 7.7 | 7.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-R135 | W | 24.7 | 0.94595 | 1.9347 | - | - | 3.7 | 7.1 | 7.9 | 8 | 7.9 | 7.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
JA-LQ2 | S | 76.6 | 1 | 5.0134 | - | - | 8.1 | 10.3 | 11.7 | 11.9 | 12.1 | 12.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
JA-LQ2 | W | 86.9 | 0.94872 | 5.0134 | - | - | 7.8 | 10.3 | 10.6 | 10.9 | 11.2 | 11.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RD-EB | S | 65.2 | 0.82927 | 9.9144 | - | - | 4.1 | 5.5 | 5 | 4.7 | 4.6 | 4.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RD-EB | W | 77.2 | 0.94737 | 9.9144 | - | - | 7.6 | 8.2 | 7.7 | 7.2 | 6.6 | 6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-RD | S | 80 | 0.84783 | 9.9144 | - | - | 4.6 | 6.1 | 5.6 | 5.3 | 5 | 5.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-RD | W | 97.2 | 0.97196 | 9.9144 | - | - | 10.7 | 11.8 | 11.7 | 11 | 10.1 | 9.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-AR | S | 94.3 | 1 | 4.1576 | - | - | 16.6 | 19.4 | 21.6 | 22.5 | 22.5 | 22.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-AR | W | 123.5 | 1 | 4.1576 | - | - | 16.9 | 21.1 | 23.1 | 23.6 | 23.8 | 24.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-VM2 | S | 144 | 0.9878 | 2.8276 | - | - | 8.2 | 9.3 | 10.3 | 10.6 | 10.8 | 10.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-VM2 | W | 155.5 | 0.98765 | 2.8276 | - | - | 8.1 | 9.7 | 10.1 | 10.4 | 10.6 | 10.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-FB | S | 88 | 1 | 0.91664 | - | - | 18.2 | 25.4 | 28.5 | 30.7 | 31.6 | 32 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-FB | W | 112 | 1 | 0.91664 | - | - | 18.5 | 28 | 31.3 | 32.4 | 33.3 | 34.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BC-AR | S | 84.6 | 0.99038 | 7.9721 | - | - | 10.4 | 11.9 | 13.6 | 14.5 | 14.7 | 14.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BC-AR | W | 91.4 | 0.99065 | 7.9721 | - | - | 10.7 | 13 | 14.6 | 15.1 | 15.3 | 15.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-RP125 | S | 9 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-RP125 | W | 9.7 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-MG | S | 100.6 | 0.99533 | 12.8928 | - | - | 21.4 | 23.4 | 26.3 | 26.8 | 27 | 27.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-MG | W | 115.5 | 0.99526 | 12.8928 | - | - | 21.1 | 25.5 | 27.8 | 27.8 | 27.9 | 28.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-JA | S | 91.5 | 0.9955 | 7.3719 | - | - | 22.2 | 24.3 | 26.7 | 27.4 | 27.9 | 28.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
VM-JA | W | 98.3 | 0.9955 | 7.3719 | - | - | 22.2 | 25.9 | 27 | 27.6 | 28.3 | 29 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BK185 | S | 10.5 | 0.83333 | 4.4363 | - | - | 1.2 | 2.2 | 1.7 | 1 | 1.1 | 1.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-BK185 | W | 10.5 | 0.875 | 4.4363 | - | - | 2.4 | 2.3 | 2.2 | 1.2 | 1.3 | 1.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-SK | S | 83.5 | 0.94318 | 7.9699 | - | - | 17.6 | 21.6 | 22.8 | 23.2 | 23.3 | 23.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-SK | W | 93.2 | 0.96703 | 7.9699 | - | - | 18.2 | 22.7 | 23.6 | 24 | 24.4 | 24.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-C191 | S | 9.9 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-C191 | W | 11.2 | 1 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-VM1 | S | 130.3 | 0.98165 | 2.8276 | - | - | 10.9 | 12.4 | 13.8 | 14.1 | 14.4 | 14.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-VM1 | W | 164.6 | 0.98131 | 2.8276 | - | - | 10.7 | 12.9 | 13.5 | 13.8 | 14.2 | 14.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-NR | S | 135.5 | 0.99666 | 10.9239 | - | - | 29.9 | 30.7 | 32.3 | 35.7 | 36.2 | 36.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-NR | W | 137.2 | 0.99666 | 10.9239 | - | - | 29.9 | 32.3 | 36.6 | 36.9 | 37.3 | 37.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-F189 | S | 14.1 | 0.16667 | 4.6517 | - | - | 3 | 3.3 | 3.2 | 3.5 | 3.6 | 3.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-F189 | W | 14.8 | 0.37143 | 4.6517 | - | - | 3.5 | 3.7 | 3.8 | 3.5 | 3.5 | 3.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-TK | S | 116.6 | 0.98261 | 3.8281 | - | - | 11.5 | 13.1 | 14.4 | 14.8 | 14.9 | 14.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-TK | W | 122.3 | 0.9916 | 3.8281 | - | - | 11.9 | 14.3 | 15.3 | 15.6 | 15.7 | 15.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-E | S | 66.3 | 1 | 0.218 | - | - | 1.7 | 2.6 | 2.7 | 2.3 | 2.1 | 2.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-E | W | 86.3 | 1 | 0.218 | - | - | 3.1 | 4 | 3.8 | 3.5 | 3.5 | 3.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-CL | S | 117.2 | 0.99435 | 7.4494 | - | - | 17.7 | 20.9 | 21 | 20.6 | 20.2 | 19.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-CL | W | 126.3 | 0.99459 | 7.4494 | - | - | 18.5 | 21.8 | 22.1 | 22.2 | 22.3 | 22.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-EB | S | 94.9 | 0.86667 | 0 | - | - | 4.5 | 5.9 | 5.5 | 5.1 | 4.9 | 5.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-EB | W | 101.7 | 0.98113 | 0 | - | - | 10.6 | 11.7 | 11.6 | 10.9 | 10 | 9.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-NC/WB | S | 74.305 | 1 | 0 | - | - | 0 | 6.0843 | 6.3851 | 6.4774 | 3.5361 | 0.34657 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-NC/WB | W | 93.167 | 1 | 0 | - | - | 0 | 12.6909 | 12.5385 | 15.6183 | 11.9527 | 9.9894 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-NC | S | 74.305 | 1 | 15.3119 | - | - | 0 | -1.7806 | -2.5855 | -3.8093 | -5.1953 | -6.8615 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-NC | W | 97.1681 | 1 | 15.3119 | - | - | 0 | 3.0908 | 2.3102 | 1.7047 | -1.5815 | -2.2062 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-WB | S | 74.305 | 1 | 10.3816 | - | - | 0 | 7.8649 | 8.9706 | 10.2867 | 8.7314 | 7.2081 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BTS-WB | W | 97.1681 | 1 | 10.3816 | - | - | 0 | 9.6001 | 10.2283 | 13.9136 | 13.5343 | 12.1956 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-DA1 | S | 71.4471 | 0.96 | 3.7136 | - | - | 0 | 6.5622 | 7.4081 | 8.0911 | 8.3828 | 8.2758 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-DA1 | W | 87.4512 | 0.96 | 3.7136 | - | - | 0 | 7.6631 | 8.4492 | 9.0006 | 9.0308 | 8.9278 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-DA2 | S | 71.4471 | 0.98 | 3.7136 | - | - | 0 | 6.5622 | 7.4081 | 8.0911 | 8.3828 | 8.2758 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WMTS-DA2 | W | 87.4512 | 0.98 | 3.7136 | - | - | 0 | 7.6631 | 8.4492 | 9.0006 | 9.0308 | 8.9278 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -

## ZSS Aug Sum
Zone Substation | Season | Station N Export Rating (MVA) | Station N-1 Export Rating (MVA) | Station Nameplate Rating (MVA) | Station Power Factor at Minimum Demand | Embedded Generation Capacity (MVA) | Load Transfer Capability (MVA) | Generation Headroom (MVA) | Hours load is > 95% of Minimum Demand (Hrs) | Actual Minimum Demand (MVA) | 50% POE |  |  |  |  | % 50% POE load below N-1 Export Rating | 50% POE
[11 empty] | Forecast Minimum Demand (MVA) | [5 empty] | Energy at Risk (MWh) |  |  |  |  | Expected Energy at Risk (MWh) |  |  |  |  | Hours at Risk (Hrs)
[5 empty] | 2025 | 2025 | 2026 | 2025 | 2025 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030
AP | summer | -87 | -57 | 87 | 0.98206 | 6.1117 | 22.0629 | 50.8883 | 2.3498 | 11.2077 | 12.1826 | 12.9805 | 13.3098 | 13.5393 | 13.7588 | -
AP | winter | -87 | -57 | 87 | 0.98739 | 6.1117 | 22.0629 | 50.8883 | 16.2074 | 11.495 | 13.0877 | 13.6811 | 13.9979 | 14.2859 | 14.5142 | -
AR | summer | -60 | -30 | 60 | 0.96003 | 4.1576 | 9.5263 | 25.8424 | 2.177 | 7.288 | 7.5597 | 8.0819 | 8.072 | 7.9143 | 7.5007 | -
AR | winter | -60 | -30 | 60 | 0.96934 | 4.1576 | 9.5263 | 25.8424 | 12.5996 | 7.3384 | 8.1914 | 8.5576 | 8.5959 | 8.6442 | 8.7891 | -
B | summer | -54 | -27 | 54 | 0.99994 | 9.0985 | 13.2201 | 17.9015 | 3.1637 | 9.4639 | 9.2621 | 9.7011 | 9.8608 | 10.0005 | 10.0803 | -
B | winter | -54 | -27 | 54 | 0.99929 | 9.0985 | 13.2201 | 17.9015 | 10.7011 | 9.1965 | 9.2621 | 9.4844 | 9.6669 | 9.8394 | 10.0212 | -
BC | summer | -87 | -57 | 87 | 0.97973 | 3.8145 | 10.3455 | 53.1855 | 2.2043 | 11.265 | 12.033 | 13.6455 | 14.572 | 14.7414 | 14.861 | -
BC | winter | -87 | -57 | 87 | 0.98657 | 3.8145 | 10.3455 | 53.1855 | 16.1058 | 11.4674 | 12.9734 | 14.5704 | 15.1544 | 15.3429 | 15.4816 | -
BK | summer | -23 | -20 | 23 | 0.99562 | 4.4363 | 0 | 15.5637 | 2.1771 | 2.2465 | 3.2634 | 3.0537 | -0.79429 | -1.1498 | -1.5672 | -
BK | winter | -23 | -20 | 23 | 0.99174 | 4.4363 | 0 | 15.5637 | 7.909 | 3.7174 | 4.2303 | 4.1903 | -1.5478 | -1.5478 | -1.5381 | -
BQ | summer | -110 | -55 | 110 | 0.99942 | 27.6844 | 7.9449 | 27.3156 | 3.3983 | 31.6483 | 31.3101 | 32.658 | 32.5182 | 32.1987 | 31.8193 | -
BQ | winter | -110 | -55 | 110 | 0.9995 | 27.6844 | 7.9449 | 27.3156 | 14.9721 | 31.5891 | 31.0739 | 31.3794 | 31.2214 | 30.9947 | 30.8667 | -
CL | summer | -87 | -57 | 87 | 0.97828 | 7.4494 | 1.2384 | 49.5506 | 3.598 | 11.1931 | 11.6111 | 11.8584 | 11.9969 | 12.0265 | 11.7199 | -
CL | winter | -87 | -57 | 87 | 0.98484 | 7.4494 | 1.2384 | 49.5506 | 20.1898 | 11.4131 | 12.1868 | 12.3985 | 12.5921 | 12.776 | 12.8532 | -
CW | summer | -54 | -27 | 54 | 0.97576 | 3.4105 | 10 | 23.5895 | 2.879 | 6.6102 | 6.427 | 6.9957 | 9.621 | 9.6705 | 9.8984 | -
CW | winter | -54 | -27 | 54 | 0.98503 | 3.4105 | 10 | 23.5895 | 7.0917 | 6.6529 | 6.974 | 10.0834 | 9.9158 | 9.8859 | 9.7479 | -
DA | summer | -54 | -27 | 54 | 0.97382 | 3.7136 | 16.1977 | 23.2864 | 2.7076 | 10.1936 | 13.1243 | 14.8163 | 16.1822 | 16.7657 | 16.5516 | -
DA | winter | -54 | -27 | 54 | 0.97816 | 3.7136 | 16.1977 | 23.2864 | 7.1334 | 11.0232 | 15.3262 | 16.8984 | 18.0012 | 18.0616 | 17.8556 | -
DLF | summer | -66 | -33 | 66 | 0.88673 | 0.34125 | 0 | 32.6587 | 2.3405 | 4.759 | 4.9585 | 5.2089 | 5.3675 | 5.5269 | 5.6774 | -
DLF | winter | -66 | -33 | 66 | 0.89718 | 0.34125 | 0 | 32.6587 | 30.7406 | 4.5736 | 4.7945 | 4.9585 | 5.1069 | 5.2577 | 5.4141 | -
E | summer | -13.5 | 0 | 13.5 | 1 | 0.218 | 2.9951 | 0 | 2.4359 | -5.5511e-17 | -0.07 | -0.08 | -0.08 | -0.08 | -0.09 | 100% | -0.41395 | -0.45173 | -0.48077 | -0.48434 | -0.47661 | -0.001343 | -0.001466 | -0.00156 | -0.001571 | -0.001546 | 10 | 10 | 10 | 9 | 8.5
E | winter | -13.5 | 0 | 13.5 | 1 | 0.218 | 2.9951 | 0 | 2.4067 | -5.5511e-17 | 0.05 | 0.06 | 0.06 | 0.07 | 0.08 | -
F | summer | -20 | -10 | 20 | 1 | 4.6517 | 2.3092 | 5.3483 | 2.2288 | 1.7967 | 2.5173 | 2.152 | -1.9553 | -2.6163 | -3.43 | -
F | winter | -20 | -10 | 20 | 0.98568 | 4.6517 | 2.3092 | 5.3483 | 6.3808 | 3.3006 | 3.7597 | 3.8189 | -2.022 | -2.0318 | -2.0612 | -
FB | summer | -90 | -60 | 90 | 0.99865 | 0.91664 | 3.5628 | 59.0834 | 6.0955 | 9.7632 | 11.1846 | 12.5741 | 13.4338 | 14.2136 | 14.9234 | -
FB | winter | -90 | -60 | 90 | 0.99847 | 0.91664 | 3.5628 | 59.0834 | 26.4615 | 9.3443 | 11.7824 | 12.8943 | 13.7678 | 14.5926 | 15.3693 | -
FR | summer | -90 | -60 | 90 | 0.99994 | 0.70444 | 0 | 59.2956 | 4.7045 | 11.454 | 12.2686 | 14.3474 | 14.4373 | 14.2574 | 14.0475 | -
FR | winter | -90 | -60 | 90 | 0.99975 | 0.70444 | 0 | 59.2956 | 70.1787 | 11.4062 | 13.7183 | 14.5225 | 14.3799 | 14.2273 | 14.0442 | -
JA | summer | -165 | -110 | 165 | 0.99019 | 4.5443 | 59.8822 | 105.4557 | 3.4824 | 31.9165 | 35.136 | 37.7735 | 38.8625 | 39.8118 | 40.6211 | -
JA | winter | -165 | -110 | 165 | 0.99137 | 4.5443 | 59.8822 | 105.4557 | 29.8115 | 32.4467 | 36.1683 | 37.5995 | 38.7937 | 39.9193 | 40.8663 | -
L | summer | -60 | -30 | 60 | 0.99226 | 13.7034 | 16.4043 | 16.2966 | 1.4785 | 3.8397 | 5.0401 | 3.6828 | 2.5538 | -2.3612 | -3.5968 | -
L | winter | -60 | -30 | 60 | 0.98456 | 13.7034 | 16.4043 | 16.2966 | 7.3804 | 6.5884 | 7.7232 | 6.448 | 5.1884 | 4.0121 | 3.1732 | -
LQ | summer | -180 | -120 | 180 | 0.99849 | 0.46918 | 21.5294 | 119.5308 | 12.9921 | 16.2512 | 20.4677 | 23.1256 | 23.5953 | 24.025 | 24.3648 | -
LQ | winter | -180 | -120 | 180 | 0.99822 | 0.46918 | 21.5294 | 119.5308 | 115.8363 | 15.5177 | 20.4876 | 21.2355 | 21.772 | 22.2985 | 22.7855 | -
MG | summer | -87 | -57 | 87 | 0.99498 | 12.8928 | 9.6787 | 44.1072 | 3.6218 | 10.1577 | 11.2 | 13.24 | 13.46 | 13.35 | 13.2 | -
MG | winter | -87 | -57 | 87 | 0.99385 | 12.8928 | 9.6787 | 44.1072 | 20.4719 | 9.5722 | 12.3015 | 13.6356 | 13.6256 | 13.5351 | 13.3946 | -
MP | summer | -165 | -110 | 165 | 0.99972 | 3.0965 | 0 | 106.9035 | 3.8941 | 22.6796 | 20.0417 | 21.4816 | 21.4716 | 21.2316 | 21.0816 | -
MP | winter | -165 | -110 | 165 | 0.9998 | 3.0965 | 0 | 106.9035 | 19.4594 | 22.2678 | 19.8024 | 20.0717 | 19.9021 | 19.8324 | 19.9221 | -
NC | summer | -60 | -30 | 60 | 0.70906 | 15.3119 | 0 | 14.6881 | 0.68256 | -1.7065 | -1.7806 | -2.5855 | -3.8093 | -5.1953 | -6.8615 | -
NC | winter | -60 | -30 | 60 | 0.92387 | 15.3119 | 0 | 14.6881 | 4.6553 | 2.9874 | 3.0908 | 2.3102 | 1.7047 | -1.5815 | -2.2062 | -
NR | summer | -83 | -55 | 83 | 0.98578 | 10.9239 | 4.001 | 44.0761 | 3.5959 | 14.1614 | 15.3132 | 15.8318 | 16.3904 | 16.6498 | 16.8692 | -
NR | winter | -83 | -55 | 83 | 0.98651 | 10.9239 | 4.001 | 44.0761 | 18.6595 | 14.1712 | 16.2877 | 16.8604 | 17.3158 | 17.6427 | 17.8611 | -
PM | summer | -27 | -13.5 | 27 | 1 | 2.3792 | 5.7386 | 11.1208 | 1.8338 | 1.6567 | 2.6573 | 2.7068 | 2.3213 | 2.0849 | 2.026 | -
PM | winter | -27 | -13.5 | 27 | 0.9952 | 2.3792 | 5.7386 | 11.1208 | 15.0898 | 3.1053 | 3.99 | 3.7805 | 3.5324 | 3.5128 | 3.5224 | -
Q | summer | -60 | -30 | 60 | 0.95142 | 9.1666 | 6.0016 | 20.8334 | 2.132 | 4.2113 | 5.481 | 4.5135 | 3.4337 | 2.5006 | 1.9331 | -
Q | winter | -60 | -30 | 60 | 0.97873 | 9.1666 | 6.0016 | 20.8334 | 9.4862 | 6.8729 | 7.4586 | 6.944 | 5.977 | 5.0882 | 4.2008 | -
R | summer | -40 | -26.5 | 40 | 0.92169 | 1.9347 | 13.5105 | 24.5653 | 2.1977 | 5.7829 | 8.4792 | 12.1014 | 12.3107 | 12.1712 | 11.9619 | -
R | winter | -40 | -26.5 | 40 | 0.93677 | 1.9347 | 13.5105 | 24.5653 | 4.503 | 5.8677 | 11.1462 | 12.4268 | 12.5264 | 12.3871 | 12.2279 | -
RD | summer | -60 | -30 | 60 | 0.23313 | 9.9144 | 6.7637 | 20.0856 | 0.97106 | 1.5871 | 2.5469 | -2.5381 | -3.0821 | -4.1041 | -5.5097 | -
RD | winter | -60 | -30 | 60 | 0.93352 | 9.9144 | 6.7637 | 20.0856 | 7.7228 | 3.3565 | 3.5828 | 3.0427 | 2.631 | 2.5702 | -2.6433 | -
SB | summer | -110 | -55 | 110 | 0.99892 | 7.9439 | 0 | 47.0561 | 3.6888 | 14.0151 | 16.2409 | 19.0308 | 19.5207 | 19.9007 | 20.1907 | -
SB | winter | -110 | -55 | 110 | 0.99926 | 7.9439 | 0 | 47.0561 | 32.4791 | 14.3873 | 18.5897 | 19.3641 | 19.787 | 20.1896 | 20.5524 | -
SK | summer | -87 | -57 | 87 | 0.9965 | 7.9699 | 0 | 49.0301 | 3.6763 | 14.2365 | 15.7748 | 16.8245 | 17.1444 | 17.2744 | 17.6043 | -
SK | winter | -87 | -57 | 87 | 0.99718 | 7.9699 | 0 | 49.0301 | 25.9019 | 14.3806 | 16.6611 | 17.37 | 17.52 | 17.8802 | 18.2307 | -
SO | summer | -87 | -57 | 87 | 0.99602 | 0.9262 | 0 | 56.0738 | 3.5071 | 9.1197 | 8.9565 | 9.3662 | 9.616 | 9.8559 | 10.0657 | -
SO | winter | -87 | -57 | 87 | 0.99796 | 0.9262 | 0 | 56.0738 | 30.3627 | 9.2923 | 10.03 | 10.3704 | 10.6815 | 10.9733 | 11.2558 | -
TK | summer | -87 | -57 | 87 | 0.97399 | 3.8281 | 13.3939 | 53.1719 | 2.7154 | 11.4751 | 13.1579 | 14.0728 | 14.2519 | 14.3912 | 14.5106 | -
TK | winter | -87 | -57 | 87 | 0.98213 | 3.8281 | 13.3939 | 53.1719 | 15.9055 | 11.7602 | 14.2074 | 14.746 | 14.9715 | 15.1779 | 15.2959 | -
VM | summer | -84 | -54 | 84 | 0.99686 | 2.8276 | 16.3852 | 51.1724 | 3.0707 | 20.4944 | 19.5402 | 21.0502 | 21.2902 | 21.5801 | 21.7601 | -
VM | winter | -84 | -54 | 84 | 0.99588 | 2.8276 | 16.3852 | 51.1724 | 10.4442 | 22.3856 | 20.8501 | 21.3502 | 21.6705 | 21.9506 | 22.2008 | -
WA | summer | -84 | -54 | 84 | 0.99781 | 0.41042 | 2.3816 | 53.5896 | 2.4017 | 10.9306 | 9.9364 | 10.953 | 11.0627 | 11.1524 | 11.2222 | -
WA | winter | -84 | -54 | 84 | 0.9964 | 0.41042 | 2.3816 | 53.5896 | 11.7644 | 10.2168 | 11.1036 | 11.3375 | 11.4997 | 11.642 | 11.7535 | -
WB | summer | -52.7 | -31.8 | 52.7 | 0.9944 | 10.3816 | 3.1551 | 21.4184 | 2.0754 | 4.4784 | 7.8649 | 8.9706 | 10.2867 | 8.7314 | 7.2081 | -
WB | winter | -52.7 | -31.8 | 52.7 | 0.99923 | 10.3816 | 3.1551 | 21.4184 | 8.8305 | 8.0962 | 9.6001 | 10.2283 | 13.9136 | 13.5343 | 12.1956 | -
WG | summer | -81 | -54 | 81 | 0.98864 | 25.3788 | 18.119 | 28.6212 | 3.3262 | 10.1554 | 15.8001 | 16.8501 | 17.5401 | 18.1801 | 18.7701 | -
WG | winter | -81 | -54 | 81 | 0.9999 | 25.3788 | 18.119 | 28.6212 | 19.7995 | 12.818 | 19.285 | 20.2847 | 21.164 | 22.0046 | 22.7642 | -
WP | summer | -110 | -55 | 110 | 0.99991 | 0.0709 | 0 | 54.9291 | 5.8383 | 7.6107 | 7.42 | 7.67 | 7.77 | 7.86 | 7.93 | -
WP | winter | -110 | -55 | 110 | 0.99999 | 0.0709 | 0 | 54.9291 | 37.545 | 7.1667 | 7.42 | 7.5802 | 7.7204 | 7.8608 | 7.9812 | -