## Zone Substation
Zone Substation |  | On-load Capacity - Nameplate Rating (MVA) | Hot or Cold Spare Capacity - Nameplate Rating (MVA) | Total Capacity - Nameplate Rating (MVA) | Cyclic N-1 Rating (MVA) | Hours Load is ≥ 95% of MD (note 4) | Station Power Factor at MD | Load Transfers (MVA) | Generation Capacity <1MW (MW) (notes 3) | Generation Capacity >1MW (1MW) (note 3) | Actual Demand (MVA) | 50% PoE Forecast Demand (MVA) |  |  |  |  | % Load Above N-1 Rating (2019) | Energy at Risk (MWh) (N-1 50% PoE) |  |  |  |  | Hours at Risk (N-1 50% PoE)
[11 empty] | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 |  | 2019 | 2020 | 2020 | 2021 | 2022 | 2019 | 2020 | 2021 | 2022 | 2023
BTS 22kV
BK | S | 23 | 10 | 33 | 27.2 |  | 0.96088 |  | 1.2 |  | 14.4486 | 13.3799 | 13.764 | 14.483 | 14.7345 | 15.2039 | -
| W | 23 | 10 | 33 | 28.6 |  | 0.98193 |  | 1.2 |  | 13.1851 | 13.7652 | 14.0966 | 14.6535 | 14.8641 | 15.1426 | -
C | S | 22.5 |  | 22.5 | 17 |  | 0.97273 |  | 0.7 |  | 11.0883 | 10.9086 | 11.0465 | 11.7574 | 12.0275 | 12.342 | -
| W | 22.5 |  | 22.5 | 17 |  | 0.98077 |  | 0.7 |  | 9.9144 | 10.363 | 10.5976 | 10.841 | 11.0987 | 11.2988 | -
F | S | 20 |  | 20 | 13 |  | 0.98347 | 4.4 | 1.4 |  | 10.8939 | 10.4049 | 10.598 | 11.2298 | 11.5542 | 11.9286 | -
| W | 20 |  | 20 | 15.3 |  | 0.99301 | 4.4 | 1.4 |  | 10.7626 | 11.4928 | 11.7614 | 12.2021 | 12.6057 | 12.9599 | -
BTS 66kV
BQ | S | 55 | 55 | 110 | 64.9 |  | 0.98008 |  | 1.3 |  | 63.4736 | 59.9239 | 61.7162 | 61.9195 | 64.4252 | 66.1274 | -
| W | 55 | 55 | 110 | 72.3 |  | 0.9974 |  | 1.3 |  | 46.4858 | 54.1412 | 56.326 | 58.493 | 59.8903 | 61.7963 | -
VM | S | 57 | 27 | 84 | 62.8 |  | 1 |  | 0.6 |  | 42.2878 | 41.616 | 45.3908 | 52.1251 | 54.4631 | 56.0342 | -
| W | 57 | 27 | 84 | 69.2 |  | 0.98769 |  | 0.6 |  | 32.6439 | 36.8168 | 41.8899 | 44.4459 | 46.0658 | 47.5416 | -
WA | S | 84 |  | 84 | 61 |  | 0.99434 |  |  |  | 54.5073 | 57.7922 | 60.9497 | 64.4488 | 67.6782 | 69.0331 | -
| W | 84 |  | 84 | 61 |  | 1 |  |  |  | 36.0574 | 43.2991 | 45.7165 | 47.7667 | 49.27 | 50.2996 | -
MP | S | 165 |  | 165 | 124 | [5 empty] | Note 4 | Note 4 | 119.0614 | 126.1252 | 134.2809 | 138.3179
| W | 165 |  | 165 | 123.4 | [5 empty] | Note 4 | Note 4 | 87.0899 | 92.1621 | 95.945 | 98.3954
DLF 22kV
TP | S | 20 |  | 20 | 11.6 |  | 0.87027 |  |  |  | 3.345 | 3.4 | Note 9 | Note 9 | Note 9 | Note 9 | -
| W | 20 |  | 20 | 12 |  | 0.91483 |  |  |  | 2.0255 | 2.3 | Note 9 | Note 9 | Note 9 | Note 9 | -
FBTS 66kV
AP | S | 60 | 27 | 87 | 70 |  | 0.99827 |  | 2 | 6 | 48.6351 | 49.5597 | 51.09 | 53.1571 | 55.3111 | 57.7937 | -
| W | 60 | 27 | 87 | 71.3 |  | 1 |  | 2 | 6 | 37.1512 | 42.431 | 43.8959 | 45.1342 | 46.59 | 48.1395 | -
E | S | 33.5 |  | 33.5 | 10.85 |  | 0.91667 |  |  |  | 3.4499 | 3.9467 | 4.1177 | 4.2869 | 4.484 | 4.671 | -
| W | 33.5 |  | 33.5 | 12.05 |  | 0.92593 |  |  |  | 2.2131 | 3.1052 | 3.2223 | 3.353 | 3.4722 | 3.602 | -
FB | S | 90 |  | 90 | 63.7 |  | 0.99245 |  | 0.1 |  | 23.8278 | 26.6312 | 30.2466 | 31.2378 | 32.6234 | 33.485 | -
| W | 90 |  | 90 | 62 |  | 0.95812 |  | 0.1 |  | 21.4268 | 22.5649 | 26.4036 | 26.5474 | 27.4617 | 28.3814 | -
MG | S | 60 | 27 | 87 | 64.3 |  | 1 |  | 1.1 |  | 34.5568 | 33.9773 | 35.2161 | 37.6234 | 39.5024 | 41.1863 | -
| W | 60 | 27 | 87 | 75 |  | 0.9697 |  | 1.1 |  | 26.2542 | 27.1328 | 28.151 | 29.5538 | 30.8618 | 32.1724 | -
PM | S | 27 | 13.5 | 40.5 | 28.2 |  | 0.99425 |  | 0.3 |  | 17.1218 | 16.8015 | 17.4819 | 18.8657 | 19.2783 | 20.1972 | -
| W | 27 | 13.5 | 40.5 | 28.2 |  | 1 |  | 0.3 |  | 13.7766 | 14.0603 | 14.4571 | 14.9897 | 15.4745 | 15.964 | -
SB | S | 110 |  | 110 | 59.7 |  | 0.95822 |  | 1.1 |  | 39.301 | 39.0372 | 40.9464 | 45.2701 | 47.9214 | 50.347 | -
| W | 110 |  | 110 | 63.6 |  | 0.97071 |  | 1.1 |  | 26.6444 | 29.6396 | 32.1057 | 34.794 | 36.5382 | 38.3299 | -
SO |  | 60 | 27 | 87 | 63.7 |  | 0.97531 |  | 0.3 |  | 41.1584 | 43.3337 | 45.4969 | 47.2642 | 49.7482 | 52.3506 | -
| W | 60 | 27 | 87 | 71.7 |  | 0.95342 |  | 0.3 |  | 26.834 | 34.0491 | 35.4279 | 36.8988 | 38.5133 | 39.9569 | -
WG | S | 81 |  | 81 | 67.6 |  | 0.9556 |  | 1.2 | 1.8 | 45.9189 | 46.5315 | 54.1856 | 57.2273 | 60.2119 | 63.1895 | -
| W | 81 |  | 81 | 71.9 |  | 0.95518 |  | 1.2 | 1.8 | 33.7628 | 40.2522 | 45.9527 | 47.557 | 49.8185 | 52.0276 | -
RTS 66kV
AR | S | 60 |  | 60 | 32.9 | 4 | 0.99709 | 4.6 | 0.8 |  | 36.3309 | 35.2175 | 36.1232 | 37.8571 | 38.802 | 39.353 | 7.044% | 12 | 12 | 58 | 103 | 179 | 10 | 11 | 26 | 37 | 57
| W | 60 |  | 60 | 35.8 | 6 | 0.99317 | 4.6 | 0.8 |  | 28.9861 | 31.3383 | 31.8801 | 32.8301 | 33.5056 | 34.1699 | -
B | S | 54 |  | 54 | 29 | 3 | 0.99716 | 11.3 | 0.7 | 6.2 | 30.3967 | 34.3828 | 34.7846 | 35.8132 | 36.4248 | 37.0873 | 18.56% | 2 | 5 | 23 | 56 | 122 | 4 | 8 | 21 | 37 | 64
| W | 54 |  | 54 | 32.2 | 5 | 0.99638 | 11.3 | 0.7 | 6.2 | 23.8102 | 27.7407 | 28.3506 | 28.918 | 29.3617 | 29.941 | -
BC | S | 57 | 30 | 87 | 71.6 |  | 0.99093 |  | 0.8 |  | 46.0375 | 45.9498 | 46.3942 | 48.9467 | 50.0175 | 50.7045 | -
| W | 57 | 30 | 87 | 70.6 |  | 0.98864 |  | 0.8 |  | 41.4314 | 44.4089 | 45.1219 | 46.1593 | 47.0684 | 47.6714 | -
CL | S | 60 | 27 | 87 | 71.7 |  | 0.97699 |  | 1.8 |  | 55.0764 | 49.2755 | 51.9209 | 55.3043 | 55.8103 | 57.1267 | -
| W | 60 | 27 | 87 | 70.7 |  | 1 |  | 1.8 |  | 35.6445 | 37.7493 | 39.4569 | 40.4189 | 40.9417 | 41.6848 | -
CW | S | 54 |  | 54 | 34.4 |  | 1 |  | 1.1 |  | 28.8251 | 26.8388 | 27.1511 | 28.0422 | 28.5774 | 29.2649 | -
| W | 54 |  | 54 | 38.2 |  | 0.9685 |  | 1.1 |  | 23.798 | 25.1079 | 25.4955 | 26.1609 | 26.6725 | 27.2754 | -
FR | S | 90 |  | 90 | 61.3 |  | 0.97065 |  | 0.8 |  | 55.0298 | 58.0414 | 61.394 | 65.236 | 69.3222 | 71.8125 | -
| W | 90 |  | 90 | 72.1 |  | 0.98163 |  | 0.8 |  | 35.4558 | 41.1434 | 43.1927 | 45.5844 | 47.4262 | 48.7658 | -
MP | S | 165 |  | 165 | 124 |  | 0.99433 |  | 0.4 | 1.2 | 103.8103 | 111.2761 | Note 7 | Note 7 | Note 7 | Note 7 | -
| W | 165 |  | 165 | 123.4 |  | 1 |  | 0.4 | 1.2 | 68.6584 | 82.3836 | Note 7 | Note 7 | Note 7 | Note 7 | -
NR | S | 83 |  | 83 | 65.2 |  | 0.99155 |  | 2.2 |  | 53.0313 | 53.7979 | 56.8307 | 58.9872 | 59.9631 | 61.8292 | -
| W | 83 |  | 83 | 71.7 |  | 1 |  | 2.2 |  | 39.2414 | 48.4851 | 50.7577 | 52.3152 | 53.0451 | 53.9511 | -
SK | S | 60 | 27 | 87 | 63.2 |  | 0.99575 |  | 0.4 | 6.2 | 48.1034 | 51.0858 | 51.8417 | 52.2063 | 52.8762 | 54.082 | -
| W | 60 | 27 | 87 | 72.9 |  | 1 |  | 0.4 | 6.2 | 36.0061 | 40.6155 | 41.1914 | 42.0953 | 42.7096 | 43.3335 | -
TK | S | 60 | 27 | 87 | 52.5 | 3 | 0.97804 | 18.9 | 0.9 |  | 51.3737 | 51.4173 | 52.7266 | 55.0231 | 57.2702 | 58.9607 | -
| W | 60 | 27 | 87 | 54.7 | 9 | 0.97494 | 18.9 | 0.9 |  | 40.1641 | 45.401 | 46.1742 | 48.8332 | 50.0263 | 50.7499 | -
RTS 22kV
R | S | 40 |  | 40 | 30.1 |  | 0.98846 |  | 0.4 |  | 23.1635 | 22.2933 | 23.5433 | 25.8579 | 26.5406 | 27.0039 | -
| W | 40 |  | 40 | 36 |  | 0.97183 |  | 0.4 |  | 18.4397 | 19.7053 | 21.4425 | 22.2427 | 22.6613 | 22.951 | -
RP | S | 20 |  | 20 | 9.45 | 4 | 0.8978 | 4.5 | 0.1 |  | 9.4219 | 10.2174 | 10.8081 | 11.5616 | 12.1412 | 12.2807 | 8.121% | 4 | 11 | 34 | 81 | 102 | 10 | 34 | 103 | 189 | 221
| W | 20 |  | 20 | 10.2 | 5 | 0.91429 | 4.5 | 0.1 |  | 6.8044 | 7.2582 | 7.6306 | 8.0542 | 8.3735 | 8.5381 | -
WMTS 66kV
JA | S | 165 |  | 165 | 127.8 |  | 1 |  | 3.8 |  | 105.4446 | 105.5562 | 121.4921 | 132.3395 | 140.8783 | 147.4549 | -
| W | 165 |  | 165 | 127.4 |  | 0.9973 |  | 3.8 |  | 66.6077 | 79.0612 | 85.6192 | 92.692 | 97.6844 | 100.625 | -
LQ | S | 120 | 60 | 180 | 131.8 |  | 0.99892 |  | 0.2 |  | 90.172 | 94.4752 | 100.1335 | 105.4155 | 110.6629 | 114.6009 | -
| W | 120 | 60 | 180 | 142.2 |  | 0.99257 |  | 0.2 |  | 61.8667 | 67.5108 | 71.6147 | 74.6226 | 77.3682 | 79.0487 | -
NC | S | 60 |  | 60 | 31.9 |  | 1 | 0 | 4.2 |  | 32.2816 | 29.3751 | 29.4738 | 30.7215 | 31.5349 | 31.9893 | -
| W | 60 |  | 60 | 40.2 |  | 0.9854 | 0 | 4.2 |  | 27.491 | 28.6454 | 29.0945 | 29.9053 | 30.3217 | 30.6082 | -
DA | S | 40.5 |  | 40.5 | 29.2 |  |  |  | 0.6 | 2 | Note 8 | Note 8 | Note 8 | 27.9791 | 30.3978 | 31.6183
| W | 40.5 |  | 40.5 | 32.6 |  |  |  | 0.6 | 2 | Note 8 | Note 8 | Note 8 | 25.4886 | 27.095 | 28.32
WB | S | 60 |  | 60 | 17.1 | 9 | 0.96279 | 4.2 | 2.1 |  | 22.243 | 22.3535 | 22.7084 | 23.9166 | 24.6698 | 25.1038 | 30.72% | 131 | 159 | 259 | 335 | 404 | 135 | 165 | 252 | 320 | 387
| W | 60 |  | 60 | 18.4 | 17 | 0.97608 | 4.2 | 2.1 |  | 19.5757 | 21.3658 | 21.8297 | 22.4657 | 22.838 | 23.3165 | 16.12%
WMTS 22kV
DA | S | 40.5 |  | 40.5 | 29.2 |  | 0.9863 |  | 0.6 | 2 | 25.4175 | 24.4266 | 25.3967 | Note 6 | Note 6 | Note 6 | -
| W | 40.5 |  | 40.5 | 32.6 |  | 1 |  | 0.6 | 2 | 21.4147 | 22.0758 | 23.0721 | Note 6 | Note 6 | Note 6 | -
J | S | 30 | 10 | 40 | 15.4 |  | 0.92958 |  | 0.4 |  | 6.7161 | 7.2206 | Note 1 | Note 1 | Note 1 | Note 1 | -
| W | 30 | 10 | 40 | 17.2 |  | 0.9322 |  | 0.4 |  | 4.6577 | 5.596 | Note 1 | Note 1 | Note 1 | Note 1 | -
LS | S | 30 |  | 30 | 24.2 |  | 0.97738 |  | 0.5 |  | 21.7527 | 20.3781 | 21.8008 | Note 2 | Note 2 | Note 2 | -
| W | 30 |  | 30 | 27 |  | 0.98958 |  | 0.5 |  | 18.3922 | 18.6559 | 19.9061 | Note 2 | Note 2 | Note 2 | -
TSTS 66kV
L | S | 60 |  | 60 | 32.1 | 6 | 0.98961 | 14.2 | 2.7 |  | 41.271 | 40.4501 | 41.0447 | 42.4535 | 43.0513 | 43.1789 | 26.01% | 192 | 220 | 302 | 341 | 356 | 68 | 73 | 85 | 90 | 92
| W | 60 |  | 60 | 36.4 | 7 | 0.98264 | 14.2 | 2.7 |  | 26.6708 | 27.9934 | 28.3745 | 28.8398 | 29.218 | 29.5707 | -
Q | S | 60 |  | 60 | 24.9 | 4 | 0.99241 | 7.4 | 2 |  | 35.2542 | 34.8199 | 35.0301 | 36.8935 | 38.1082 | 38.338 | 39.84% | 102 | 105 | 199 | 259 | 289 | 51 | 53 | 81 | 97 | 106
| W | 60 |  | 60 | 24.9 | 7 | 0.99653 | 7.4 | 2 |  | 26.4704 | 28.2915 | 28.6956 | 29.3927 | 29.8905 | 30.2737 | 13.62%
SVTS 66kV
RD | S | 60 |  | 60 | 32.1 | 3 | 0.99104 | 5.3 | 2.4 |  | 37.4175 | 33.8016 | 34.6586 | 35.554 | 35.6744 | 36.0726 | 5.301% | 374 | 439 | 547 | 547 | 590 | 98 | 109 | 126 | 128 | 137
| W | 60 |  | 60 | 24.9 | 7 | 1 | 5.3 | 2.4 |  | 23.4172 | 25.5606 | 25.9613 | 26.3495 | 26.6032 | 27.0661 | 2.653%
Note 1: J offloaded to JA
Note 2: LS off loaded to BQ
Note 3: Generation capacity <1MW is mostly solar PV
Note 4: Refer to RTS66 untill 2020
Note 5: Where load is above N-1 rating
Note 6: DA transferred to WMTS66
Note 7: Refer BTS66 for 2020 onwards
Note 8: Refer to WMTS22 untill 2021
Note 9: TP offloaded to JA
Note on F86: Rob Ingram: Was 30.7MVA now 24.9MVA due to lower Tx cable rating
Note on F87: Rob Ingram: Was 35.6 MVA now 24.9 MVA due to lower Tx cable rating
Note on F89: Rob Ingram: Was 32.1 MVA now 24.9 MVA due to lower Tx cable rating
Note on F90: Rob Ingram: Was 36.8 MVA now 24.9 MVA due to lower Tx cable rating

## Subtransmission lines
Subtransmission line |  | Line Rating (MVA) | Hours Load is 95% of MD | Power Factor at MD | Load Transfers (MVA) | Generation Capacity (MW) | Historical Demand Worst case N-1 Scenario (MVA) | Forecast Demand Worst case N-1 Scenario (MVA) |  |  |  |  | % Load Above N-1 Rating (2018) | Energy at Risk (MWh) (N-1 50% PoE) |  |  |  |  | Hours at Risk (N-1 50% PoE)
[7 empty] | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2019 | 2020 | 2021 | 2022 | 2023
BTS 22kV
BTS-BK185 | S | 10.5 |  | 0.91 |  |  | 7.7 | 7.1 | 7.6 | 8 | 8.1 | 8.4 | -
| W | 10.5 |  | 0.97 |  |  | 7 | 7.1 | 7 | 7.1 | 7.5 | 7.8 | -
BTS-BK187 | S | 10.3 |  | 0.91 |  |  | 6.5 | 6.8 | 7.2 | 7.1 | 7.7 | 7.3 | -
| W | 10.3 |  | 0.97 |  |  | 7 | 6.4 | 6.4 | 6.7 | 6.8 | 7.1 | -
BTS-BK194 | S | 10.3 |  | 0.91 |  |  | 7.7 | 7.1 | 7.6 | 8 | 8.1 | 8.4 | -
| W | 10.3 |  | 0.97 |  |  | 7 | 7.1 | 7 | 7.1 | 7.5 | 7.9 | -
BTS-C186 | S | 9.9 |  | 0.93 |  |  | 5.6 | 5.5 | 5.6 | 5.9 | 6.1 | 6.3 | -
| W | 11.2 |  | 1 |  |  | 5.4 | 5.1 | 5.2 | 5.3 | 5.5 | 5.6 | -
BTS-C191 | S | 9.9 |  | 0.93 |  |  | 5.6 | 5.5 | 5.6 | 5.9 | 6.1 | 6.2 | -
| W | 11.2 |  | 1 |  |  | 5.4 | 5.1 | 5.3 | 5.3 | 5.5 | 5.6 | -
BTS-C196 | S | 9.9 |  | 0.93 |  |  | 5.6 | 5.5 | 5.6 | 5.9 | 6.1 | 6.3 | -
| W | 11.2 |  | 1 |  |  | 5.4 | 5.1 | 5.3 | 5.3 | 5.5 | 5.6 | -
BTS-F179 | S | 12 |  | 0.93 |  |  | 11.3 | 10.6 | 10.8 | 11.4 | 11.7 | 12.2 | -
| W | 12.6 |  | 0.99 |  |  | 11.3 | 11.5 | 11.9 | 12.1 | 12.6 | 13 | -
BTS-F182 | S | 12 |  | 0.93 |  |  | Note 11 | Note 11 | Note 11 | Note 11 | Note 11 | Note 11
| W | 12.6 |  | 0.99 |  |  | Note 11 | Note 11 | Note 11 | Note 11 | Note 11 | Note 11
BTS-F189 | S | 14.1 |  | 0.93 |  |  | 11.2 | 10.5 | 10.7 | 11.3 | 11.6 | 12.1 | -
| W | 14.8 |  | 0.99 |  |  | 11.2 | 11.4 | 11.8 | 12 | 12.5 | 12.9 | -
BTS 66kV
BTS-BQ1 | S | 125.7 |  | 0.97 |  |  | 95.9 | 95.3 | 102 | 108.8 | 115 | 117.6 | -
| W | 128 |  | 1 |  |  | 68.9 | 71.8 | 76.3 | 82 | 87 | 90.1 | -
BTS-BQ3 | S | 145.2 |  | 0.97 |  |  | 90.5 | 89.9 | 96.4 | 102.6 | 108.5 | 111 | -
| W | 153.2 |  | 1 |  |  | 65 | 67.7 | 72 | 77.3 | 82.1 | 85 | -
BTS-VM1 | S | 125.7 |  | 0.97 |  |  | 82.8 | 82.6 | 88.5 | 94.7 | 100.1 | 102.3 | -
| W | 128 |  | 1 |  |  | 59.5 | 61.7 | 65.7 | 70.9 | 75.3 | 77.9 | -
BQ-WP2 | S | 137.5214 |  | 0.97 |  |  | Note 5 | Note 5 | Note 5 | 43.3 | 46.2 | 48.1 | -
| W | 146.8952 |  | 1 |  |  | Note 5 | Note 5 | Note 5 | 25.6 | 27.3 | 28.9 | -
BQ-WP3 | S | 137.5214 |  | 0.97 |  |  | Note 5 | Note 5 | Note 5 | 43.3 | 46.2 | 48.1 | -
| W | 146.8952 |  | 1 |  |  | Note 5 | Note 5 | Note 5 | 25.6 | 27.3 | 28.9 | -
BTS-WP | S | 125.7 |  | 0.97 |  |  | Note 5 | Note 5 | Note 5 | 105.2 | 111.4 | 114 | -
| W | 128 |  | 1 |  |  | Note 5 | Note 5 | Note 5 | 78.1 | 82.9 | 85.9 | -
VM-BQ1 | S | 162.3278 |  | 0.99 |  |  | 48 | 49.4 | 53.1 | 58.3 | 61.8 | 62.7 | -
| W | 173.7593 |  | 0.99 |  |  | 34.5 | 34.9 | 37.6 | 42.1 | 44.6 | 46.2 | -
VM-BQ3 | S | 125.7469 |  | 0.99 |  |  | 47.9 | 49.3 | 53 | 58.2 | 61.6 | 62.6 | -
| W | 128.0332 |  | 0.99 |  |  | 34.5 | 34.9 | 37.6 | 42 | 44.6 | 46.1 | -
WP-MP1 | S | 76.6 |  | 0.97 |  |  | Note 5 | Note 5 | Note 5 | 66.9 | 71 | 73.4 | -
| W | 84.6 |  | 1 |  |  | Note 5 | Note 5 | Note 5 | 45.2 | 48.2 | 50.1 | -
WP-MP2 | S | 82.3 |  | 0.97 |  |  | Note 5 | Note 5 | Note 5 | 66.8 | 70.8 | 73.5 | -
| W | 87.5 |  | 1 |  |  | Note 5 | Note 5 | Note 5 | 45.3 | 48.3 | 50.2 | -
WP-MP3 | S | 76.6 |  | 0.97 |  |  | Note 5 | Note 5 | Note 5 | 66.8 | 71 | 73.3 | -
| W | 84.6 |  | 1 |  |  | Note 5 | Note 5 | Note 5 | 45.2 | 48.1 | 50.1 | -
VM-WA1 | S | 37.7 |  | 0.97 |  |  | 30.5 | 32.8 | 35.5 | 38.7 | 41.1 | 40.7 | -
| W | 40 |  | 1 |  |  | 18.6 | 18.9 | 20.3 | 21.4 | 22.8 | 23.6 | -
VM-WA2 | S | 37.7 |  | 0.97 |  |  | 31.1 | 33.5 | 36.2 | 39.5 | 41.4 | 41.4 | -
| W | 40 |  | 1 |  |  | 18.9 | 19.3 | 20.8 | 21.9 | 23.2 | 24 | -
VM-WA3 | S | 37.7 |  | 0.97 |  |  | 25.8 | 27.9 | 28.9 | 30.3 | 32.2 | 33.3 | -
| W | 40 |  | 1 |  |  | 18.5 | 19.2 | 20.7 | 21.8 | 22.7 | 23.5 | -
FBTS 66kV
FBTS-AP | S | 135.5 |  | 1 |  |  | 86.4 | 86 | 89.2 | 93.5 | 96.2 | 101.1 | -
| W | 137.2 |  | 1 |  |  | 68 | 69.1 | 71.8 | 74.4 | 76.1 | 78.9 | -
FBTS-MG | S | 100.6 |  | 1 |  |  | 86.3 | 85.9 | 88.7 | 93 | 96.1 | 100.6 | -
| W | 125.7 |  | 1 |  |  | 67.8 | 69.2 | 71.8 | 74.6 | 76.4 | 79.1 | -
AP-MG | S | 91.5 |  | 1 |  |  | 50.2 | 51 | 52.4 | 54.4 | 56 | 58.7 | -
| W | 91.5 |  | 1 |  |  | 42.6 | 44 | 45.6 | 47.1 | 47.8 | 49.1 | -
FBTS-E | S | 66.3 |  | 0.93 |  |  | 18.6 | 19.1 | 20 | 21 | 21.6 | 22.7 | -
| W | 86.3 |  | 0.9 |  |  | 17.6 | 17.5 | 18 | 18.4 | 18.9 | 19.4 | -
FBTS-PM | S | 66.3 |  | 0.93 |  |  | 18.6 | 19.2 | 20 | 21 | 21.6 | 22.8 | -
| W | 86.9 |  | 0.9 |  |  | 17.6 | 17.5 | 18 | 18.4 | 18.9 | 19.4 | -
E-PM | S | 74.3 |  | 0.93 |  |  | 15.6 | 15.8 | 16.4 | 17.3 | 17.6 | 18.5 | -
| W | 91.5 |  | 0.9 |  |  | 16.1 | 15.8 | 16.1 | 16.4 | 16.8 | 17.2 | -
FBTS-FB | S | 88 |  | 0.95 |  |  | 73.7 | 76.4 | 88.5 | 94.7 | 99.5 | 104.2 | -
| W | 112 |  | 0.99 |  |  | 32.6 | 84.4 | 92.7 | 111 | 115.8 | 122.3 | -
FBTS-WG | S | 88 |  | 0.95 |  |  | 73.2 | 76 | 89 | 94.6 | 99.4 | 104.6 | -
| W | 112 |  | 0.99 |  |  | 33 | 87.1 | 95.8 | 115.3 | 121.7 | 129.7 | -
FB-WG | S | 89.7 |  | 0.97 |  |  | 54.5 | 54.8 | 63.1 | 68 | 71.3 | 74.8 | -
| W | 94.3 |  | 0.99 |  |  | 29 | 80.5 | 87.3 | 101.9 | 106.1 | 111.4 | -
FBTS-SB | S | 135.5 |  | 0.96 |  |  | 85.3 | 88.9 | 93.8 | 102.3 | 108.9 | 115.1 | -
| W | 142.3 |  | 0.96 |  |  | 57.5 | 61.8 | 64.8 | 68.9 | 73.2 | 77.5 | -
FBTS-SO | S | 109.2 |  | 0.96 |  |  | 85.5 | 89.3 | 94.4 | 102.5 | 109.1 | 115.4 | -
| W | 134.9 |  | 0.96 |  |  | 57.6 | 61.9 | 64.9 | 69 | 73.8 | 77.6 | -
SB-SO | S | 130.3 |  | 0.96 |  |  | 42.3 | 44.5 | 46.8 | 52.7 | 56.6 | 59.8 | -
| W | 137.2 |  | 0.96 |  |  | 30.3 | 33 | 34.4 | 35.9 | 37.2 | 39.3 | -
DLF 22kV
DLF64-TP278 | S | 12.5 |  | 0.98 |  |  | 3.4 | 3.4 | 1 | 1.1 | Note 7 | Note 7 | -
| W | 13.2 |  | 0.99 |  |  | 2.2 | 2.3 | 2.3 | 0.7 | Note 7 | Note 7 | -
DLF5-TP53 | S | 12.5 |  | 0.98 |  |  | 3.4 | 3.4 | 0.7 | 0.7 | Note 7 | Note 7 | -
| W | 13.2 |  | 0.99 |  |  | 2.2 | 2.3 | 2.3 | 0.4 | Note 7 | Note 7 | -
RTS 22kV
RTS-R134 | S | 19.9 |  | 0.952 |  |  | 7.6 | 7.5 | 7.7 | 8.3 | 8.4 | 8.5 | -
| W | 18.8 |  | 0.9234 |  |  | 6.6 | 6.9 | 7 | 7.4 | 7.5 | 7.6 | -
RTS-R135 | S | 16.5 |  | 0.952 |  |  | 13 | 12.7 | 13.2 | 14 | 14.2 | 14.4 | -
| W | 17.1 |  | 0.9234 |  |  | 11.1 | 11.7 | 11.9 | 12.6 | 12.7 | 12.9 | -
RTS-R136 | S | 16.5 |  | 0.952 |  |  | 12.9 | 12.6 | 13 | 13.9 | 14.1 | 14.3 | -
| W | 17.1 |  | 0.9234 |  |  | 11 | 11.6 | 11.8 | 12.5 | 12.6 | 12.8 | -
RTS-RP123 | S | 11.4 |  | 0.90552 |  |  | Note 12 | Note 12 | Note 12 | Note 12 | Note 12 | Note 12 | -
| W | 11.4 |  | 0.85308 |  |  | Note 12 | Note 12 | Note 12 | Note 12 | Note 12 | Note 12 | -
RTS-RP124 | S | 11.4 |  | 0.90552 |  |  | 9.7 | 10.4 | 11.1 | 11.9 | 12.5 | 12.8 | -
| W | 11.4 |  | 0.85308 |  |  | 7 | 6.8 | 7.2 | 7.5 | 8 | 8.3 | -
RTS-RP125 | S | 11.1 |  | 0.90552 |  |  | 9.8 | 10.6 | 11.2 | 12 | 12.8 | 12.9 | -
| W | 11.1 |  | 0.85308 |  |  | 7.1 | 6.9 | 7.2 | 7.6 | 8.1 | 8.4 | -
RTS 66kV
RTS-AR | S | 94.3 |  | 0.89977 |  |  | 88.4 | 72.5 | 73.5 | 78.6 | 80.5 | 81 | -
| W | 123.5 |  | 0.93 |  |  | 77.5 | 79.5 | 80 | 82.1 | 83.9 | 85.8 | -
RTS-TK | S | 116.6 |  | 0.89977 |  |  | 54.5 | 51.7 | 52.9 | 56 | 58.3 | 59.3 | -
| W | 122.3 |  | 0.93 |  |  | 45.8 | 48.1 | 49 | 49.7 | 51.7 | 53.3 | -
RTS-TK/BC | S | 120 |  | 0.89977 |  |  | 105.6 | 94.5 | 97 | 101.8 | 104.7 | 107.6 | -
| W | 120 |  | 0.93 |  |  | 88.9 | 93.7 | 95 | 96.6 | 101 | 102.7 | -
BC-AR | S | 84.6 |  | 0.89977 |  |  | 50.7 | 36.6 | 37 | 39.2 | 40.2 | 40.4 | -
| W | 91.5 |  | 0.93 |  |  | 46.1 | 47.1 | 47.9 | 48.8 | 49.7 | 50.7 | -
BC-TK | S | 84.6 |  | 0.89977 |  |  | 85.4 | 70.5 | 72.6 | 76.9 | 78.5 | 80 | -
| W | 91.5 |  | 0.93 |  |  | 74.2 | 76.1 | 77.3 | 78.5 | 80.5 | 82.9 | -
RTS-CL | S | 135.5 |  | 0.9546 |  |  | 104.3 | 94.4 | 98.3 | 101.8 | 103 | 105.3 | -
| W | 142.3 |  | 0.9685 |  |  | 66.3 | 69.5 | 71.1 | 72.6 | 73.7 | 74.2 | -
CL-K | S | 91.5 |  | 0.9546 |  |  | 58.2 | 53.2 | 56.6 | 60.6 | 61 | 62.7 | -
| W | 91.5 |  | 0.9685 |  |  | 38.4 | 38.3 | 39.4 | 41.5 | 41.9 | 43 | -
RTS-CW | S | 117.2 |  | 0.945 |  |  | 115.7 | 116.7 | 120.2 | 124.3 | 126.6 | 129.1 | -
| W | 142.9 |  | 0.9634 |  |  | 91.1 | 92.8 | 94.8 | 101 | 103.8 | 106.7 | -
RTS-NR | S | 117.2 |  | 0.945 |  |  | 113.4 | 115.6 | 117.8 | 123 | 124.6 | 127 | -
| W | 142.3 |  | 0.9634 |  |  | 90.3 | 90.6 | 93.9 | 100.1 | 102.5 | 105.4 | -
B-CW | S | 85.7 |  | 0.945 |  |  | 82.1 | 82.9 | 85.4 | 88.1 | 89.5 | 91.1 | -
| W | 91.5 |  | 0.9634 |  |  | 65.1 | 70.4 | 70.8 | 72.5 | 75.1 | 77 | -
B-NR | S | 85.7 |  | 0.945 |  |  | 63.1 | 66.8 | 67.6 | 69.7 | 70.3 | 71.9 | -
| W | 91.5 |  | 0.9634 |  |  | 51.4 | 48.3 | 50.9 | 55.5 | 56.1 | 57.9 | -
RTS-SK | S | 98.9 |  | 0.9331 |  |  | 83.5 | 78.4 | 80.3 | 80.5 | 81.4 | 83.1 | -
| W | 106.3 |  | 0.9714 |  |  | 63.6 | 69.3 | 70.7 | 71.3 | 72.5 | 73.2 | -
RTS-FR1 | S | 82.3 |  | 0.96 |  |  | 82.576 | 88.088 | 38.2 | 40 | 42.6 | 43.7 | 7.033% | Energy at Risk (MWh) (N-1 50% PoE) 2019: 124; Hours at Risk (N-1 50% PoE) 2019: 35
| W | 87.5 |  | 0.96 |  |  | 53.663 | 63.654 | 24.2 | 25.7 | 27.4 | 28.8 | -
RTS-FR2 | S | 82.3 |  | 0.96 |  |  | 81.782 | 87.241 | 40.8 | 42.8 | 45.3 | 46.8 | 6.004% | Energy at Risk (MWh) (N-1 50% PoE) 2019: 94; Hours at Risk (N-1 50% PoE) 2019: 30
| W | 87.5 |  | 0.96 |  |  | 53.142 | 63.036 | 26.4 | 28.1 | 29.9 | 31.5 | -
RTS-FR3 | S | 82.3 |  | 0.96 |  |  | 81.7026 | 87.1563 | 40.6 | 42.6 | 45.3 | 46.5 | 5.901% | Energy at Risk (MWh) (N-1 50% PoE) 2019: 94; Hours at Risk (N-1 50% PoE) 2019: 30
| W | 87.5 |  | 0.96 |  |  | 53.142 | 63.036 | 26.3 | 27.9 | 29.8 | 31.3 | -
FR-MP1 | S | 76.6 |  | 0.95541 |  |  | 35 | 35 | 36 | Note 5 | Note 5 | Note 5 | -
| W | 84.6 |  | 0.91558 |  |  | 22 | 28 | 29 | Note 5 | Note 5 | Note 5 | -
FR-WP1 | S | 76.6 |  |  |  |  | Note 5 | Note 5 | Note 5 | 10.3 | 11.1 | 11.4 | -
| W | 84.6 |  |  |  |  | Note 5 | Note 5 | Note 5 | 8.5 | 9.1 | 9.5 | -
FR-MP2 | S | 82.3 |  | 0.95541 |  |  | 35 | 35 | 36 | Note 5 | Note 5 | Note 5 | -
| W | 87.5 |  | 0.91558 |  |  | 22 | 28 | 29 | Note 5 | Note 5 | Note 5 | -
FR-WP2 | S | 82.3 |  |  |  |  | Note 5 | Note 5 | Note 5 | 10.7 | 11.1 | 11.7 | -
| W | 87.5 |  |  |  |  | Note 5 | Note 5 | Note 5 | 8.8 | 9.5 | 9.9 | -
BQ-FR3 | S | 82.3 |  | 0.95541 |  |  | 37 | 38 | 39 | Note 5 | Note 5 | Note 5 | -
| W | 87.5 |  | 0.91558 |  |  | 26 | 29 | 30 | Note 5 | Note 5 | Note 5 | -
FR-WP3 | S | 82.3 |  |  |  |  | Note 5 | Note 5 | Note 5 | 10.9 | 11.6 | 12 | -
| W | 87.5 |  |  |  |  | Note 5 | Note 5 | Note 5 | 9 | 9.7 | 10.1 | -
BQ-MP3 | S | 76.6 |  | 0.95541 |  |  | 37 | 38 | 39 | Note 5 | Note 5 | Note 5 | -
| W | 84.6 |  | 0.91558 |  |  | 26 | 29 | 30 | Note 5 | Note 5 | Note 5 | -
SVTS 66kV
SVTS-RD | S | 116.6 |  | 0.97366 |  |  | 99.5 | 96 | 98.2 | 100.4 | 101.9 | 104.4 | -
| W | 122.3 |  | 0.97366 |  |  | 67.4 | 68 | 68.7 | 69.1 | 69.7 | 69.8 | -
TSTS 66kV
TSTS-L | S | 106.9 |  | 0.97 |  |  | 101.3 | 99.4 | 100.2 | 103.6 | 105.8 | 106.3 | -
| W | 108.6 |  | 0.97 |  |  | 76.4 | 76.2 | 76.1 | 77 | 78.2 | 79.6 | -
HB-Q | S | 95.5 |  | 0.97 |  |  | 74.9 | 72.9 | 73.9 | 76.7 | 78.7 | 78.7 | -
| W | 108.6 |  | 0.97 |  |  | 60.7 | 60.8 | 60.9 | 61.8 | 62.9 | 63.3 | -
Q-L | S | 95.5 |  | 0.97 |  |  | 39.4 | 38.5 | 39.1 | 40.3 | 41.2 | 41.3 | -
| W | 108.6 |  | 0.97 |  |  | 32.4 | 32.7 | 32.8 | 33.2 | 33.6 | 34.1 | -
WMTS 22kV
WMTS-BS216 | S | 21.9 |  | 0.95 |  |  | Note 9 | Note 9 | Note 9 | Note 9 | Note 9 | Note 9
| W | 26.5 |  | 0.98 |  |  | Note 9 | Note 9 | Note 9 | Note 9 | Note 9 | Note 9
WMTS-BS218 | S | 21.9 |  | 0.95 |  |  | Note 10 | Note 9 | Note 9 | Note 9 | Note 9 | Note 9
| W | 26.5 |  | 0.98 |  |  | Note 10 | Note 9 | Note 9 | Note 9 | Note 9 | Note 9
WMTS-DA213 | S | 29.5 |  | 0.95 |  |  | 24.4 | 24.2 | 25.1 | 27.6 | Note 6 | Note 6 | -
| W | 32.4 |  | 0.98 |  |  | 21.5 | 20.8 | 21.4 | 22.6 | Note 6 | Note 6 | -
WMTS-DA222 | S | 29.5 |  | 0.95 |  |  | 24.2 | 24 | 24.9 | 27.6 | Note 6 | Note 6 | -
| W | 32.4 |  | 0.98 |  |  | 21.5 | 20.8 | 21.5 | 22.8 | Note 6 | Note 6 | -
WMTS-J220 | S | 25.5 |  | 0.95 |  |  | 14.7 | 14.4 | Note 7 | Note 7 | Note 7 | Note 7 | -
| W | 26.7 |  | 0.98 |  |  | 12.1 | 12.4 | Note 7 | Note 7 | Note 7 | Note 7 | -
WMTS-LS214 | S | 19.1 |  | 0.95 |  |  | 15.4 | 15 | Note 8 | Note 8 | Note 8 | Note 8 | -
| W | 19.1 |  | 0.98 |  |  | 14.1 | 14.1 | Note 8 | Note 8 | Note 8 | Note 8 | -
WMTS-LS226 | S | 19.1 |  | 0.95 |  |  | 15.3 | 14.9 | Note 8 | Note 8 | Note 8 | Note 8 | -
| W | 19.1 |  | 0.98 |  |  | 12.6 | 12.9 | Note 8 | Note 8 | Note 8 | Note 8 | -
BS-J324 | S | 23.7 |  | 0.95 |  |  | Note 9 | Note 9 | Note 9 | Note 9 | Note 9 | Note 9 | -
| W | 26.7 |  | 0.98 |  |  | Note 9 | Note 9 | Note 9 | Note 9 | Note 9 | Note 9
LS-J325 | S | 21.3 |  | 0.95 |  |  | 1 | 8.2 | Note 7 | Note 7 | Note 7 | Note 7 | -
| W | 25.9 |  | 0.98 |  |  | 1 | 7.4 | Note 7 | Note 7 | Note 7 | Note 7 | -
WMTS 66kV
WMTS-JA1 | S | 145.2 |  | 0.99 |  |  | 76.9 | 78.5 | 85.3 | 93.2 | 99.4 | 105.2 | -
| W | 153.2 |  | 0.99 |  |  | 48.3 | 52.2 | 55.3 | 59.6 | 64 | 67.6 | -
WMTS-JA3 | S | 114.8869 |  | 0.99 |  |  | 70.2 | 72.2 | 77.9 | 84.2 | 89.5 | 94.8 | -
| W | 121.1743 |  | 0.99 |  |  | 44.8 | 48.4 | 51.2 | 55.1 | 58.8 | 62 | -
WMTS-VM1 | S | 130.3195 |  | 0.99 |  |  | 47.7 | 49.4 | 53.3 | 57.1 | 60.7 | 64 | -
| W | 164.6141 |  | 0.99 |  |  | 30.8 | 33.3 | 35.3 | 37.8 | 40.1 | 42 | -
WMTS-VM2 | S | 144.0373 |  | 0.99 |  |  | 35.2 | 36.5 | 39.3 | 42.2 | 44.8 | 47.3 | -
| W | 155.4689 |  | 0.99 |  |  | 22.8 | 24.6 | 26 | 27.9 | 29.6 | 31 | -
WMTS-VM3 | S | 144.0373 |  | 0.99 |  |  | 56.3 | 58.2 | 62.8 | 67.4 | 71.6 | 75.5 | -
| W | 155.4689 |  | 0.99 |  |  | 36.4 | 39.4 | 41.6 | 44.6 | 47.3 | 49.8 | -
VM-LQ1 | S | 76.5913 |  | 0.99 |  |  | 44.3 | 46.3 | 48.6 | 51.6 | 54.3 | 56.2 | -
| W | 86.8797 |  | 0.99 |  |  | 29.8 | 31.9 | 32.9 | 35.4 | 37 | 38.6 | -
VM-LQ3 | S | 76.5913 |  | 0.99 |  |  | 50.2 | 54 | 58.4 | 61.8 | 67 | 69.2 | -
| W | 86.8797 |  | 0.99 |  |  | 34.1 | 38.1 | 40.9 | 43.8 | 45.6 | 47.3 | -
VM-JA | S | 91.4523 |  | 0.99 |  |  | 83.4 | 85.1 | 92 | 100.1 | 106.4 | 112.9 | -
| W | 98.3112 |  | 0.99 |  |  | 52.7 | 56.9 | 60.1 | 64.9 | 69.6 | 73.5 | -
JA-LQ2 | S | 76.5913 |  | 0.99 |  |  | 50.1 | 54 | 58.4 | 61.9 | 67.2 | 69.2 | -
| W | 86.8797 |  | 0.99 |  |  | 34.1 | 38.2 | 41 | 43.8 | 45.7 | 47.4 | -
JA-WP | S | 120.5 |  | 0.99 |  |  | Note 5 | Note 5 | Note 5 | 0 | 0 | 0 | -
| W | 128 |  | 0.99 |  |  | Note 5 | Note 5 | Note 5 | 0 | 0 | 0 | -
WMTS-NC | S | 54.8714 |  | 0.98 |  |  | 55.7 | 49.2 | 49.5 | 52.4 | 54.1 | 54.9 | -
| W | 70.3039 |  | 0.99 |  |  | 50.5 | 51.1 | 52.2 | 53.2 | 54.6 | 55.8 | -
WMTS-WB | S | 54.9 |  | 0.98 |  |  | 55.9 | 49.6 | 49.9 | 52.4 | 54.2 | 55.1 | -
| W | 70.3039 |  | 0.99 |  |  | 50.9 | 51.5 | 52.6 | 53.6 | 55.1 | 56.3 | -
NC-WB | S | 74.305 |  | 0.98 |  |  | 31.7 | 27.9 | 28 | 29.4 | 30.4 | 30.7 | -
| W | 97.1681 |  | 0.99 |  |  | 28.4 | 28.7 | 28.9 | 29.4 | 30.2 | 30.8 | -
Note 1: Generation capacity is specified at the location (sub-transmission line/ loop) where the generation is connected to the network.
Note 2: The 2015 demand figures are actuals for summer and forecast for winter.
Note 3: Forecast demand worst case N-1 scenario refers to the expected load that the sub-transmission line would supply in the event of the worst case outage of a sub-transmission line within the loop system.
Note 4: Tx 2 failed during summer 2016/17 and sub trans cable out of service.
Note 5: Cut in of New WP requires new BTS-WP & JA-WP and creates new WP-MP1, 2 & 3 and FR-WP1, 2 & 3 from FR-MP1 & 2 and BQ-MP3; and also creates new BQ-WP2 & 3 from BQ-FR3 and BQ-MP3
Note 6: DA transffered to WMTS66
Note 7: Offloaded to JA
Note 8: Offloaded to BQ
Note 9: WMTS-BS216 & 218 to be used for supply new HV customer. J-LS cable to be retired
Note 10: Cable faulted 12/2016
Note: 11 Cable Faulted 2017
Note: 12 Cable out of service