## Zone Substations
Zone Substation |  | On-load Capacity - Nameplate Rating (MVA) | Hot or Cold Spare Capacity - Nameplate Rating (MVA) (note 1) | Total Capacity - Nameplate Rating (MVA) | Cyclic N-1 Rating (MVA) | Hours Load is ≥ 95% of MD (note 4) | Station Power Factor at MD | Load Transfers (MVA) | Generation Capacity <1MW (MW) (notes 2 & 6) | Generation Capacity >1MW (1MW) (note 2) | Actual Demand (MVA) (note 3) | 50% PoE Forecast Demand (MVA) |  |  |  |  | % Load Above N-1 Rating (2019) | Energy at Risk (MWh) (N-1 50% PoE) |  |  |  |  | Hours at Risk (N-1 50% PoE)
[11 empty] | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2019 | 2020 | 2021 | 2022 | 2023
ATS 66kV
LV | S | 99 |  | 99 | 79.8 | 4 | 0.98362 | 18.8 | 20.9 | - | 104.95 | 107.8 | 114.5 | 124.1 | 130.6 | 128.6 | 35.09% | 608 | 1032 | 1881 | 2613 | 2375 | 66 | 91 | 136 | 170 | 159
| W | 99 |  | 99 | 95.4 | 4 | 0.99166 | 35 | 20.9 | - | 78.34 | 71.8 | 76.1 | 81.2 | 82.7 | 83 | -
WBE | S | 99 |  | 99 | 82.8 | 4 | 0.99121 | 19.8 | 16.8 | 11.7 | 108.85 | 111.2 | 118.1 | 128.6 | 136.7 | 144.9 | 34.3% | 727 | 1196 | 2190 | 3188 | 4561 | 73 | 98 | 146 | 197 | 301
| W | 99 |  | 99 | 92.2 | 7 | 0.99126 | 40.8 | 16.8 | 11.7 | 73.52 | 84.9 | 90.5 | 95.2 | 100.7 | 106.7 | -
ATS/BLTS 66kV
AC | S | 40 |  | 40 | 30 | - | 0.95 | - | - | - | 1.96 | 2.7 | 2.5 | 2.8 | 2.9 | 2.9 | -
| W | 40 |  | 40 | 30 | - | 0.91304 | - | - | - | 2.31 | 2.3 | 2.3 | 2.2 | 2.3 | 2.3 | -
AL | S | 30 |  | 30 | 0 | 4 | 1 | 30.4 | 2.5 | - | 20.18 | 18.3 | 18.5 | 19.1 | 19.3 | 19.5 | 100% | 48517 | 50859 | 51606 | 52345 | 53704 | 8760 | 8760 | 8760 | 8760 | 8760
| W | 30 |  | 30 | 0 | - | 1 | 33 | 2.5 | - | 17.87 | 15.7 | 16 | 16.2 | 16.3 | 16.6 | 100%
BMH | S | 27 |  | 27 | 19.1 | 4 | 1 | 3.2 | 6.6 | - | 31.09 | 27.2 | 28.8 | 30.5 | 32.3 | 33.9 | 42.41% | 292 | 513 | 825 | 1342 | 2045 | 125 | 219 | 355 | 543 | 783
| W | 27 |  | 27 | 20.1 | 13 | 1 | 7.5 | 6.6 | - | 24.13 | 20.9 | 22.2 | 23.2 | 24.4 | 25.7 | 3.98%
LVN11 | S | 30 |  | 30 | 0 | 808 | 0.992 | 1.5 | - | - | 12.5 | 12.7188 | 12.9231 | 12.7956 | 12.663 | 12.6773 | 100%
| W | 30 |  | 30 | 0 | 312 | 0.992 | 1.5 | - | - | 12.5 | 13.1279 | 12.996 | 12.9119 | 13.0364 | 12.9253 | 100%
LVN22 | S | 99 |  | 99 | 79.7 | - | 0.99748 | - | 1.5 | - | 67.64 | 64.9702 | 66.1383 | 66.7666 | 67.3873 |  | -
| W | 99 |  | 99 | 85 | - | 0.99729 | - | 1.5 | - | 76.93 | 65.4963 | 62.4381 | 63.5521 | 64.0824 |  | -
BATS 66kV
ART | S | 20 |  | 20 | 13.6 | 4 | 0.98765 | 5 | 2.4 | 6.8 | 15.85 | 15.2697 | 15.3082 | 14.9694 | 14.9751 | 14.9184 | 12.28% | 16 | 14 | 10 | 9 | 8 | 22 | 20 | 16 | 16 | 15
| W | 20 |  | 20 | 15.2 | 4 | 0.99281 | 5.3 | 2.4 | - | 14.16 | 11.7446 | 11.7337 | 11.6788 | 11.6671 | 11.6695 | -
BAN | S | 120 |  | 120 | 96.4 | - | 0.99048 | - | 13.1 | 6.1 | 83.81 | 71.35 | 73.094 | 75.4952 | 77.6174 | 78.5985 | -
| W | 120 |  | 120 | 104.4 | - | 0.99613 | - | 13.1 | 6.1 | 73.45 | 76.2044 | 77.7538 | 80.0922 | 81.5827 | 83.1542 | -
BAS | S | 99 |  | 99 | 76 | 4 | 0.97324 | 15.3084 | 14.6 | 7.2 | 75.59 | 65.2255 | 67.4668 | 71.7213 | 73.6784 | 74.5661 | -
| W | 99 |  | 99 | 84.6 | 9 | 0.98348 | 20.3366 | 14.6 | 7.2 | 65.42 | 68.7372 | 70.9407 | 72.7136 | 74.332 | 75.9505 | -
BETS 66kV
BGO | S | 66 |  | 66 | 38.5 | 5 | 1 | 13.9 | 7.6 | - | 46.05 | 45.8225 | 47.3319 | 51.017 | 52.2554 | 53.0105 | 19.02% | 99 | 161 | 356 | 413 | 487 | 37 | 52 | 92 | 101 | 113
| W | 66 |  | 66 | 45.4 | 9 | 1 | 14.7 | 7.6 | - | 33.6 | 35.2973 | 38.1107 | 39.9688 | 40.4189 | 41.0436 | -
CMN | S | 66 |  | 66 | 43 | - | 0.98893 | - | 8 | - | 28.55 | 29.8544 | 30.4047 | 31.167 | 31.9299 | 31.9804 | -
| W | 66 |  | 66 | 49.5 | - | 0.93305 | - | 8 | - | 23.9 | 22.1694 | 22.503 | 22.9276 | 23.2166 | 23.2283 | -
CTN | S | 39.5 |  | 39.5 | 33.7 | - | 0.99537 | - | 4.2 | - | 20.01 | 22.0913 | 22.1574 | 22.3745 | 21.4928 | 21.1857 | -
| W | 39.5 |  | 39.5 | 38.4 | - | 0.9596 | - | 4.2 | - | 20.14 | 18.3261 | 18.2098 | 18.0967 | 17.969 | 17.8878 | -
EHK | S | 54 |  | 54 | 36.4 | 4 | 0.99629 | 16.1 | 8.8 |  | 52.04 | 50.4687 | 50.7882 | 53.6334 | 55.0162 | 56.2044 | 38.65% | 843 | 894 | 1437 | 1759 | 2069 | 184 | 193 | 270 | 309 | 348
| W | 54 |  | 54 | 41 | 3 | 0.99744 | 15.8 | 8.8 | - | 38.95 | 38.9943 | 39.7152 | 41.127 | 42.0979 | 43.1646 | -
MRO | S | 27 |  | 27 | 18.3 | 6 | 1 | 3.9 | 5.7 | - | 21.74 | 21.2626 | 21.3452 | 22.3242 | 22.597 | 22.6061 | 16.19% | 35 | 38 | 71 | 84 | 86 | 32 | 33 | 53 | 59 | 60
| W | 27 |  | 27 | 20.2 | 4 | 0.99454 | 3.4 | 5.7 | - | 18.32 | 16.7491 | 16.8663 | 16.9572 | 16.9775 | 16.9997 | -
DPTS 66kV
MLN | S | 99 |  | 99 | 79.8 | 5 | 0.97518 | 4.4 | 13.3 | - | 56.8 | 66.2491 | 71.2769 | 76.587 | 80.8888 | 84.8411 | -
| W | 99 |  | 99 | 87.6 | 11 | 1 | 12.8 | 13.3 | - | 41.32 | 47.9952 | 50.7627 | 52.8023 | 55.5759 | 58.9145 | -
SU | S | 99 |  | 99 | 93 | 7 | 0.99884 | 53.2 | 11.9 | - | 85.02 | 86.4 | 95.1 | 103.8 | 106.1 | 107.6 | -
| W | 99 |  | 99 | 99 | 4 | 1 | 71.2 | 11.9 | - | 67.28 | 78.4 | 86.7 | 88.4 | 89.8 | 91.4 | -
TNA | S | 66 |  | 66 | 47.6 | 7 | 0.95152 | 52.2 | 10.6 | 8.8 | 22.9772 | 46.8 | 50.3 | 56.9 | 60.6 | 73 | - | 0 | 9 | 109.96 | 252.79 | 2772.311 | 0 | 7.5 | 32.5 | 595 | 621.75
| W | 66 |  | 66 | 47.6 | 4 | 0.96355 | 50.9 | 10.6 | 8.8 | Note 7 | 45.313 | 48.1827 | 54.9105 | 56.9995 | 69.0056 | -
FBTS 66kV
DLF | S | 66 |  | 66 | 40 | - | 0.96316 | - | - | - | 18.81 | 18.5958 | 16.5818 | 17.6617 | 18.6591 | 19.7373 | -
| W | 66 |  | 66 | 46.2 | - | 0.98496 | - | - | - | 13.5 | 13.3388 | 12.6968 | 13.3633 | 14.0743 | 14.7674 | -
GTS 66kV
CLC | S | 79 |  | 79 | 50.4 | - | 1 | - | 5.3 | 2.9 | 42.86 | 38.7046 | 38.7614 | 39.0072 | 39.4373 | 39.5436 | -
| W | 79 |  | 79 | 56.1 | - | 1 | - | 5.3 | 2.9 | 43.75 | 35.3568 | 35.4014 | 35.5348 | 35.4751 | 35.6016 | -
CRO | S | 60 |  | 60 | 34.3 | 3 | 0.92982 | 20.1 | 4 | - | 28.61 | 29.6482 | 30.2584 | 31.3546 | 31.5798 | 31.1454 | -
| W | 60 |  | 60 | 38 | 11 | 0.99 | 20.1 | 4 | - | 25.35 | 27.3292 | 27.5064 | 27.7728 | 27.7988 | 27.8461 | -
DDL | S | 66 |  | 66 | 39.7 | 2 | 0.98778 | 4.4 | 13.7 | - | 67.17 | 63 | 65.6 | 65.2 | 65.7 | 72.7 | 58.69% | 291 | 370 | 354 | 388 | 670 | 36 | 43 | 42 | 47 | 80
| W | 66 |  | 66 | 47.2 | 3 | 0.99737 | 8 | 13.7 | - | 39.4 | 42.4 | 44.4 | 46.8 | 48.9 | 51.3 | -
FNS | S | 99 |  | 99 | 87.2 | - | 0.99704 | - | 5.9 | 1 | 35.76 | 52.8684 | 55.2143 | 58.8058 | 59.5367 | 60.0956 | -
| W | 99 |  | 99 | 98.6 | - | 0.99707 | - | 5.9 | 1 | 29.3 | 53.6444 | 56.3084 | 55.4402 | 55.8906 | 56.5444 | -
GB | S | 37.5 |  | 37.5 | 37.6 | - | 0.98551 | - | 0.8 | - | 11.4 | 12.3451 | 12.4347 | 12.2281 | 12.64 | 12.5292 | -
| W | 37.5 |  | 37.5 | 37.6 | - | 0.99219 | - | 0.8 | - | 12.74 | 12.7533 | 12.9757 | 12.9146 | 13.1608 | 13.2976 | -
GCY | S | 66 |  | 66 | 37.8 | 5 | 0.93126 | 15.9 | 2.8 | 5.5 | 46.2 | 49.8788 | 51.0041 | 52.4412 | 54.2351 | 55.0639 | 31.95% | 359 | 455 | 602 | 833 | 961 | 65 | 80 | 103 | 134 | 153
| W | 66 |  | 66 | 43.9 | 6 | 0.89197 | 15 | 2.8 | 5.5 | 31.88 | 34.9336 | 35.6874 | 36.7217 | 37.1906 | 37.611 | -
GL | S | 80 |  | 80 | 47.6 | 3 | 0.99461 | 11.9 | 9.5 | - | 64.57 | 60.3031 | 62.7225 | 66.8053 | 68.5395 | 69.4082 | 26.69% | 128 | 248 | 423 | 506 | 592 | 29 | 65 | 92 | 105 | 122
| W | 80 |  | 80 | 47.6 | 5 | 1 | 21.9 | 9.5 | - | 47.61 | 49.8451 | 53.7836 | 54.7916 | 55.3265 | 55.9684 | 4.717%
GLE | S | 79.5 |  | 79.5 | 66.9 | - | 0.98044 | - | 7.1 | 1.2 | 52.51 | 46.9319 | 48.3941 | 50.828 | 52.6238 | 52.6278 | -
| W | 79.5 |  | 79.5 | 68.8 | - | 1 | - | 7.1 | 1.2 | 39.84 | 41.8253 | 42.658 | 43.6691 | 44.0829 | 44.8556 | -
WIN | S | 13.5 | 7 | 20.5 | 10.5 | - | 0.97059 | - | 2 | - | 8.31 | 8.6521 | 8.9856 | 8.375 | 8.203 | 8.2961 | -
| W | 13.5 | 7 | 20.5 | 10.5 | - | 0.96552 | - | 2 | - | 8.58 | 8.0146 | 8.1638 | 8.3307 | 8.4377 | 8.6089 | -
WPD | S | 79.5 |  | 79.5 | 56.8 | 3 | 0.99879 | 9.5 | 15 | - | 80.66 | 83.4 | 86.4 | 88.2 | 91.1 | 97.3 | 46.83% | 302 | 426 | 519 | 744 | 1284 | 37 | 55 | 73 | 119 | 213
| W | 79.5 |  | 79.5 | 62.6 | 4 | 1 | 19.8 | 15 | - | 66.8 | 64.2 | 67.3 | 68.9 | 72.2 | 75.4 | 2.556%
HOTS 66kV | [5 empty] | -
CHM | S | 33 |  | 33 | 0 | 3 | 1 | 1.1 | 0.5 | - | 2.9661 | 2.3852 | 2.3575 | 2.3141 | 2.2702 | 2.2445 | 100% | 8071 | 7965 | 7871 | 7728 | 7608 | 8760 | 8760 | 8760 | 8760 | 8760
| W | 33 |  | 33 | 0 | 5 | 0.99143 | 1.3 | 0.5 | - | 2.979 | 2.7249 | 2.7102 | 2.6776 | 2.6252 | 2.5891 | 100%
HSM | S | 40.5 |  | 40.5 | 39.7 | 5 | 0.99546 | 4 | 8.7 | - | 41.85 | 43.9466 | 44.1708 | 46.0481 | 45.8095 | 45.949 | 10.7% | 37 | 43 | 89 | 87 | 85 | 20 | 22 | 36 | 35 | 34
| W | 40.5 |  | 40.5 | 40.4 | 3 | 1 | 4 | 8.7 | - | 36.72 | 31.893 | 32.2934 | 32.3665 | 32.3907 | 32.469 | -
NHL | S | 20 |  | 20 | 13 | - | 0.99153 | - | 2.1 | - | 11.26 | 12.0006 | 12.0604 | 12.0292 | 11.8697 | 11.9124 | -
| W | 20 |  | 20 | 16.2 | - | 0.98095 | - | 2.1 | - | 10.3 | 9.0178 | 8.9692 | 8.8478 | 8.7331 | 8.6457 | -
STL | S | 27 |  | 27 | 18.5 | 9 | 0.96951 | 4.5 | 2.8 | - | 15.71 | 16.1171 | 16.4304 | 15.9893 | 15.701 | 15.6609 | -
| W | 27 |  | 27 | 18.8 | 7 | 0.98953 | 4.5 | 2.8 | - | 15.08 | 19.2955 | 19.0939 | 18.6054 | 18.6979 | 18.552 | 2.636%
KGTS 66kV
CHA | S | 27 |  | 27 | 15.2 | 5 | 0.99338 | 0.3 | 2.8 | - | 15.04 | 13.5168 | 13.563 | 13.1747 | 12.9614 | 12.7967 | -
| W | 27 |  | 27 | 15.2 | 6 | 0.99375 | 0.3 | 2.8 | - | 15.44 | 14.3237 | 14.3923 | 14.3331 | 14.2375 | 14.1835 | -
SHL | S | 40.5 |  | 40.5 | 36.7 | 8 | 1 | 0.8 | 6.1 | - | 38.007 | 38.8273 | 39.0469 | 39.4004 | 38.7693 | 38.4793 | 5.797% | 9 | 14 | 14 | 10 | 6 | 10 | 13 | 13 | 11 | 8
| W | 40.5 |  | 40.5 | 40.4 | 4 | 0.97749 | 1.7 | 6.1 | - | 30.82 | 29.7507 | 29.8944 | 29.88 | 29.9836 | 30.1345 | -
KTS 66kV
GSB | S | 66 |  | 66 | 49.5 | - | 1 | - | 5.4 | - | 21.3 | 22.2065 | 22.9344 | 23.1562 | 23.6307 | 24.3929 | -
| W | 66 |  | 66 | 49.5 | - | 1 | - | 5.4 | - | 23.9 | 21.2078 | 21.7052 | 22.3955 | 22.761 | 23.2925 | -
SA | S | 93 |  | 93 | 76.2 | 5 | 0.99492 | 11.9 | 13.8 | - | 85.14 | 84.1703 | 85.8095 | 86.6589 | 87.7383 | 88.9496 | 10.46% | 21 | 37 | 50 | 67 | 88 | 8 | 11 | 13 | 16 | 18
| W | 93 |  | 93 | 76.2 | 10 | 0.99837 | 22.5 | 13.8 | - | 61.47 | 56.6181 | 58.0159 | 59.1949 | 59.6854 | 61.127 | -
SSE | S | 99 |  | 99 | 89.7 | - | 0.92006 | - | 6.3 | - | 73.01 | 68.6419 | 70.9255 | 71.9614 | 72.3045 | 74.8647 | -
| W | 99 |  | 99 | 99 | - | 0.92879 | - | 6.3 | - | 62.56 | 64.3702 | 65.1864 | 66.2962 | 67.1359 | 67.6019 | -
SU | S | 99 |  | 99 | 93 | 7 | 0.99884 | 53.2 | 11.9 | - | 85.02 | 79.3841 | 80.6178 | 86.6464 | 89.056 | 90.7446 | -
| W | 99 |  | 99 | 99 | 4 | 1 | 71.2 | 11.9 | - | 67.28 | 60.4886 | 62.2682 | 64.037 | 65.3139 | 66.8507 | -
WND | S | 66 |  | 66 | 38.3 | - | 0.99571 | - | 8.5 | - | 25.74 | 23.3435 | 24.0402 | 25.0419 | 25.5883 | 26.2288 | -
| W | 66 |  | 66 | 43.2 | - | 1 | - | 8.5 | - | 23.7838 | 27.7232 | 28.1956 | 28.8832 | 29.3344 | 29.9489 | -
RCTS 66kV
BBD | S | 66 |  | 66 | 47.2 | - | 0.99291 | - | 0.2 | - | 27.7 | 30.2246 | 29.8835 | 29.2737 | 29.2683 | 27.9547 | -
| W | 66 |  | 66 | 50 | - | 0.99265 | - | 0.2 | - | 11.1 | 9.7923 | 9.5701 | 9.4213 | 9.7205 | 9.6017 | -
MBN | S | 59 |  | 59 | 37.6 | 7 | 0.9976 | 22.4 | 5.7 | - | 40.95 | 44.8732 | 45.2917 | 45.5117 | 45.6726 | 46.0289 | 19.34% | 173 | 199 | 208 | 219 | 249 | 65 | 71 | 73 | 76 | 84
| W | 59 |  | 59 | 40.8 | 5 | 0.99617 | 20.6 | 5.7 | - | 27.34 | 30.1177 | 30.5924 | 31.3269 | 31.5168 | 31.8694 | -
MDA | S | 66 |  | 66 | 39.7 | 9 | 0.95257 | 14.9 | 5.6 | - | 46.3 | 41.4982 | 42.0907 | 42.0491 | 42.603 | 42.3852 | 4.53% | 2 | 8 | 6 | 10 | 9 | 5 | 9 | 8 | 11 | 10
| W | 66 |  | 66 | 44.6 | 3 | 0.97619 | 19.7 | 5.6 | - | 34.26 | 36.3184 | 37.0018 | 36.7147 | 37.2972 | 37.6233 | -
SHTS 66kV
CME | S | 40.5 |  | 40.5 | 32.7 | 5 | 0.99974 | 0 | 6.9 | 9.45 | 35.41 | 34.3188 | 34.5004 | 35.0136 | 36.2216 | 35.9796 | 4.95% | 1 | 2 | 6 | 19 | 15 | 3 | 4 | 8 | 16 | 14
| W | 40.5 |  | 40.5 | 39.2 | 7 | 1 | 0 | 6.9 | 9.45 | 26.14 | 25.6683 | 25.9899 | 25.3781 | 25.5202 | 25.968 | -
ECA | S | 39.5 |  | 39.5 | 34.6 | - | 1 | - | 7.4 | - | 32.7 | 34.1361 | 35.5874 | 34.188 | 33.669 | 33.8541 | -
| W | 39.5 |  | 39.5 | 40.4 | - | 0.99644 | - | 7.4 | - | 26.16 | 25.6621 | 26.1276 | 26.2196 | 26.3907 | 26.653 | -
KYM | S | 40.5 |  | 40.5 | 33.8 | - | 0.99661 | - | 6.5 | - | 28.06 | 28.3069 | 28.326 | 29.9306 | 29.5657 | 29.4374 | -
| W | 40.5 |  | 40.5 | 38.8 | - | 0.9789 | - | 6.5 | - | 23.09 | 21.7038 | 21.9892 | 21.8457 | 21.923 | 22.0456 | -
MNA | S | 66 |  | 66 | 37 | 2 | 0.98345 | 7.3162 | 5.9 | 1 | 39.73 | 42.7575 | 43.3447 | 45.4117 | 46.1557 | 46.1625 | 15.56% | 89 | 116 | 256 | 324 | 324 | 44 | 53 | 92 | 108 | 108
| W | 66 |  | 66 | 42.5 | 11 | 1 | 7.3162 | 5.9 | 1 | 29.38 | 27.5414 | 27.9776 | 28.2183 | 28.5103 | 28.8994 | -
NKA | S | 39.5 |  | 39.5 | 30.5 | 6 | 0.97595 | 1.8 | 6.5 | - | 29.6 | 29.352 | 29.4073 | 29.4763 | 29.146 | 29.1968 | -
| W | 39.5 |  | 39.5 | 30.5 | 7 | 0.99291 | 0 | 6.5 | - | 27.04 | 26.6253 | 26.952 | 27.4098 | 27.3643 | 27.6158 | -
SHN | S | 66 |  | 66 | 40 | - | 0.9973 | - | 5.9 | 1 | 34.881 | 35.4157 | 36.2204 | 36.2777 | 36.4378 | 36.5828 | -
| W | 66 |  | 66 | 44.1 | - | 0.99617 | - | 5.9 | 1 | 26.139 | 24.8316 | 25.2831 | 25.3158 | 25.6973 | 25.954 | -
SHP | S | 66 |  | 66 | 36.6 | - | 0.94681 | - | 3.4 | - | 23.7 | 21.1476 | 22.5677 | 27.0943 | 27.06 | 27.0112 | -
| W | 66 |  | 66 | 41.9 | - | 1 | - | 3.4 | - | 17.35 | 16.3209 | 19.3062 | 19.5185 | 19.3962 | 19.4769 | -
STN | S | 79 |  | 79 | 61.9 | - | 0.99789 | - | 7.5 | - | 50.66 | 47.4641 | 48.6041 | 51.9396 | 53.006 | 53.9711 | -
| W | 79 |  | 79 | 61.9 | - | 0.98485 | - | 7.5 | - | 36.15 | 31.2284 | 32.9411 | 33.7822 | 34.258 | 34.6724 | -
TGTS 66kV
CDN | S | 20 |  | 20 | 17.2 | - | 0.9875 | - | 1.9 | - | 15.18 | 13.8993 | 13.9833 | 14.3861 | 14.6443 | 14.58 | -
| W | 20 |  | 20 | 18.2 | - | 0.98378 | - | 1.9 | - | 17.51 | 16.7318 | 16.7911 | 16.7758 | 16.6934 | 16.6217 | -
COB | S | 26 |  | 26 | 15 | 9 | 0.88489 | 5 | 0.1 | - | 14.75 | 13.5337 | 13.5967 | 13.532 | 13.3955 | 13.2213 | -
| W | 26 |  | 26 | 15 | 7 | 0.91558 | 5 | 0.1 | - | 14.22 | 13.4395 | 13.2765 | 13.2262 | 13.1258 | 13.0971 | -
HTN | S | 39.5 |  | 39.5 | 34.2 | - | 1 | - | 2.7 | - | 28.94 | 28.4473 | 29.225 | 28.5661 | 27.6539 | 27.5559 | -
| W | 39.5 |  | 39.5 | 38.4 | - | 1 | - | 3.4 | - | 31.79 | 28.3539 | 28.3761 | 28.7869 | 28.663 | 28.6674 | -
KRT | S | 40.5 |  | 40.5 | 33.4 | - | 0.99623 | - | 2.6 | - | 22.67 | 25.9871 | 26.1506 | 26.4277 | 26.0995 | 26.3576 | -
| W | 40.5 |  | 40.5 | 37.6 | - | 0.99635 | - | 2.6 | - | 25.6 | 26.5648 | 27.0017 | 26.4896 | 26.6991 | 26.7418 | -
PLD | S | 32 |  | 32 | 22.1 | - | 1 | - | 3.6 | - | 17.37 | 16.6568 | 16.4867 | 16.6127 | 16.8459 | 16.6674 | -
| W | 32 |  | 32 | 24 | - | 1 | - | 3.6 | - | 19.85 | 19.4185 | 19.5701 | 19.2429 | 19.2144 | 19.214 | -
TRG | S | 27 |  | 27 | 19.2 | 7 | 0.99573 | 11.1 | 2.2 | - | 20.21 | 20.307 | 20.255 | 20.2276 | 20.2534 | 20.1431 | 5.765% | 223 | 226 | 217 | 209 | 209 | 149 | 151 | 150 | 147 | 146
| W | 27 |  | 27 | 19.4 | 7 | 0.99608 | 11.4 | 2.2 | - | 25.92 | 23.6459 | 23.7181 | 23.6718 | 23.5476 | 23.5475 | 21.89%
WBL | S | 60 |  | 60 | 38.2 | 3 | 0.99216 | 12.3 | 4.7 | 1.5 | 50.15 | 52.4171 | 53.043 | 55.4427 | 56.5568 | 56.3521 | 37.22% | 466 | 550 | 964 | 1248 | 1218 | 121 | 148 | 264 | 350 | 342
| W | 60 |  | 60 | 42.2 | 4 | 0.99783 | 12.1 | 4.7 | 1.5 | 46.88 | 42.7733 | 43.6036 | 44.3217 | 44.7332 | 45.2039 | 1.358%
WETS 66kV
OYN | S | 27 |  | 27 | 15.2 | - | 0.93103 | - | 1.6 | - | 8.59 | 7.8143 | 7.6981 | 7.9835 | 7.9361 | 7.8927 | -
| W | 27 |  | 27 | 15.2 | - | 0.8913 | - | 1.6 | - | 9.16 | 8.3731 | 8.3181 | 8.2539 | 8.1629 | 8.0846 | -
RVL | S | 19.5 |  | 19.5 | 20.4 | - | 1 | - | 0.8 | - | 21.75 | 20.5715 | 20.6688 | 21.5721 | 21.6888 | 21.3451 | 0.8406%
| W | 19.5 |  | 19.5 | 22.9 | - | 0.96471 | - | 0.8 | - | 10.11 | 10.2715 | 10.4904 | 10.3724 | 10.31 | 10.3261 | -
WMN | S | 33 | 13.5 | 46.5 | 17.2 | 11 | 0.98413 | 1.5 | 0.05 | - | 20.99 | 19.3796 | 19.342 | 18.8069 | 18.4085 | 18.2493 | 12.67% | 235 | 255 | 228 | 326 | 297 | 302 | 319 | 295 | 376 | 353
| W | 33 | 13.5 | 46.5 | 20.2 | 3 | 0.96429 | 5.3 | 0.05 | - | 11.99 | 8.8367 | 8.9023 | 8.8446 | 8.7371 | 8.7568 | -
Note 1: * indicates cold standby transformer
Note 2: Generation capacity <1MW is mostly solar PV
Note 3: The 2017 demand figures are actuals for summer and forecast for winter.
Note 4: Where load is above N-1 rating
Note 5: Supplied from DPTS from late 2017
Note 6: TNA generation <1MW based on load transfers to TNA
Note 6: TNA not commissioned in winter 2017

## Subtransmission lines
Subtransmission line |  | Line Rating (MVA) | Hours Load is 95% of MD | Power Factor at MD | Load Transfers (MVA) | Generation Capacity (MW) | Historical Demand Worst case N-1 Scenario (MVA) | Forecast Demand Worst case N-1 Scenario (MVA) |  |  |  |  | % Load Above N-1 Rating (2019) | Energy at Risk (MWh) (N-1 50% PoE) |  |  |  |  | Hours at Risk (N-1 50% PoE)
[7 empty] | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2019 | 2020 | 2021 | 2022 | 2023
ATS 66kV
ATS-HCP | S | 109.7 | 4 | 0.95 | 19.8 |  | 115.2 | 116.5 | 125.5 | 138.8 | 148.5 | 158.4 | 6.199% | 33 | 109 | 358 | 645 | 1040 | 5 | 14 | 27 | 39 | 52
| W | 134.9 | 4 | 0.98 | 40.8 |  | 72.1 | 92.2 | 98.9 | 103.9 | 111 | 119 | -
ATS-WBE | S | 109.7 | 4 | 0.95 | 19.8 |  | 115.3 | 116.6 | 125.6 | 138.9 | 150.2 | 158.5 | 6.29% | 33 | 110 | 360 | 706 | 1044 | 5 | 14 | 27 | 41 | 53
| W | 134.9 | 4 | 0.98 | 40.8 |  | 72.1 | 92.3 | 99 | 104 | 111.1 | 119.1 | -
HCP-WBE | S | 109.7 | 4 | 0.95 | 19.8 |  | 103.4 | 105.6 | 113.7 | 124.7 | 132.9 | 140.9 | -
| W | 134.9 | 4 | 0.98 | 40.8 |  | 65.7 | 83.6 | 89.6 | 94.1 | 100.3 | 107.1 | -
ATS-LV1 | S | 135.5 |  | 0.94 |  |  | 105.9 | 116 | 124 | 136.3 | 143.3 | 140.8 | -
| W | 142.3 |  | 0.96 |  |  | 68.3 | 74.1 | 79.2 | 84.6 | 86.2 | 86.5 | -
ATS-LV2 | S | 135.5 |  | 0.94 |  |  | 106 | 117.3 | 125.5 | 137.9 | 146.8 | 142.5 | -
| W | 142.3 |  | 0.96 |  |  | 69 | 74.9 | 79.3 | 85.5 | 87.2 | 87.5 | -
ATS/BLTS 66kV
ATS-AC | S | 102.3 |  | 0.97 |  |  | 28.7 | 26.7 | 26.1 | 26.8 | 27.5 | 26.8 | -
| W | 108 |  | 0.98 |  |  | 25.3 | 23.9 | 23.6 | 23.5 | 23.7 | 24.5 | -
AC-CPL | S | 102.9 |  | 0.97 |  | 22.5 | 27.7 | 25.6 | 25.1 | 25.7 | 26.4 | 25.7 | -
| W | 108 |  | 0.98 |  | 22.5 | 24.4 | 23 | 22.7 | 22.6 | 22.8 | 23.5 | -
CPL-AL | S | 91.5 |  | 0.98 |  | 22.5 | 21.8 | 21 | 20.8 | 21.6 | 22 | 21.4 | -
| W | 91.5 |  | 0.98 |  | 22.5 | 20.1 | 20.9 | 21.1 | 21.3 | 20.4 | 20.1 | -
AL-BLTS | S | 91.5 |  | 0.97 |  |  | 17.2 | 15.7 | 15.5 | 15.9 | 16.1 | 16 | -
| W | 91.5 |  | 0.98 |  |  | 15.7 | 14.6 | 14.1 | 13.8 | 13.2 | 13.7 | -
ATS-ATD | S | 101.7407 |  | 0.95 |  |  | Note 8 | 8.2 | 7.9 | 11.3 | 13.5 | 15.2 | -
| W | 122.3174 |  | 0.95 |  |  | Note 8 | 9.8 | 13.3 | 16.6 | 14.6 | 17.5 | -
BLTS-ATD | S | 97.1681 |  | 0.95 |  |  | Note 8 | 8.1 | 7.9 | 8.7 | 9.9 | 13.8 | -
| W | 125.7469 |  | 0.95 |  |  | Note 8 | 11.5 | 13.4 | 16.7 | 14.7 | 17.6 | -
ATS-LVN | S | 109.7 |  | 0.96 |  |  | 79.8 | 78.8 | 80.5 | 81.4 | 81.7 | 82.6 | -
| W | 134.9 |  | 0.86 |  |  | 72 | 75.7 | 76.6 | 77.6 | 74.7 | 75.7 | -
BLTS-LVN | S | 109.7 |  | 0.96 |  |  | 80.8 | 79.8 | 80.9 | 82.5 | 82.8 | 83 | -
| W | 122.3 |  | 0.86 |  |  | 72.5 | 76.2 | 77 | 78.6 | 75.1 | 76 | -
ATS-SCI Radial Line | S | 90.8 |  | 0.84 |  |  | 43.7 | 48 | 52.7 | 44.9 | 43.9 | 46.4 | -
| W | 116 |  | 0.84 |  |  | 45.5 | 45.3 | 45.3 | 45.4 | 45.4 | 45.4 | -
BLTS-SCI Radial Line | S | 97.2 |  | 0.99 |  |  | 69.2 | 69.1 | 69.1 | 68.9 | 68.6 | 68.4 | -
| W | 125.7 |  | 0.99 |  |  | 68.6 | 68.2 | 68.1 | 68 | 68 | 69.1 | -
ATS-TYA | S | 102.3 |  | 0.95 |  |  | 21.8 | 20.6 | 19.9 | 20.9 | 21.3 | 20.3 | -
| W | 130.3 |  | 0.95 |  |  | 22.4 | 22.1 | 21.6 | 21.4 | 20.6 | 20.3 | -
BLTS-TYA | S | 88 |  | 0.95 |  |  | 20.5 | 19.2 | 18.6 | 19.6 | 20 | 19 | -
| W | 112 |  | 0.95 |  |  | 20 | 21.1 | 20.9 | 20.6 | 19.8 | 19.5 | -
BLTS-BMH | S | 32.6 | 3 | 0.97 | 3.2 |  | 30.2 | 25.8 | 27.7 | 29.6 | 31.9 | 34.6 | -
| W | 37.7 | 12 | 0.98 | 7.5 |  | 21.8 | 19.2 | 20.6 | 21.6 | 22.8 | 24.8 | -
BATS 66kV
BATS-BAN1 | S | 96 | 6 | 0.94 | 12.3 |  | 86.8 | 75.5 | 78.4 | 81.4 | 82.6 | 83.6 | -
| W | 102.9 | 21 | 0.97 | 15 |  | 71.8 | 76.8 | 78.6 | 80.5 | 82.4 | 83.4 | -
BATS-BAN2 | S | 96 | 6 | 0.94 | 12.3 |  | 87.1 | 75.7 | 77.9 | 80.9 | 82.1 | 83.8 | -
| W | 102.9 | 21 | 0.97 | 15 |  | 72.1 | 77.1 | 78.2 | 80 | 82.7 | 83.7 | -
BAN-BGR | S | 25.7 |  | 0.99 |  | 52.5 | 15.5 | 16.7 | 16.6 | 16.3 | 16.3 | 16.2 | -
| W | 34.9 |  | 1 |  | 52.5 | 13.6 | 12.9 | 12.7 | 12.8 | 12.8 | 12.8 | -
BGR-ART | S | 45.7261 |  | 0.92 |  | 52.5 | 14.4 | 15.5 | 15.4 | 15.2 | 15.1 | 15 | -
| W | 47.4409 |  | 0.98 |  | 52.5 | 11.9 | 11.2 | 11 | 11.1 | 11.1 | 11.1 | -
BATS-YSW - BGL - T - off | S | 33.3 | 4 | 0.97 | 3.2 | 28.7 | 33.2 | 28.9 | 31 | 32.8 | 35.8 | 37.3 | -
| W | 33.3 | 5 | 0.98 | 7.5 | 28.7 | 25.2 | 23 | 24 | 24.8 | 26 | 27 | -
YSW-BMH | S | 38.9 | 4 | 0.97 | 3.2 | 28.7 | 27.9 | 24.1 | 26 | 27.6 | 30 | 31.1 | -
| W | 38.9 | 5 | 0.98 | 7.5 | 28.7 | 20.5 | 18.1 | 19.1 | 20 | 21.2 | 22.3 | -
BATS-BAS1 | S | 83.5 |  | 0.96 | 15.3084 |  | 73.2 | 65.5 | 67.8 | 72 | 73.8 | 74.9 | -
| W | 102.9 |  | 0.98 | 20.3366 |  | 63.1 | 66.5 | 68.1 | 70.5 | 72.3 | 73.8 | -
BATS-BAS 2 BGF - T - off | S | 93.2 |  | 0.96 |  |  | 73.2 | 65.6 | 67.8 | 72.1 | 73.8 | 75 | -
| W | 94.9 |  | 0.98 |  |  | 63.2 | 66.6 | 68.1 | 70.5 | 72.4 | 73.8 | -
BETS 66kV
BETS-BGO | S | 109.7 |  | 0.99 |  |  | 91.7 | 93 | 95.9 | 101.7 | 104.3 | 107.7 | -
| W | 114.3 |  | 1 |  |  | 69 | 68.4 | 70.3 | 73.4 | 76.4 | 77.6 | -
BGO-EHK | S | 54.9 | 4 | 0.99 | 0 |  | 48.8 | 47.9 | 48.7 | 51.3 | 52.8 | 54.7 | -
| W | 52.6 | 3 | 1 | 4.8 |  | 35.6 | 36.4 | 37.4 | 38 | 39.4 | 40.2 | -
BETS-EHK | S | 111.5 |  | 0.99 |  |  | 93.1 | 93.7 | 96.7 | 104.4 | 107.5 | 109.3 | -
| W | 111.5 |  | 1 |  |  | 69 | 68.3 | 70.3 | 73.9 | 77 | 78.2 | -
BETS-CMN | S | 64 |  | 0.99 |  |  | 56.1 | 57.9 | 59.3 | 61.4 | 62.9 | 63.1 | -
| W | 65.2 |  | 0.99 |  |  | 41.4 | 40.5 | 40.8 | 41 | 41.1 | 41.8 | -
CMN-MRO | S | 26.3 | 6 | 0.9982 | 0 |  | 26.6 | 27.7 | 27.6 | 28.1 | 27.9 | 27.7 | 5.323% | 3 | 3 | 5 | 4 | 3 | 4 | 4 | 5 | 4 | 4
| W | 35.4 | 4 | 1 | 0 |  | 21.6 | 21.7 | 21.6 | 21.4 | 21.2 | 21.2 | -
BETS-MRO | S | 76.6 |  | 0.99 |  |  | 62.1 | 65.5 | 66.5 | 69.3 | 71.5 | 71.8 | -
| W | 89.2 |  | 0.99 |  |  | 44 | 43.3 | 43.5 | 43 | 42.8 | 42.9 | -
BETS-CTN Radial Line | S | 27.4 | 6.5 | 0.96 | 0.4 | 19.8 | 20.8 | 24.7 | 24.8 | 25.1 | 23.8 | 23.3 | -
| W | 26.3 | 3 | 0.99 | 0.4 | 19.8 | 19.7 | 19.4 | 19.2 | 19 | 19.1 | 19.2 | -
CTN-CBW Radial Line | S | 28 |  | 0.92 |  | 19.8 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | -
| W | 28 |  | 0.92 |  | 19.8 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | -
DPTS 66kV
DPTS-MLN1 | S | 135.4 |  | 0.94 |  |  | 60.4 | 65.6 | 78.4 | 88.6 | 94.6 | 100.9 | -
| W | 142.3 |  | 0.95 |  |  | 43 | 42.4 | 50.3 | 53.7 | 55.7 | 59.2 | -
DPTS-MLN2 | S | 135.4 |  | 0.94 |  |  | 60.4 | 65.5 | 77.5 | 88.5 | 94.6 | 99.7 | -
| W | 142.3 |  | 0.95 |  |  | 43 | 42.4 | 50.3 | 53.7 | 55.7 | 59.2 | -
DPTS-SU1 | S | 135.4 |  | 0.94 |  |  | 87.6 | 96.9 | 108.1 | 117.9 | 121.7 | 124.3 | -
| W | 142.3 |  | 0.95 |  |  | 64.4 | 83.3 | 93.6 | 95.3 | 97.4 | 98.9 | -
DPTS-SU2 | S | 135.4 |  | 0.94 |  |  | 88.7 | 98.2 | 109.5 | 120.6 | 124.7 | 126 | -
| W | 142.3 |  | 0.95 |  |  | 64.4 | 85.1 | 94.7 | 96.4 | 98.6 | 101.2 | -
DPTS-TNA1 | S | 135.4 |  | 0.94 |  |  | 46.4 | 48.8 | 52.7 | 60.6 | 64.5 | 79.3 | -
| W | 142.3 |  | 0.95 |  |  | 41.9 | 32.5 | 37 | 39.6 | 45.7 | 49.1 | -
DPTS-TNA2 | S | 135.4 |  | 0.94 |  |  | 46.4 | 48.8 | 52.7 | 60.6 | 64.5 | 79.3 | -
| W | 142.3 |  | 0.95 |  |  | 41.9 | 32.5 | 37 | 39.6 | 45.7 | 49.1 | -
FBTS 66kV
FBTS-DLF1 | S | 87.4512 |  | 0.94 |  |  | 26.6 | 25 | 20.1 | 21.2 | 22.3 | 23.5 | -
| W | 87.4512 |  | 0.95 |  |  | 17.6 | 17.5 | 17.9 | 15.6 | 16.2 | 17 | -
FBTS-DLF3 | S | 87.4512 |  | 0.94 |  |  | 26.6 | 25 | 20.1 | 21.2 | 22.3 | 23.5 | -
| W | 87.4512 |  | 0.95 |  |  | 17.6 | 17.6 | 18 | 15.6 | 16.3 | 17 | -
GTS 66kV
GTS-BCG | S | 109.7 |  | 0.95 |  |  | 69.9 | 73.5 | 77.2 | 78.1 | 79.8 | 84.2 | -
| W | 134.9 |  | 0.96 |  |  | 51.9 | 54.7 | 57.4 | 59.4 | 61.9 | 64.4 | -
BCG-WPD | S | 91.5 |  | 0.97 |  |  | 63.4 | 63.4 | 66.8 | 67.9 | 69.6 | 73.4 | -
| W | 91.5 |  | 0.99 |  |  | 46.9 | 48.6 | 51.1 | 53 | 55.4 | 57.7 | -
GTS-WPD | S | 91.5 | 3 | 0.98 | 9.5 |  | 68.7 | 73.4 | 76 | 78 | 79.7 | 84.1 | -
| W | 91.5 | 5 | 0.98 | 19.8 |  | 51.8 | 54.6 | 57.3 | 58.5 | 60.9 | 64.3 | -
GTS-WIN | S | 74.3 |  | 0.97 |  |  | 44.3 | 41.7 | 41.5 | 42.4 | 42.6 | 42.7 | -
| W | 87.4 |  | 0.99 |  |  | 41.3 | 37.8 | 37.7 | 38.1 | 38.2 | 38.4 | -
CLC-MGW | S | 92 |  | 1 |  |  | 36.1 | 33.9 | 33.9 | 34.2 | 34.5 | 34.6 | -
| W | 92 |  | 1 |  |  | 32.2 | 29.1 | 29.2 | 29.4 | 29.4 | 29.4 | -
MGW-WIN | S | 95 |  | 1 |  |  | 36.6 | 34.4 | 33.8 | 34.5 | 34.8 | 35 | -
| W | 100 |  | 1 |  |  | 33.3 | 30.2 | 30.1 | 30.4 | 30.4 | 30.5 | -
GTS-CRO | S | 91.5 |  | 0.9 |  |  | 28.1 | 30.4 | 31.2 | 32.3 | 32.4 | 32.4 | -
| W | 91.5 |  | 0.89 |  |  | 27.5 | 28.9 | 29.8 | 29.8 | 30.4 | 30.4 | -
CRO-FDN | S | 109.7 |  | 0.9 |  |  | 28 | 30.3 | 31.1 | 32.1 | 32.3 | 32.3 | -
| W | 134.9 |  | 0.89 |  |  | 25 | 26.4 | 27.3 | 27.3 | 27.8 | 27.8 | -
GTS-FDN | S | 102.9 |  | 0.84 |  |  | 28.1 | 30.4 | 31.2 | 32.3 | 32.4 | 32.4 | -
| W | 134.9 |  | 0.94 |  |  | 27.5 | 29 | 29.8 | 29.8 | 30.4 | 30.4 | -
GTS-FNS | S | 88 |  | 0.95 |  |  | 69.1 | 76.9 | 79.6 | 82.8 | 83.6 | 83.5 | -
| W | 112 |  | 0.95 |  |  | 60.3 | 71.6 | 72.4 | 74.6 | 74.4 | 74.6 | -
FNS-SRC | S | 109.7 |  | 0.95 |  |  | 40.8 | 40.6 | 41.2 | 41.4 | 41.6 | 41.5 | -
| W | 126.9 |  | 0.95 |  |  | 36.4 | 36.6 | 36.9 | 37.1 | 37.5 | 37.3 | -
GTS-SRC | S | 109.7 |  | 0.95 |  |  | 69.2 | 76.9 | 79.6 | 82.9 | 83.6 | 83.5 | -
| W | 134.9 |  | 0.95 |  |  | 60.3 | 71.6 | 72.4 | 74.6 | 74.4 | 74.6 | -
GTS-GB | S | 135.5 |  | 0.86 |  |  | 113.2 | 113.3 | 118.6 | 124.4 | 128.1 | 130.8 | -
| W | 151.5 |  | 0.89 |  |  | 81.1 | 85.1 | 86.7 | 91.5 | 93.3 | 94.4 | -
GB-GL | S | 110.3 | 3 | 0.97 | 15.9 |  | 100.1 | 99.3 | 104.1 | 109.7 | 112.7 | 115.3 | -
| W | 131.4 | 4 | 0.98 | 18.5 |  | 69.2 | 72.3 | 73.9 | 78.4 | 79.8 | 80.8 | -
GL-GCY | S | 109.7 |  | 0.92 |  |  | 66 | 65.2 | 67.2 | 72.3 | 73.5 | 74.1 | -
| W | 134.9 |  | 0.95 |  |  | 51.7 | 54 | 55.6 | 59.1 | 60.6 | 61.2 | -
GTS-GCY | S | 102.9 | 4 | 0.92 | 15.9 |  | 113.2 | 113.3 | 116.1 | 124.4 | 128.2 | 130 | 10.11% | 24 | 30 | 59 | 82 | 96 | 2 | 3 | 6 | 8 | 9
| W | 110.3 | 7 | 0.95 | 18.5 |  | 81.8 | 84.9 | 87.5 | 91.4 | 94.1 | 95.3 | -
GTS-GLE1 | S | 135.5 |  | 0.96 |  |  | 119.3 | 120.7 | 123.1 | 125.8 | 126.3 | 132 | -
| W | 151.5 |  | 0.95 |  |  | 84.7 | 84.6 | 87.7 | 89.6 | 92.8 | 94.3 | -
GTS-GLE 2 | S | 135.5 |  | 0.96 |  |  | 126.1 | 127.6 | 131.3 | 130.9 | 133.4 | 141.9 | -
| W | 151.5 |  | 0.95 |  |  | 86.5 | 86.7 | 89.7 | 93.1 | 96 | 98 | -
GLE-DDL1 | S | 74.3 |  | 0.96 |  |  | 68.4 | 69.1 | 71.1 | 69.4 | 68.7 | 74.7 | -
| W | 86.9 |  | 0.98 |  |  | 42.1 | 42.2 | 43 | 44.8 | 45.9 | 46.9 | -
GLE-DDL2 | S | 74.3 |  | 0.96 |  |  | 69.1 | 70.4 | 71.2 | 69.5 | 68.8 | 76.7 | -
| W | 86.9 |  | 0.98 |  |  | 42.8 | 42.2 | 43.7 | 44.9 | 46.7 | 47.7 | -
HOTS 66kV
HOTS-STL1 | S | 49.2 |  | 0.95 |  |  | 21.4 | 21.3 | 21.4 | 21.2 | 21.2 | 21.3 | -
| W | 57.2 |  | 0.99 |  |  | 21.2 | 24.7 | 24.8 | 24.7 | 24.6 | 24.7 | -
HOTS-STL2 | S | 25.7 |  | 0.95 |  |  | 20.2 | 20.1 | 20.2 | 19.9 | 20 | 20 | -
| W | 34.9 |  | 0.99 |  |  | 19.8 | 23.2 | 23.3 | 23.2 | 23.2 | 23.2 | -
STL-ART | S | 38.3 |  | 0.92 |  |  | 14.7 | 15.6 | 15.5 | 15.2 | 15.2 | 15.1 | -
| W | 43.4 |  | 0.98 |  |  | 12.5 | 11.6 | 11.6 | 11.6 | 11.7 | 11.7 | -
HOTS-HSM1 | S | 49.2 |  | 0.95 |  |  | 41.7 | 45.7 | 46 | 47.8 | 47.7 | 47.7 | -
| W | 52.6 |  | 0.99 |  |  | 35 | 31.3 | 31.7 | 32 | 32.1 | 32.2 | -
HOTS-HSM2 | S | 49.2 |  | 0.95 |  |  | 41.7 | 45.7 | 46 | 47.8 | 47.7 | 47.7 | -
| W | 52.6 |  | 0.99 |  |  | 35 | 31.2 | 31.7 | 32 | 32.1 | 32.2 | -
HOTS-KWF Radial Line | S | 44 |  | 0.99 |  | 31 | 13.5 | 15.4 | 15.5 | 15.4 | 15.2 | 15.3 | -
| W | 43.4 |  | 1 |  | 31 | 11.6 | 11 | 10.7 | 10.8 | 10.6 | 10.6 | -
KWF-NHL Radial Line | S | 44 |  | 0.99 |  |  | 9.4 | 10.7 | 10.7 | 10.7 | 10.5 | 10.6
| W | 43.4 |  | 1 |  |  | 8.5 | 7.8 | 7.8 | 7.8 | 7.6 | 7.6
HOTS-CHM Radial Line | S | 26.2925 |  | 0.99 |  |  | 2.9 | 2.6 | 2.6 | 2.5 | 2.5 | 2.5 | -
| W | 35.4378 |  | 1 |  |  | 3 | 2.9 | 2.8 | 2.8 | 2.8 | 2.7 | -
KTS 66kV
SBY-GSB1 | S | 51.4 |  | 1 |  |  | 48.9 | 48.1 | 49.5 | 50.8 | 52 | 53.8 | -
| W | 69.7 |  | 1 |  |  | 47.6 | 48.3 | 49.6 | 50.3 | 52 | 53.4 | -
SBY-GSB2 | S | 76.6 |  | 1 |  |  | 48.9 | 48 | 49.5 | 51.3 | 51.9 | 54.2 | -
| W | 89.2 |  | 1 |  |  | 47.5 | 48.2 | 49.4 | 50.1 | 51.9 | 53.3 | -
GSB-WND1 | S | 109.7 |  | 1 |  |  | 26.3 | 24.3 | 24.9 | 26 | 26.6 | 27.2 | -
| W | 114.3 |  | 1 |  |  | 27.3 | 27.2 | 27.9 | 28.8 | 29.4 | 29.9 | -
GSB-WND2 | S | 46.3 |  | 1 |  |  | 26.8 | 24.8 | 25.4 | 26.6 | 27.1 | 27.8 | -
| W | 49.7 |  | 1 |  |  | 27.8 | 27.8 | 28.5 | 28.9 | 29.6 | 30.5 | -
KTS-SA1 | S | 108 |  | 0.94 |  |  | 87.8 | 92.7 | 95.6 | 97.7 | 98.4 | 99.4 | -
| W | 122.3 |  | 0.99 |  |  | 58.4 | 58.8 | 60 | 62.1 | 63 | 63.7 | -
KTS-SA2 | S | 116.6 |  | 0.98 |  |  | 87.8 | 92.7 | 95.6 | 97.7 | 98.4 | 99.4 | -
| W | 122.3 |  | 0.99 |  |  | 58.4 | 58.8 | 60 | 62.1 | 63 | 63.7 | -
KTS-SSE2 | S | 89.7 |  | 0.95 |  |  | 78.1 | 75.2 | 76.3 | 78.8 | 79.3 | 80.7 | -
| W | 100.6 |  | 0.95 |  |  | 66.9 | 66.8 | 68.5 | 70.4 | 71.5 | 72.3 | -
KTS-SSE1 | S | 100.6 |  | 0.92 |  |  | 78.3 | 75.6 | 76.8 | 79.3 | 79.7 | 81.2 | -
| W | 125.7 |  | 0.96 |  |  | 67.2 | 67.1 | 68.9 | 70.7 | 71.9 | 72.7 | -
KGTS 66kV
KGTS-CHA Radial Line | S | 31.4 |  | 1 |  |  | 14.5 | 14.2 | 14.3 | 13.9 | 13.7 | 13.6 | -
| W | 41.2 |  | 0.99 |  |  | 14.8 | 15.1 | 14.8 | 14.9 | 14.9 | 14.8 | -
KGTS-SHL | S | 36 | 7 | 0.98104 | 0.8 |  | 48.3 | 52.3 | 52.6 | 52.6 | 51.6 | 51.2 | 45.28% | 872 | 914 | 914 | 779 | 728 | 159 | 164 | 164 | 147 | 140 | *Data copied into GSF-SHL*
| W | 36 | 6 | 0.99732 | 1.7 |  | 34.4 | 34.5 | 34.9 | 35.1 | 34.9 | 35.5 | -
KGTS-GSF | S | 48.6 | 7 | 0.98104 | 0.8 |  | 42.8 | 45.5 | 46.5 | 47 | 45.5 | 45.1 | -
| W | 52.6 | 6 | 0.99732 | 1.7 |  | 31.3 | 31.3 | 31.7 | 31.8 | 31.7 | 31.7 | -
GSF-SHL | S | 40 | 7 | 0.98104 | 0.8 |  | 40.9 | 43.3 | 44.2 | 44.8 | 43.4 | 43 | 8.25% | 355 | 378 | 378 | 305 | 279 | 79 | 83 | 83 | 72 | 68
| W | 49.7 | 6 | 0.99732 | 1.7 |  | 30.6 | 30.6 | 31 | 31.1 | 30.9 | 31 | -
RCTS 66kV
RCTS-MBN | S | 97.2 |  | 0.98 |  |  | 48 | 49.6 | 50.1 | 50.3 | 50.5 | 50.7 | -
| W | 114.3 |  | 1 |  |  | 32.9 | 35 | 35.2 | 35.9 | 36.3 | 36.4 | -
MBN-DTN Radial Line | S | 74.305 |  | 0.84 |  |  | 22.9 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | -
| W | 86.8797 |  | 0.94 |  |  | 15.3 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | -
MBN-MDA | S | 74.3 |  | 0.98 |  |  | 49.1 | 53.5 | 53.8 | 53.9 | 54 | 54.9 | -
| W | 86.9 |  | 1 |  |  | 32.9 | 35.3 | 35.4 | 36 | 36.4 | 36.6 | -
MDA-BNG Radial Line | S | 104.027 |  | 0.84 |  |  | 34.7 | 37.4 | 37.4 | 37.8 | 37.8 | 38 | -
| W | 114.3154 |  | 0.94 |  |  | 25.3 | 26.4 | 26.4 | 26.6 | 26.8 | 26.8 | -
RCTS-MDA1 | S | 72.01 |  | 0.97 |  |  | 78.4 | 79.3 | 80.2 | 80.6 | 80.9 | 81.2 | 10.12% | 47 | 62 | 70 | 77 | 83 | 16 | 19 | 20 | 21 | 23
| W | 90.9 |  | 1 |  |  | 54.5 | 57.9 | 58.3 | 59.4 | 60 | 60.2 | -
RCTS-MDA2 | S | 104 |  | 0.97 |  |  | 86.8 | 87.4 | 88.4 | 88.8 | 89.2 | 89.4 | -
| W | 114.3 |  | 1 |  |  | 60.9 | 64.7 | 65.1 | 66.3 | 67 | 67.3 | -
RCTS-YSF | S | 84.6 |  | 0.94 |  |  | 8.3 | 8.5 | 8.4 | 8.5 | 8.4 | 8.4 | -
| W | 106.3 |  | 0.83 |  |  | 9.1 | 9.2 | 9.1 | 9 | 8.9 | 8.8 | -
YSF- HTH | S | 17.7 |  | 1 |  |  | 7.9 | 8.1 | 8 | 8.1 | 8 | 8 | -
| W | 35.4 |  | 1 |  |  | 8.6 | 8.7 | 8.6 | 8.5 | 8.4 | 8.3 | -
RCTS-KSF | S | 84.6 |  | 1 |  |  | 19.3 | 17.9 | 18.1 | 18.8 | 18.9 | 18.6 | -
| W | 106.3 |  | 1 |  |  | 8.1 | 7.5 | 7.5 | 7.7 | 7.6 | 7.6 | -
KSF-RVL | S | 65 |  | 1 |  |  | 19.5 | 17.9 | 18.1 | 18.9 | 19 | 18.6 | -
| W | 65 |  | 1 |  |  | 8 | 7.3 | 7.4 | 7.5 | 7.4 | 7.4 | -
RVL-BSP | S | 65.2 |  | 0.98 |  |  | 18.7 | 17.3 | 17.5 | 18.1 | 18.3 | 18 | -
| W | 67.4 |  | 1 |  |  | 8 | 7.3 | 7.4 | 7.5 | 7.4 | 7.4 | -
BSP-BBD Radial Line | S | 65.2 |  | 0.98 |  |  | 28.6 | 31.5 | 31.1 | 30.3 | 30.1 | 28.8 | -
| W | 67.4 |  | 1 |  |  | 10.9 | 9.9 | 9.8 | 9.5 | 9.4 | 9.7 | -
SHTS 66kV
SHTS-KYM1 | S | 79.4 |  | 0.99 |  |  | 48.1 | 49.5 | 52.2 | 53.8 | 53.1 | 52.8 | -
| W | 90.3 |  | 0.98 |  |  | 36.8 | 36.1 | 36.4 | 38.3 | 38.6 | 38.6 | -
SHTS-KYM2 | S | 79.4 |  | 0.99 |  |  | 48.7 | 50 | 52.8 | 54 | 53.5 | 53.4 | -
| W | 90.3 |  | 0.98 |  |  | 37.2 | 36.5 | 36.8 | 38.7 | 39.1 | 39.1 | -
KYM-ECA1 | S | 45.7 |  | 1 |  |  | 36.2 | 39.1 | 40.7 | 39.3 | 38.5 | 38.8 | -
| W | 53.2 |  | 1 |  |  | 28 | 27.3 | 27.7 | 28.1 | 28.3 | 28.4 | -
KYM-ECA2 | S | 45.7 |  | 1 |  |  | 36.3 | 39.2 | 41.5 | 39.3 | 38.6 | 38.9 | -
| W | 53.2 |  | 1 |  |  | 28 | 27.4 | 27.7 | 28.2 | 28.3 | 28.4 | -
KYM-SHP | S | 104 |  | 0.92 |  |  | 21 | 20.3 | 21.7 | 26.7 | 26.5 | 26.6 | -
| W | 114.3 |  | 0.98 |  |  | 16 | 15.8 | 15.9 | 18.7 | 18.9 | 18.7 | -
SHTS-SHP | S | 101.7 |  | 0.92 |  |  | 35.7 | 36.4 | 38.7 | 41 | 40.5 | 40.4 | -
| W | 118.3 |  | 0.98 |  |  | 27.3 | 26.8 | 27 | 29.1 | 29.4 | 29.4 | -
SHTS-MNA | S | 88 |  | 0.973 |  |  | 67.8 | 70.2 | 71.4 | 75.9 | 76.9 | 77.8 | -
| W | 111.5 |  | 0.9824 |  |  | 48 | 44.6 | 45.3 | 46.5 | 47.8 | 48.3 | -
MNA-STN | S | 48.6 |  | 0.98089 |  |  | 37.5 | 36.8 | 37.6 | 40.3 | 41 | 41.7 | -
| W | 52.6 |  | 0.989 |  |  | 24.8 | 23.4 | 23.5 | 24.7 | 25.5 | 25.8 | -
SHTS-STN | S | 91.5 |  | 0.973 |  |  | 67.3 | 69.2 | 70.4 | 74.8 | 76.3 | 77.2 | -
| W | 91.5 |  | 0.9824 |  |  | 47.5 | 44.5 | 44.8 | 46.3 | 47.3 | 47.8 | -
SHTS-NKA | S | 91 |  | 0.998 |  |  | 72.6 | 72.6 | 72.7 | 73.2 | 75.2 | 74.8 | -
| W | 91 |  | 0.991 |  |  | 54.4 | 53.5 | 54.2 | 55 | 54.8 | 54.8 | -
SHTS-NSF | S | 98 |  | 0.998 |  |  | 71.2 | 71.2 | 71.3 | 71.8 | 73.3 | 73.4 | -
| W | 144 |  | 0.991 |  |  | 54 | 53 | 53.7 | 54.5 | 54.3 | 54.8 | -
NSF-NKA | S | 103 |  | 0.998 |  |  | 66.9 | 66.9 | 67 | 67.4 | 68.6 | 68.7 | -
| W | 144 |  | 0.991 |  |  | 52.3 | 51.5 | 52.1 | 52.8 | 52.7 | 53.1 | -
NKA-CME Radial Line | S | 74.3 |  | 1 |  |  | 37.5 | 37 | 36.9 | 37.6 | 38.9 | 38.8 | -
| W | 86.9 |  | 1 |  |  | 27.3 | 26 | 26.4 | 26.9 | 26.2 | 26.3 | -
SHTS-SHN1 | S | 88 |  | 0.97 |  |  | 34.7 | 37.2 | 38.6 | 38.2 | 38.1 | 38.4 | -
| W | 112 |  | 1 |  |  | 25.5 | 25.2 | 25.3 | 25.9 | 25.9 | 26.1 | -
SHTS-SHN2 | S | 88 |  | 0.97 |  |  | 34.7 | 37.2 | 38.6 | 38.2 | 38.1 | 38.4 | -
| W | 112 |  | 1 |  |  | 25.5 | 25.2 | 25.3 | 25.9 | 25.9 | 26.1 | -
TGTS 66kV
TGTS-CDN | S | 76.6 |  | 0.91 |  |  | 41.2 | 38.8 | 39.3 | 39.4 | 39.5 | 39.6 | -
| W | 85.7 |  | 0.92 |  |  | 39.5 | 37 | 36.7 | 37.2 | 37.2 | 37.1 | -
CDN-COB | S | 49.2 |  | 0.91 |  |  | 22.2 | 20.8 | 20.3 | 21 | 21.6 | 21.8 | -
| W | 57.2 |  | 0.93 |  |  | 21.7 | 21 | 21 | 21.1 | 21.2 | 21.2 | -
CDN-CLC | S | 74.3 |  | 0.96 |  |  | 37.2 | 35 | 35.5 | 35.5 | 35.7 | 35.9 | -
| W | 86.9 |  | 0.97 |  |  | 33.2 | 30 | 30.1 | 30.3 | 30.4 | 30.4 | -
TGTS-COB | S | 109.7 |  | 0.85 |  |  | 33.7 | 31.6 | 31 | 31.9 | 32.4 | 32.5 | -
| W | 116 |  | 0.92 |  |  | 32.5 | 31.4 | 31.6 | 31.6 | 31.5 | 31.4 | -
TGTS-HTN | S | 44.9 | 5 | 0.96 | 2.7 | 86.7 | 40.6 | 40.5 | 43 | 40.7 | 38.9 | 38.7 | -
| W | 44.9 | 5 | 0.99 | 3.4 | 86.7 | 43.1 | 39.5 | 40 | 40.1 | 40.6 | 40.2 | -
HTN-NRB | S | 42.2 | 5 | 0.96 | 2.7 | 86.7 | 29.4 | 29.4 | 30.1 | 29.6 | 29 | 28.9
| W | 42.2 | 5 | 0.99 | 3.4 | 86.7 | 29.7 | 29.3 | 29.6 | 29.4 | 29.5 | 29.4
TGTS-NRB | S | 42.2 | 5 | 0.96 | 2.7 | 86.7 | 45.4 | 45.4 | 47.5 | 45.7 | 42.7 | 41.5 | 7.583% | 16 | 57 | 24 | 15 | 9 | 13 | 33 | 18 | 10 | 6
| W | 42.2 | 5 | 0.99 | 3.4 | 86.7 | 47.7 | 43.9 | 44.5 | 44.9 | 45.6 | 45.1 | 4.028%
TGTS-KRT1 | S | 44 |  | 0.97 |  |  | 33.9 | 35 | 34.8 | 36.3 | 37 | 36.9 | -
| W | 44.6 |  | 0.98 |  |  | 32 | 31.6 | 32.1 | 32.8 | 32.7 | 32.9 | -
TGTS-KRT2 | S | 97.2 |  | 0.97 |  |  | 38.7 | 39.8 | 40.2 | 42.2 | 42.5 | 42.4 | -
| W | 116 |  | 0.98 |  |  | 36.7 | 36 | 36.6 | 37.1 | 37 | 37.2 | -
KRT-PLD No.1 -CWF T -off | S | 40 |  | 0.97 |  | 18.2 | 19 | 17.7 | 17.3 | 17.8 | 18.1 | 17.8 | -
| W | 45.7 |  | 0.96 |  | 18.2 | 20.2 | 20.5 | 20.6 | 20.6 | 20.4 | 20.4 | -
KRT-PLD No.2 -YWF T -off | S | 40 |  | 0.97 |  | 30 | 20.4 | 19.1 | 18.9 | 19.1 | 19.4 | 19.1 | -
| W | 45.7 |  | 0.96 |  | 30 | 21.7 | 22.1 | 22.3 | 22.2 | 21.9 | 21.9 | -
KRT-WBL | S | 46.9 |  | 0.93 |  |  | 24.9 | 26 | 26.2 | 28.2 | 29 | 28.8 | -
| W | 47.4 |  | 0.95 |  |  | 21.1 | 18.8 | 19.1 | 19.5 | 20.1 | 20.4 | -
WBL-TRG1 | S | 47.4 |  | 0.99 |  |  | 38.9 | 40.3 | 40.2 | 42.1 | 43 | 42.9 | -
| W | 49.7 |  | 0.99 |  |  | 36.1 | 35.2 | 35.7 | 36.5 | 36.5 | 36.7 | -
WBL-TRG2 | S | 45.7 |  | 0.99 |  |  | 34.5 | 35.6 | 35.9 | 37.8 | 38.3 | 38.2 | -
| W | 46.3 |  | 0.99 |  |  | 31.9 | 30.9 | 31.4 | 31.9 | 31.9 | 32.2 | -
TGTS-TRG1 | S | 91.5 |  | 0.99 |  |  | 64.5 | 66.6 | 67 | 69 | 69.8 | 69.8 | -
| W | 91.5 |  | 1 |  |  | 64 | 62.8 | 63.6 | 64.3 | 64.7 | 65 | -
TGTS-TRG2 | S | 91.5 |  | 0.99 |  |  | 64.5 | 66.6 | 67 | 69 | 69.9 | 69.8 | -
| W | 91.5 |  | 1 |  |  | 64 | 62.8 | 63.6 | 64.3 | 64.7 | 65 | -
WETS 66kV
WETS-HTH Radial Line | S | 17.7 |  | 0.94 |  |  | 7.8 | 8 | 7.9 | 8 | 7.9 | 7.9 | -
| W | 35.4 |  | 0.83 |  |  | 8.4 | 8.5 | 8.4 | 8.4 | 8.2 | 8.1 | -
HTH-OYN Radial Line | S | 17.7 |  | 0.94 |  |  | 7.6 | 7.8 | 7.8 | 7.9 | 7.7 | 7.8 | -
| W | 35.4 |  | 0.83 |  |  | 8.2 | 8.3 | 8.2 | 8.2 | 8.1 | 7.9 | -
WETS-WSF | S | 31.4 |  | 1 |  |  | 19 | 18.1 | 18.1 | 17.1 | 16.5 | 16.2 | -
| W | 43.4 |  | 1 |  |  | 9.7 | 10.2 | 9.9 | 9.8 | 9.6 | 9.7 | -
WSF-WMN | S | 31.4 |  | 1 |  |  | 19.2 | 18.3 | 18.3 | 17.4 | 16.8 | 16.5 | -
| W | 43.4 |  | 1 |  |  | 10.1 | 10.5 | 10.3 | 10.2 | 10 | 10.1 | -
WETS-BBD/RVL Radial Line when supplying both RVL & BBD | S | 87 | 10 | 0.97664 | 0 |  | Note 10 | 52.3 | 51.6 | 51.5 | 51.8 | 49.7 | -
| W | 87 | 1 | 0.99166 | 0.76923 |  | Note 10 | 17.4 | 17.3 | 17.2 | 17 | 17.3 | -
Note 1: Generation capacity is specified at the location (sub-transmission line/ loop) where the generation is connected to the network.
Note 2: The 2017 demand figures are actuals for summer and forecast for winter.
Note 3: Forecast demand worst case N-1 scenario refers to the expected load that the sub-transmission line would supply in the event of the worst case outage of a sub-transmission line within the loop system.
Note 4: Radial lines are studied with the expected load under system normal (or N) conditions and also under N-1 if normally open loop arrangement exists. Where load does not exceed the N rating, the N-1 risk is shown if this is worse case.
Note 5: With transfer of MLN to DPTS early 2017, sections of SBY-MLN & KTS-MLN are used for new Jemena KTS-SBY2 66kV line
Note 6: With transfer of SU to DPTS Oct 2017, SU-SSE is Out Of Service, part KTS-SU1 used for DPTS-SU1 with remainder OOS, KTS-SU2 becomes KTS-SSE1 and KTS-SSE becomes KTS-SSE2
Note 7: New looped lines to MLN, SU & TNA from DPTS by late 2017 early 2018
Note 8: With the construction of ATD, part of ATS-BLTS used for ATS-ATD and BLTS-ATD in 2017, this also reduces loads in adjacent loops
Note 9:
Note 10: WETS-RVL becomes WETS-BBD/RVL in mid 2018