## Slide 1: Contestable Works Consultative Committee

## Slide 2: Introduction
Safety share
Attendees
Actions from last meeting
Overview of today
    Performance update
    Communicate progress in key areas
    Introduce process changes and follow up workshop
  Feedback is welcome
Notes: We have attendees from across industry here today:
Developers
Project Managers
Designers
Electrical contractors
Civil contractors
Auditors
Industry bodies including:
  CCF
  UDIA
  ALDE
  ESC
From the Powercor team we have a number of representatives here – I’ll get the team to quickly introduce themselves…

## Slide 3: Actions
Action | Responsible | Status
Update ESC on Charter at next meeting scheduled for the 14th July 2019 | Powercor | Closed
Provide further information on cable details inaccuracy audit category | Powercor | Closed Today
Link Bulletins to Technical Standards and provide process clarification | Powercor | In Progress
Powercor will provide an example report showing an overview of all contractor ratings. | Powercor | Closed Today
CCF to provide nominations for Road Contractors to attend the committee | CCF | Open

## Slide 4: Charter Improving performance in relation to Contestable Works
Objective
Engage with industry for the purpose of:
Improving the safety on site
Improving the quality of the built asset
Communicating process changes and receiving and incorporating feedback
Improving the understanding and application of technical standards
Providing certainty of timeframes and increasing levels of responsiveness
Membership
The membership will consist of representatives from:
Powercor: Design & Customer Programs, Field Audit & Quality, Technical Standards, Network Planning & Development
ALDE, CCF, UDIA
PM2/Designer x 2
Electrical Constructor x 2
Civil Contractor x 2
Agenda
Standard Agenda items are:
ESC overview and update
Contestable Works Team update
Audit Results and Trends
Technical Standards update
Round Table update – ALDE, UDIA, CCF, PM2/Designer, Electrical, Civil
Frequency
Meetings will occur on a quarterly basis typically:
March
June
September
December
Note: The purpose of the meeting is not to address specific project related issues however working groups can be established as required to resolve industry issues and their outcomes are reported back to the meeting

## Slide 5: Audit Performance, Results & Trends

## Slide 6: 2019 Volumes & timeframes We are delivering to audit timeframes however re-audits are increasing
Chart: Audit volumes and time
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug
Audit Volume | 11 | 35 | 41 | 47 | 72 | 53 | 30 | 36
Re-audit volume | 9 | 7 | 12 | 8 | 15 | 24 | 22 | 21
Audit time | 5.1 | 3.7 | 5 | 5.8 | 7.2 | 7 | 7.3 | 7.3
Re-audit time | 5.9 | 4.3 | 5.2 | 5.7 | 5.9 | 7.1 | 7.1 | 7.4
Year | No of Projects Audited | Total no of Audits conducted
2018 | 391 | 739
YTD 2019 | 244 | 442

## Slide 7: Trends Similar non-compliances have been identified for the past 3 years and unfortunately the volumes are trending upwards with little sign of improvement
As-Built detailing continues to be an issue – predominantly cable detailing inaccuracies
Service Pits installed too low or not to standard
Marker tape misalignment or not installed
Against Audit Policy (Work not compliant to scope)
2019 projection based on last 8 months Non-Compliance volume (Jan – Aug) - footnote

## Slide 8: 2019 Civil Non-Compliances The volume of NC’s per project has increased with marker tape still being the biggest issue
Non-compliance details
Top 3 NC’s based on volume
Marker Tape (610)
Service Pits (474)
UG HV conduit clearances (88)
Top 3 Major (-10) NC’s
Marker Tape (199)
Service Pits (53)
Variation to Documentation (18)
2019 projection based on last 8 months Non-Compliance volume (Jan – Aug) - footnote

## Slide 9: 2019 Electrical Non-Compliance Electrical non-compliances are also on the increase and trending upwards
Non-compliance details
Top 3 NC’s based on volume
PL Poles (503)
Cable Cover Slab Installation (92)
Variation to Documentation (82)
Top 3 Major (-10) NC’s
CHP Cables (22)
Kiosk Sub-Station (14)
Variation to Documentation (11)
2019 projection based on last 8 months Non-Compliance volume (Jan – Aug) - footnote

## Slide 10: 2019 YTD NC Results Continue to identify inaccurate cable detailing issues and of concern is the volume of no/misaligned marker tape
Minor NC’S

## Slide 11: Contractor Rating Comparison Contractor performance has not improved greatly since the introduction of the Rating System in 2018

## Slide 12: Contractor Ratings – 1H 2019 Large number of contractors are underperforming although we do have a number of Superior rated contractors

## Slide 13: Summary
Audit turnaround times from initial audit request to issuing the audit report is < 8 business days
  If projects passed the first audit this would reduce re-audits and result in a quicker turnaround time
Issues still associated with:
  Marker Tape
  Cable detailing inaccuracies
  Service Pits being installed too low
Contractor Ratings
  Civil Contractor Ratings are the lowest since the introduction of the scheme in 2018
  Electrical Contractor Ratings have also declined from Q1 2019
Anecdotally not all companies are performing QA checks prior to requesting final audit which has resulted in:
  Increase in the volume of re-audits
  Increase in non-conformances identified
Powercor expectation is that ALL project have undergone a site inspection including a Quality Control/Assurance check prior to submitting the Final Network Audit Request

## Slide 14: Appendices

## Slide 15: Update heading
Chart: 
| Ave time
 | 10.3
 | 22.0833
 | 33.9833
 | 137.775
 | 18.3658
 | 190.4833
 | 6.0917
 | 2.3333
 | 42.8167
3
Construction
Audit
[insert commentary
Add comments
Performance
Target
V
1. Few projects pass with zero non-conformances, most projects receive an unapproved status and their approval is subject to providing evidence that identified non-conformances have in been fixed. This sometimes happens in real time with the auditor on site or via the contractor providing photographic evidence of the fix at a later date
Chart: Audit volumes and time
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug
Audit Volume | 11 | 35 | 41 | 47 | 72 | 53 | 30 | 36
Re-audit volume | 9 | 7 | 12 | 8 | 15 | 24 | 22 | 21
Audit time | 5.1 | 3.7 | 5 | 5.8 | 7.2 | 7 | 7.3 | 7.3
Re-audit time | 5.9 | 4.3 | 5.2 | 5.7 | 5.9 | 7.1 | 7.1 | 7.4

## Slide 17: Audit Volumes We are not seeing an improvement in performance with an increase in the volume of re-audits
Year | No of Projects Audited | Total no of Audits conducted
2018 | 391 | 739
YTD 2019 | 244 | 442

## Slide 18: Turnaround Times We are continuing to meet turnaround time commitments
Audit turnaround times from initial audit request to issuing the audit report is < 8 business days
  2019 First Audit: 10 audits conducted on day 9 & 2 audits conducted on day 10
  2019 Re-Audits: 2 audits conducted on day 11
Turnaround times will reduce for the first final audit if re-audit numbers are reduced
During May and June all auditors were available and additional resources deployed to assist with the forecasted peak
Note: Turnaround times are based on receiving the initial completed audit request, scheduling the audit, conducting the audit and issuing the audit report - footnote

## Slide 19: Design QA Processes

## Slide 20: Current Project ‘Turn around Times’

## Slide 21: Current performance 48 % of first plan audits are successful.
Chart: Percentage of plans passed on first audit
| Contractor A | Contractor B | Contractor C | Contractor D | Contractor E | Contractor F | Contractor G | Contractor H | Contractor I | Contractor J | Contractor K | Contractor L | Contractor M | Contractor N
2017 | 0.125 | 0 | 0.333 | 0 | 0.176 | 0.229 | 0 | 0.5 | 0.154 | 0.122 | 0.4
2018 | 0.273 | 0.545 | 0.298 | 0.843 | 0.273 | 0.538 | 0.437 | 0.412 | 0.5 | 0.522 | 0.2 | 0.4 | 0.507 | 0.25
2019 | 0.333 | 0.571 | 0.333 | 1 | 0.222 | 0.8 | 0.491 | 0.34 | 0.5 | 0.4 | 0.538 | 0.667 | 0.588 | 0

## Slide 22: Recurring issues
Chart: 2017
| Drafting | Connection Diagrams | Trench Sections | Cable Schedule | P/L Authorisation
 | 116 | 107 | 67 | 43 | 30
Chart: 2018
| Connection Diagrams | Trench Sections | Drafting | P/L Location & Clearance | Tie in Notes
 | 280 | 252 | 174 | 147 | 145
Chart: 2019
| Connection Diagrams | Trench Sections | Drafting | Cable Schedule | Enviroment (Trees)
 | 152 | 127 | 83 | 50 | 49
Accuracy of connection diagrams continues to be an issue.
Drafting quality has shown improvement.
An increase in trench section errors is a worrying trend.
P/L authorisation was an issue early but is now being addressed.
Environment (trees) shows as an increased issue but in reality was a newish process which wasn’t handled well at first but has improved recently.

## Slide 23: ESC Technical Standards Harmonisation Technical Standards Working Group

## Slide 24: Work group members
Anthony James, Technical Standards Manager, CitiPower and Powercor (Lead)
Aza Masoudtehrani, Technical Standards Engineer, CitiPower and Powercor
Jim Tsirikis, Principle Engineer Distribution, United Energy
Max Demko, Senior Engineer, Jemena
Saman De Silva, Principle Engineer, Distribution Standards

## Slide 25: Scope of Technical Standards Harmonisation
Review the civil URD (urban residential development) design and construction standards across all five Victorian Distribution Businesses and where possible align key design and construction parameters across the Victorian Distribution Businesses.
The criteria for alignment will be based on:
Compliance to government regulations and Australian Standards
Least cost, technically acceptable solutions
Constructability
Ease of use and understanding of the standards
In addition to the harmonisation activity the following areas of the standards will also be reviewed1:
CitiPower/Powercor’s2 type 1 & 2 kiosk easements would be reviewed, with the intention of only using type 2 kiosk easements for URDs. This would align with the other distribution businesses.
The potential to install HV cables into conduits for future stages. That is, cables will be capped and then jointed into the future stage.
Decision required:
Endorse project scope
1 As agreed at the Technical Standards Working Group and Construction meeting held on the 5th of July
2 This change only impacts CitiPower/Powercor kiosk reserves, proposed change will align with other DBs

## Slide 26: Deliverables
Gap analysis report outlining difference and commonalities between all five Victorian Distribution Business standards related to URDs
Harmonisation report outlining key design and construction parameters for alignment
Implementation plan & communication strategy for each DB
Implementation of agreed changes to Technical Standards
Decision required:
Endorse deliverables

## Slide 27: Activities
Established Technical Standards working group | 
Determined relevant URD standards across all five DBs | 
Developed gap analysis scope for quotation | 
Obtained quotes from consultants | 
Evaluating quotes from consultants and appointment of successful consultant | 
Completed activities
Gap analysis report | 
In progress activity
13/09/2019

## Slide 28: Proposed timeline
1Date to be confirmed following completion of 22 November milestone
Review, comment and endorse the implementation & communication strategy
Gap analysis finding update
12 December 2019
22 November 2019
11 October 2019
Review gap analysis and agree on harmonisation opportunities
Develop implementation plan & communication strategy
1 November 2019
Complete gap analysis
13 September 2019
25 September 2019
Technical Standards Steering Committee
Technical Standards Working Group
Consultant
Technical Standards Steering Committee meeting
Technical Standards Working Group
Technical Standards Steering Committee
Technical Standards Steering Committee meeting
Technical Standards Steering Committee
Decision required:
Endorse proposed timeline
Appoint consultant
12 July 2019
Technical Standards Working Group
Feedback from Technical Standards Steering Committee regarding updated standards
End of May 2020
Technical Standards published & communicated
Progress update
End of Feb 2020
Q1 2020
(TBC) 1
Technical Standards Steering Committee
Technical Standards Working Group
Technical Standards Steering Committee meeting
Technical Standards Steering Committee meeting
Technical Standards Steering Committee
Review and endorse harmonisation opportunities
(via circulation)
IN PROGRESS

## Slide 29: ESC Update
1H 2019

## Slide 30: The Essential Services Commission (ESC) Service Improvement Commitments (SIC)
Service Improvement Commitments
Improve developers and contractors understanding of distribution business’ policies and practises, or how they can influence them
Minimising avoidable delays in connecting greenfield developments to existing distribution networks
Improving how technical standards are managed and communicated
Improve audit processes and practises
Promoting efficient competition in connection services (or component parts)
Resource constraints – evidence that resourcing is sufficiently aligned to increased residential development activities
Performance Commitments
Master Plan and Stage Scopes
‘As-built’ Construction Audit
Design Approvals
Change process to allow Developer to submit Master Plan and Stage Scopes to Powercor for review/ approval
Complete audit of design plan in less than 20 business days
Undertake construction audit within 5 to 8 business days of compliant audit request
Construction ‘tie-in’
New Process – offer option of ‘tie-in’ within 20 business days from achieving practical completion
Grant Practical Completion in less than 10 business days
Grant Practical Completion

## Slide 31: ESC Governance meeting #5 was held in early July
ESC outcome sought
Improving developers and contractors understanding of the distribution business’ policies and practices and how they can influence them
Status
On track
1
Minimising avoidable delays in connecting greenfield developments to the existing distribution network
On track
Improving how technical standards are managed and communicated
ON track
2
3
Promoting efficient competition in connection services
Resource constraints – evidence that resourcing is sufficiently aligned to increased residential development activities
Reviewing and improving audit processes
4
5
6
On track
Completed
On track
Established Technical Standards Harmonisation Committee
Held first Technical Standards Harmonisation Committee meeting and engaged consultant to undertake ‘gap’ analysis
Commenced development of an IT portal to assist stakeholders track progress of their project (go-live expected later this year)
Developed 2 new processes that will be subject of follow up workshops
  Master Plan review
  20 day construction tie-in
Tabled a detailed report of our performance against 5 key stages of Option 2 development
Highlights

## Slide 32: Powercor has committed to improving in 5 key stages of the connection process
1
2
3
4
5
Master
plan review
Design
review
Practical completion
Construction ‘tie-in’
Construction
audit
Replace staged scopes with a Master Plan review process – target to complete Master Plan reviews in 10 business days
Target completion of design plan audits and re-audits within 20 business days
Complete construction audit (from request to final report) within 5 to 8 business days
Grant practical completion in less than 10 business days from request
Meet customer dates and implement new process to offer the option of a 20-business day construction tie in
New process 16.0 days2
Old process 34.0 days
6.1 days
2.3 days
18.4 days
New process being implemented
90% customer target date met in June
Stage
Target
1H19 Performance1
All performance measures are in business days
New process is in trial and we only have a small sample size. We expect to roll the new process out in 2H2019

## Slide 33: Role of the PM2

## Slide 34: Overview & Proposal
Overview
Following discussions from the last industry forum a working group was to be formed to determine the role of the PM2
In some instances not all PM2’s are across all activities on an Option 2 project and greater clarity around the responsibilities were required
This includes being the key contact between Powercor and the Developer
Proposal
Developer appoints and nominates one person/organisation who is accountable and responsible for their project. This role will oversee the construction and project manage all aspects of the Option 2 project and they will be nominated on the tender document
Responsibilities include:
    Conduit/one point of contact between Powercor and the Developer
    Co-ordinate construction activities on-site
    Submits all relevant documentation
    Responsible for rectification of audit non-compliances on site including re-audit invoice payments

## Slide 35: Workshop Introductions

## Slide 36: Process improvement focus areas
SOC = Statement of compliance
Application response | Customer acceptance | Scope Development | Design plan development | Design Plan Audit | Construction | Construction Audit | Practical Completion | Construction Tie-in
Powercor | Developer | Powercor | Developer | Powercor | Developer | Powercor | Powercor | Powercor
10.3 | 22.1 | 34.0 | 137.8 | 18.4 | 190.5 | 6.1 | 2.3 | 42.8
Timelines based on projects that were completed in 1H2019 which took an average of ~421 business days from Application to SOC1
Developer application
Consent for SOC
Master plan review
Design review & Safety in Design
Tie in process
IT Systems

## Slide 37: Upcoming: Process improvement workshop
Electric House, 40 Market St. Tuesday 8th October, 9am-1pm
Topics to be covered
    Tie in process
    Master Plan Review
    Design review and Safety in Design
    IT systems
Who should attend.
Everybody welcome, however we are targeting engagement with:
    PM2’s
    Design houses