## Zone substations
Zone Substation |  | On-load Capacity - Nameplate Rating (MVA) | Hot or Cold Spare Capacity - Nameplate Rating (MVA) (note 1) | Total Capacity - Nameplate Rating (MVA) | Cyclic N-1 Rating (MVA) | Hours Load is ≥ 95% of MD (note 4) | Station Power Factor at MD | Load Transfers (MVA) | Generation Capacity <1MW (MW) (notes 2 & 6) | Generation Capacity >1MW (1MW) (note 2) | Actual Demand (MVA) (note 3) | 50% PoE Forecast Demand (MVA) |  |  |  |  | % Load Above N-1 Rating (2020) | Energy at Risk (MWh) (N-1 50% PoE) |  |  |  |  | Hours at Risk (N-1 50% PoE)
[11 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 |  | 2020 | 2021 | 2022 | 2023 | 2024 | 2020 | 2021 | 2022 | 2023 | 2024
ATS 66kV
LV | S | 99 |  | 99 | 79.8 | 4 | 0.98362 | 14.1 | 20.9 | - | 106.7595 | 97.8 | 99.9 | 104.4 | 100.7 | 104.1 | 22.56% | 155.6459 | 206.622 | 346.4165 | 228.1216 | 336.2907 | 26 | 31 | 44 | 32 | 44
| W | 99 |  | 99 | 95.4 | 4 | 0.99166 | 35 | 20.9 | - | 70.1461 | 70.3078 | 73.0169 | 73.6179 | 72.6208 | 73.5939 | -
WBE | S | 99 |  | 99 | 82.8 | 4 | 0.99121 | 7.2 | 16.8 | 11.7 | 101.856 | 112.2809 | 120.3922 | 128.8921 | 135.1583 | 141.0531 | 35.6% | 720.3055 | 1284.577 | 2077.231 | 2782.4734 | 3537.389 | 71.75 | 101.5 | 138 | 164.75 | 194
| W | 99 |  | 99 | 92.2 | 7 | 0.99126 | 40.8 | 16.8 | 11.7 | 71.5751 | 83.53 | 85.6497 | 88.9248 | 92.4119 | 94.7426 | -
ATS/BLTS 66kV
AC | S | 40 |  | 40 | 30 | - | 0.95 | - | - | - | 2.0421 | 1.9258 | 1.9247 | 1.9122 | 1.9467 | 1.9792 | -
| W | 40 |  | 40 | 30 | - | 0.91304 | - | - | - | 16.6625 | 2.0455 | 1.9851 | 1.9791 | 2.0012 | 2.0907 | -
AL | S | 30 |  | 30 | 0 | 4 | 1 | 0 | 2.5 | - | 20.3776 | 21.4971 | 21.9452 | 21.6823 | 22.0897 | 22.1701 | 100% | 41145.748 | 42083.5902 | 41533.267 | 42388.1889 | 42565.3572 | 8760 | 8760 | 8760 | 8760 | 8760
| W | 30 |  | 30 | 0 | - | 1 | 33 | 2.5 | - | 16.7744 | 16.9043 | 16.8507 | 16.8507 | 17.0336 | 17.7189 | 100%
BMH | S | 27 |  | 27 | 19.1 | 4 | 1 | 4.4 | 6.6 | - | 27.2961 | 27.4009 | 29.2099 | 30.825 | 32.7501 | 34.2746 | 43.46% | 292.3086 | 513.1784 | 825.2718 | 1341.8573 | 2045.4325 | 125 | 219 | 355 | 543 | 783
| W | 27 |  | 27 | 20.1 | 13 | 1 | 7.5 | 6.6 | - | 24.0782 | 22.1818 | 23.7983 | 25.2059 | 26.9298 | 28.4087 | 10.36%
LVN11 | S | 30 |  | 30 | 0 | 808 | 0.992 | 1.5 | - | - | 12.5 | 12.7188 | 12.9231 | 12.7956 | 12.663 | 12.6773 | 100%
| W | 30 |  | 30 | 0 | 312 | 0.992 | 1.5 | - | - | 12.5 | 13.1279 | 12.996 | 12.9119 | 13.0364 | 12.9253 | 100%
LVN22 | S | 99 |  | 99 | 79.7 | - | 0.99748 | - | 1.5 | - | 67.1082 | 69.6441 | 70.5523 | 70.3973 | 71.7935 | 72.1905 | -
| W | 99 |  | 99 | 85 | - | 0.99729 | - | 1.5 | - | 62.5062 | 65.8813 | 65.7198 | 65.7349 | 66.5411 | 68.5347 | -
BATS 66kV
ART | S | 20 |  | 20 | 13.6 | 4 | 0.98765 | 4.5 | 2.4 | 6.8 | 14.1319 | 12.081 | 12.5182 | 13.3152 | 12.7547 | 12.9605 | -
| W | 20 |  | 20 | 15.2 | 4 | 0.99281 | 5.3 | 2.4 | - | 13.0816 | 10.5884 | 11.2132 | 11.3746 | 11.2784 | 10.804 | -
BAN | S | 120 |  | 120 | 96.4 | - | 0.99048 | 6.8 | 13.1 | 6.1 | 85.6958 | 78.2317 | 82.6485 | 86.0857 | 85.4605 | 89.1767 | -
| W | 120 |  | 120 | 104.4 | - | 0.99613 | - | 13.1 | 6.1 | 76.8044 | 69.0401 | 72.4061 | 75.0781 | 77.6471 | 77.1021 | -
BAS | S | 99 |  | 99 | 76 | 4 | 0.97324 | 8.7 | 14.6 | 7.2 | 78.3487 | 68.8698 | 72.3047 | 75.8817 | 74.8699 | 77.6102 | -
| W | 99 |  | 99 | 84.6 | 9 | 0.98348 | 20.3366 | 14.6 | 7.2 | 69.3853 | 62.2243 | 65.4149 | 67.9925 | 70.322 | 69.5508 | -
BETS 66kV
BGO | S | 66 |  | 66 | 38.5 | 5 | 1 | 23.8 | 7.6 | - | 49.7907 | 43.5824 | 43.9062 | 44.2062 | 44.4118 | 44.9333 | 13.2% | 24.6913 | 28.5964 | 32.6381 | 35.6302 | 44.3378 | 13 | 14 | 16 | 17 | 21
| W | 66 |  | 66 | 45.4 | 9 | 1 | 14.7 | 7.6 | - | 35.6572 | 32.1226 | 32.5607 | 32.4027 | 32.3006 | 31.9435 | -
CMN | S | 66 |  | 66 | 43 | - | 0.98893 | - | 8 | - | 30.6451 | 23.8993 | 24.0373 | 24.4514 | 24.2383 | 24.3894 | -
| W | 66 |  | 66 | 49.5 | - | 0.93305 | - | 8 | - | 23.8803 | 19.6893 | 19.6021 | 19.3764 | 19.1699 | 18.9232 | -
CTN | S | 39.5 |  | 39.5 | 33.7 | - | 0.99537 | - | 4.2 | - | 20.5658 | 17.7824 | 16.9326 | 16.5036 | 16.1161 | 15.9695 | -
| W | 39.5 |  | 39.5 | 38.4 | - | 0.9596 | - | 4.2 | - | 17.1803 | 13.7368 | 13.488 | 13.1498 | 12.7928 | 12.3827 | -
EHK | S | 54 |  | 54 | 36.4 | 4 | 0.99629 | 17.9 | 8.8 |  | 51.8 | 45.6 | 45.7 | 46.2 | 46.9 | 47.7 | 25.27% | 246.9 | 257.1434 | 290.6132 | 358.2471 | 432.9594 | 82.25 | 84.75 | 91.5 | 105.75 | 119.25
| W | 54 |  | 54 | 41 | 3 | 0.99744 | 15.8 | 8.8 | - | 37.2617 | 34.6976 | 35.0137 | 35.342 | 35.6205 | 35.3522 | -
MRO | S | 27 |  | 27 | 18.3 | 6 | 1 | 4 | 5.7 | - | 23.9908 | 20.8 | 20.4 | 20.6 | 20.3 | 20.2 | 13.66% | 19.1 | 12.4 | 16.1 | 11.2 | 9.8 | 21 | 15 | 18 | 15 | 14
| W | 27 |  | 27 | 20.2 | 4 | 0.99454 | 3.4 | 5.7 | - | 17.8085 | 14.5512 | 14.2147 | 13.9952 | 13.8041 | 13.4545 | -
DPTS 66kV
MLN | S | 99 |  | 99 | 79.8 | 5 | 0.97518 | 4.4 | 13.3 | - | 71.4445 | 71.1803 | 74.6061 | 79.5468 | 84.581 | 89.4795 | -
| W | 99 |  | 99 | 87.6 | 11 | 1 | 12.8 | 13.3 | - | 44.8475 | 51.399 | 54.4405 | 57.3687 | 60.9367 | 63.3023 | -
SU | S | 99 |  | 99 | 93 | 7 | 0.99884 | 7 | 11.9 | - | 85.8182 | 101.0349 | 107.544 | 109.545 | 112.253 | 114.3011 | 8.64% | 79.427 | 288.8652 | 383.5789 | 538.0069 | 676.7713 | 22.75 | 47 | 56.5 | 70.75 | 81.75
| W | 99 |  | 99 | 99 | 4 | 1 | 71.2 | 11.9 | - | 75.7643 | 82.807 | 85.6633 | 87.2827 | 89.0574 | 89.2848 | -
TNA | S | 66 |  | 66 | 47.6 | 7 | 0.95152 | 10.3 | 10.6 | 8.8 | 43.0738 | 51.4696 | 55.9397 | 59.2543 | 69.9231 | 73.359 | 8.129% | 15.1332 | 70.3148 | 162.7499 | 841.5988 | 1324.9785 | 7.75 | 23 | 41.5 | 155.5 | 243.25
| W | 66 |  | 66 | 47.6 | 4 | 0.96355 | 50.9 | 10.6 | 8.8 | 42.3696 | 43.4758 | 45.9658 | 50.5716 | 54.0057 | 55.2517 | -
FBTS 66kV
DLF | S | 66 |  | 66 | 40 | - | 0.96316 | - | - | - | 19.9433 | 16.9309 | 17.5725 | 18.4395 | 19.5602 | 20.4698 | -
| W | 66 |  | 66 | 46.2 | - | 0.98496 | - | - | - | 13.3046 | 12.0325 | 12.8346 | 13.5866 | 14.2032 | 14.3756 | -
GTS 66kV
CLC | S | 79 |  | 79 | 50.4 | - | 1 | - | 5.3 | 2.9 | 38.4335 | 33.3624 | 33.9066 | 36.2704 | 35.5432 | 36.2654 | -
| W | 79 |  | 79 | 56.1 | - | 1 | - | 5.3 | 2.9 | 36.5129 | 29.0803 | 30.0117 | 30.5009 | 31.0736 | 30.6848 | -
CRO | S | 60 |  | 60 | 34.3 | 3 | 0.92982 | 1.9 | 4 | - | 31.3173 | 28.0604 | 29.5751 | 31.1345 | 30.1492 | 30.5593 | -
| W | 60 |  | 60 | 38 | 11 | 0.99 | 20.1 | 4 | - | 26.893 | 20.4513 | 20.6877 | 20.6471 | 20.5832 | 20.2768 | -
DDL | S | 66 |  | 66 | 39.7 | 2 | 0.98778 | 10.7 | 13.7 | - | 57.2265 | 64.0699 | 66.7788 | 66.2577 | 67.2999 | 74.2884 | 61.39% | 304.4696 | 383.3093 | 367.1522 | 402.3119 | 693.0228 | 36 | 43 | 41 | 48 | 83
| W | 66 |  | 66 | 47.2 | 3 | 0.99737 | 8 | 13.7 | - | 38.8457 | 34.4203 | 35.4793 | 35.9814 | 36.6134 | 36.5084 | -
FNS | S | 99 |  | 99 | 87.2 | - | 0.99704 | - | 5.9 | 1 | 38.255 | 46.2692 | 50.2804 | 53.2736 | 52.3297 | 52.887 | -
| W | 99 |  | 99 | 98.6 | - | 0.99707 | - | 5.9 | 1 | 29.4873 | 35.5398 | 36.2489 | 36.4189 | 36.5919 | 36.0019 | -
GB | S | 37.5 |  | 37.5 | 37.6 | - | 0.98551 | - | 0.8 | - | 12.4801 | 13.2097 | 13.3067 | 14.164 | 13.5858 | 13.4677 | -
| W | 37.5 |  | 37.5 | 37.6 | - | 0.99219 | - | 0.8 | - | 14.5805 | 10.4423 | 9.8801 | 9.8661 | 9.8201 | 9.5121 | -
GCY | S | 66 |  | 66 | 37.8 | 5 | 0.93126 | 16 | 2.8 | 5.5 | 48.9717 | 47.8 | 50 | 53.2 | 52.1 | 53.6 | 26.46% | 162.7 | 267 | 498.1 | 400.8 | 531.6 | 46 | 67 | 112 | 94 | 118
| W | 66 |  | 66 | 43.9 | 6 | 0.89197 | 15 | 2.8 | 5.5 | 34.8236 | 30.3488 | 30.8652 | 31.4329 | 31.4155 | 31.0302 | -
GL | S | 80 |  | 80 | 47.6 | 3 | 0.99461 | 18.5 | 9.5 | - | 59.7327 | 63 | 66.8 | 67.2 | 68.4 | 68.5 | 32.35% | 175.3 | 299 | 314.5 | 360.6 | 365.7 | 33 | 46 | 48.75 | 54 | 53.75
| W | 80 |  | 80 | 47.6 | 5 | 1 | 21.9 | 9.5 | - | 48.2832 | 45.3384 | 47.0214 | 47.0654 | 47.2984 | 46.8724 | -
GLE | S | 79.5 |  | 79.5 | 66.9 | - | 0.98044 | 21 | 7.1 | 1.2 | 53.3477 | 48.7687 | 52.1838 | 55.4834 | 55.0367 | 55.3971 | -
| W | 79.5 |  | 79.5 | 68.8 | - | 1 | - | 7.1 | 1.2 | 42.4307 | 34.3202 | 35.1205 | 35.4394 | 35.65 | 35.2589 | -
WIN | S | 13.5 | 7 | 20.5 | 10.5 | - | 0.97059 | - | 2 | - | 7.7629 | 7.6756 | 7.9406 | 8.255 | 8.1123 | 8.1574 | -
| W | 13.5 | 7 | 20.5 | 10.5 | - | 0.96552 | - | 2 | - | 8.8568 | 6.3812 | 6.4839 | 6.4968 | 6.5325 | 6.4471 | -
WPD | S | 79.5 |  | 79.5 | 56.8 | 3 | 0.99879 | 13 | 15 | - | 78.7064 | 90.682 | 90.5199 | 92.3036 | 95.1569 | 99.3409 | 59.65% | 649.8337 | 642.6904 | 724.3897 | 871.7993 | 1128.3029 | 60 | 59 | 66 | 78 | 99
| W | 79.5 |  | 79.5 | 62.6 | 4 | 1 | 19.8 | 15 | - | 62.7173 | 56.4329 | 58.0812 | 59.0733 | 59.9625 | 59.8505 | -
HOTS 66kV | [5 empty] | -
CHM | S | 33 |  | 33 | 0 | 3 | 1 | 0 | 0.5 | - | 3 | 2.4 | 2.4 | 2.3 | 2.3 | 2.2 | 100% | 7722.9169 | 7669.2861 | 7470.1317 | 7128.4176 | 6825.7048 | 8760 | 8760 | 8760 | 8760 | 8760
| W | 33 |  | 33 | 0 | 5 | 0.99143 | 1.3 | 0.5 | - | 3 | 2.7 | 2.7 | 2.7 | 2.6 | 2.6 | 100%
HSM | S | 40.5 |  | 40.5 | 39.7 | 5 | 0.99546 | 4.2 | 8.7 | - | 42.2209 | 37.537 | 38.513 | 39.351 | 37.916 | 37.198 | -
| W | 40.5 |  | 40.5 | 40.4 | 3 | 1 | 4 | 8.7 | - | 31.8882 | 31.989 | 32.5311 | 32.1089 | 31.1418 | 30.3086 | -
NHL | S | 20 |  | 20 | 13 | - | 0.99153 | 0 | 2.1 | - | 11.3809 | 9.6262 | 9.6743 | 9.6552 | 9.1903 | 8.8457 | -
| W | 20 |  | 20 | 16.2 | - | 0.98095 | - | 2.1 | - | 9.0249 | 8.4655 | 8.425 | 8.255 | 7.918 | 7.577 | -
STL | S | 27 |  | 27 | 18.5 | 9 | 0.96951 | 4.5 | 2.8 | - | 19.1691 | 15.2139 | 14.8728 | 14.5328 | 14.2857 | 14.1117 | -
| W | 27 |  | 27 | 18.8 | 7 | 0.98953 | 4.5 | 2.8 | - | 14.7889 | 18.0826 | 16.7874 | 16.6306 | 16.1832 | 15.4598 | -
KGTS 66kV
CHA | S | 27 |  | 27 | 15.2 | 5 | 0.99338 | 2.2 | 2.8 | - | 15.0886 | 12.0652 | 12.0432 | 12.0222 | 11.7106 | 11.6855 | -
| W | 27 |  | 27 | 15.2 | 6 | 0.99375 | 0.3 | 2.8 | - | 15.3662 | 13.945 | 14.6424 | 15.3104 | 15.6743 | 15.457 | -
SHL | S | 40.5 |  | 40.5 | 36.7 | 8 | 1 | 1.4 | 6.1 | - | 38.9072 | 37.5458 | 37.5357 | 38.1869 | 38.0556 | 38.199 | 2.305%
| W | 40.5 |  | 40.5 | 40.4 | 4 | 0.97749 | 1.7 | 6.1 | - | 27.7212 | 31.283 | 33.3918 | 35.1585 | 36.4874 | 36.3037 | -
KTS 66kV
GSB | S | 66 |  | 66 | 49.5 | - | 1 | - | 5.4 | - | 20.8219 | 18.4192 | 19.6391 | 20.6804 | 21.0111 | 21.5384 | -
| W | 66 |  | 66 | 49.5 | - | 1 | - | 5.4 | - | 19.6853 | 21.11 | 21.7043 | 21.9509 | 22.5201 | 22.7527 | -
SA | S | 93 |  | 93 | 76.2 | 5 | 0.99492 | 15 | 13.8 | - | 85.0186 | 78.3695 | 76.8847 | 78.1874 | 79.9576 | 81.4475 | 2.847%
| W | 93 |  | 93 | 76.2 | 10 | 0.99837 | 22.5 | 13.8 | - | 57.7789 | 58.4191 | 59.6078 | 60.5502 | 62.0333 | 62.1709 | -
SSE | S | 99 |  | 99 | 89.7 | - | 0.92006 | - | 6.3 | - | 69.6747 | 75.6374 | 76.8782 | 78.9109 | 80.3631 | 81.7385 | -
| W | 99 |  | 99 | 99 | - | 0.92879 | - | 6.3 | - | 65.6929 | 64.5414 | 65.8777 | 66.4312 | 67.4703 | 67.4337 | -
SU | S | 99 |  | NOTE 9 | NOTE 9 | NOTE 9 | NOTE 9 | NOTE 9 | NOTE 9 | NOTE 9 | NOTE 9 | NOTE 9 | NOTE 9 | NOTE 9 | NOTE 9 | NOTE 9 | NOTE 9 | 79 | 289 | 384 | 538 | 677 | 23 | 47 | 57 | 71 | 82
| W | 99 |  | NOTE 9 | NOTE 9 | NOTE 9 | NOTE 9 | NOTE 9 | NOTE 9 | NOTE 9 | NOTE 9 | NOTE 9 | NOTE 9 | NOTE 9 | NOTE 9 | NOTE 9 | NOTE 9
WND | S | 66 |  | 66 | 38.3 | - | 0.99571 | - | 8.5 | - | 27.9424 | 28.7852 | 29.4198 | 30.0372 | 30.7404 | 31.6969 | -
| W | 66 |  | 66 | 43.2 | - | 1 | - | 8.5 | - | 27.1953 | 27.1848 | 27.7633 | 28.1736 | 28.8242 | 28.9413 | -
RCTS 66kV
BBD | S | 66 |  | 66 | 47.2 | - | 0.99291 | - | 0.2 | - | 28.1016 | 28.9554 | 27.9452 | 27.8659 | 28.305 | 27.5854 | -
| W | 66 |  | 66 | 50 | - | 0.99265 | - | 0.2 | - | 19.8117 | 8.2553 | 7.1692 | 6.7093 | 6.7124 | 7.1888 | -
MBN | S | 59 |  | 59 | 37.6 | 7 | 0.9976 | 11.7 | 5.7 | - | 41.4587 | 41.8 | 42.6 | 44.5 | 45.7 | 46.8 | 11.17% | 43.1 | 65.4 | 146.4 | 216.1 | 291.8 | 27 | 34 | 58 | 74 | 92
| W | 59 |  | 59 | 40.8 | 5 | 0.99617 | 20.6 | 5.7 | - | 26.8583 | 15.5814 | 16.856 | 17.6264 | 18.3157 | 18.5548 | -
MDA | S | 66 |  | 66 | 39.7 | 9 | 0.95257 | 16.5 | 5.6 | - | 48.7944 | 46.6 | 47.4 | 48.8 | 50.9 | 52 | 17.38% | 124.7 | 158.4 | 245.1 | 417.2 | 531.4 | 46 | 54 | 73 | 103 | 120
| W | 66 |  | 66 | 44.6 | 3 | 0.97619 | 19.7 | 5.6 | - | 34.1821 | 19.4188 | 20.8786 | 21.9911 | 22.8408 | 23.2113 | -
SHTS 66kV
CME | S | 40.5 |  | 40.5 | 32.7 | 5 | 0.99974 | 1 | 6.9 | 9.45 | 39.3882 | 36.9 | 36.5 | 37.8 | 38.3 | 38.8 | 12.84% | 20.8 | 15.6 | 37.2 | 48.4 | 62.5 | 16 | 13 | 23 | 27 | 34
| W | 40.5 |  | 40.5 | 39.2 | 7 | 1 | 0 | 6.9 | 9.45 | 25.8583 | 27.379 | 27.518 | 29.107 | 30.331 | 30.639 | -
ECA | S | 39.5 |  | 39.5 | 34.6 | - | 1 | 0.6 | 7.4 | - | 33.0976 | 37.8 | 36.6 | 36.5 | 36.8 | 36.9 | 9.249% | 19.1 | 6.9 | 6.3 | 8 | 8.9 | 15 | 8 | 8 | 9 | 9
| W | 39.5 |  | 39.5 | 40.4 | - | 0.99644 | - | 7.4 | - | 22.5709 | 25.8909 | 27.0097 | 27.8122 | 28.7749 | 29.1405 | -
KYM | S | 40.5 |  | 40.5 | 33.8 | - | 0.99661 | - | 6.5 | - | 30.1524 | 30.9418 | 31.1519 | 31.5562 | 31.6312 | 31.7563 | -
| W | 40.5 |  | 40.5 | 38.8 | - | 0.9789 | - | 6.5 | - | 23.3797 | 21.4011 | 21.9265 | 22.6633 | 23.2831 | 23.513 | -
MNA | S | 66 |  | 66 | 37 | 2 | 0.98345 | 7.8 | 5.9 | 1 | 42.7139 | 44.6 | 45.1 | 45.8 | 46.4 | 46.6 | 20.54% | 186.8 | 223.5 | 280.4 | 331.3 | 350.1 | 74 | 82 | 96 | 109 | 112
| W | 66 |  | 66 | 42.5 | 11 | 1 | 7.3162 | 5.9 | 1 | 28.8699 | 27.9265 | 29.2827 | 30.4529 | 31.397 | 31.8711 | -
NKA | S | 39.5 |  | 39.5 | 30.5 | 6 | 0.97595 | 0.6 | 6.5 | - | 29.3849 | 30.2285 | 29.1783 | 29.5783 | 29.8014 | 30.4315 | -
| W | 39.5 |  | 39.5 | 30.5 | 7 | 0.99291 | 0 | 6.5 | - | 27.163 | 26.0717 | 27.1264 | 27.9599 | 28.8664 | 29.172 | -
SHN | S | 66 |  | 66 | 40 | - | 0.9973 | - | 5.9 | 1 | 36.4793 | 36.6966 | 36.8848 | 37.091 | 38.0771 | 38.905 | -
| W | 66 |  | 66 | 44.1 | - | 0.99617 | - | 5.9 | 1 | 24.7629 | 25.7778 | 27.0843 | 28.1885 | 29.2636 | 29.7767 | -
SHP | S | 66 |  | 66 | 36.6 | - | 0.94681 | - | 3.4 | - | 22.9537 | 20.3656 | 23.6519 | 24.3955 | 24.3721 | 24.3731 | -
| W | 66 |  | 66 | 41.9 | - | 1 | - | 3.4 | - | 17.9691 | 18.821 | 19.7067 | 20.1826 | 20.6586 | 20.7018 | -
STN | S | 79 |  | 79 | 61.9 | - | 0.99789 | 1.4 | 7.5 | - | 48.9972 | 45.8578 | 47.267 | 48.9775 | 49.4178 | 50.2025 | -
| W | 79 |  | 79 | 61.9 | - | 0.98485 | - | 7.5 | - | 32.2044 | 33.7968 | 35.862 | 37.4775 | 39.0578 | 39.5869 | -
TGTS 66kV
CDN | S | 20 |  | 20 | 17.2 | - | 0.9875 | - | 1.9 | - | 13.6439 | 13.8751 | 13.7291 | 13.5619 | 13.6505 | 13.7542 | -
| W | 20 |  | 20 | 18.2 | - | 0.98378 | - | 1.9 | - | 15.1465 | 17.0346 | 17.357 | 17.5443 | 17.8047 | 17.9509 | -
COB | S | 26 |  | 26 | 15 | 9 | 0.88489 | 3.8 | 0.1 | - | 14.2904 | 13.8466 | 13.8801 | 14.0969 | 14.1708 | 14.2042 | -
| W | 26 |  | 26 | 15 | 7 | 0.91558 | 5 | 0.1 | - | 13.5823 | 14.0696 | 14.2899 | 14.4458 | 14.7467 | 14.7306 | -
HTN | S | 39.5 |  | 39.5 | 34.2 | - | 1 | 0 | 2.7 | - | 28.0501 | 24.0898 | 24.4769 | 24.795 | 24.83 | 24.953 | -
| W | 39.5 |  | 39.5 | 38.4 | - | 1 | - | 3.4 | - | 25.0837 | 29.5552 | 30.2284 | 30.6648 | 31.1012 | 31.4725 | -
KRT | S | 40.5 |  | 40.5 | 33.4 | - | 0.99623 | 0 | 2.6 | - | 24.1426 | 23.7872 | 24.0467 | 24.4114 | 24.5877 | 25.2169 | -
| W | 40.5 |  | 40.5 | 37.6 | - | 0.99635 | - | 2.6 | - | 23.9963 | 28.6109 | 29.2329 | 29.9194 | 31.1151 | 31.0789 | -
PLD | S | 32 |  | 32 | 22.1 | - | 1 | 0 | 3.6 | - | 16.6908 | 15.6631 | 16.0502 | 16.4383 | 16.5018 | 16.9333 | -
| W | 32 |  | 32 | 24 | - | 1 | - | 3.6 | - | 18.5405 | 19.2415 | 19.7683 | 20.0609 | 20.4242 | 20.622 | -
TRG | S | 27 |  | 27 | 19.2 | 7 | 0.99573 | 5.6 | 2.2 | - | 19.8057 | 19.0659 | 19.0922 | 19.0079 | 19.1523 | 19.3568 | - | 233 | 274.1 | 323.1 | 381.3 | 435 | 144 | 156 | 170 | 187 | 201
| W | 27 |  | 27 | 19.4 | 7 | 0.99608 | 11.4 | 2.2 | - | 22.422 | 24.1 | 24.4 | 24.8 | 25.2 | 25.5 | 24.23%
WBL | S | 79.5 |  | 79.5 | 64 | 3 | 0.99216 | 11.2 | 4.7 | 1.5 | 52.2157 | 45.1309 | 46.1924 | 48.3888 | 49.0629 | 50.2512 | - | 101 | 193 | 393 | 629 | 944 | 48 | 92 | 166 | 261 | 366
| W | 79.5 |  | 79.5 | 68.7 | 4 | 0.99783 | 12.1 | 4.7 | 1.5 | 44.7077 | 43.8694 | 45.6796 | 47.081 | 48.564 | 49.6644 | -
WETS 66kV
OYN | S | 27 |  | 27 | 15.2 | - | 0.93103 | 0 | 1.6 | - | 8.8625 | 6.928 | 7.0303 | 7.14 | 7.2518 | 7.2191 | -
| W | 27 |  | 27 | 15.2 | - | 0.8913 | - | 1.6 | - | 8.2457 | 1.0865 | 1.4713 | 1.5995 | 1.6649 | 1.5392 | -
RVL | S | 19.5 |  | 19.5 | 20.4 | - | 1 | 0.6 | 0.8 | - | 21.6949 | 20.6336 | 21.0467 | 21.2298 | 21.5059 | 21.5909 | 1.145%
| W | 19.5 |  | 19.5 | 22.9 | - | 0.96471 | - | 0.8 | - | 13.121 | 6.0328 | 6.7667 | 7.1021 | 7.1197 | 7.1723 | -
WMN | S | 33 | 13.5 | 46.5 | 17.2 | 11 | 0.98413 | 3.4 | 0.05 | - | 22.6872 | 21.3 | 20.9 | 20.8 | 20.9 | 21.4 | 23.84% | 337 | 261 | 221 | 250 | 371 | 456 | 379 | 338 | 368 | 488
| W | 33 | 13.5 | 46.5 | 20.2 | 3 | 0.96429 | 5.3 | 0.05 | - | 12.3653 | 8.2211 | 7.7813 | 8.0425 | 8.166 | 8.0885 | -
Note 1: * indicates cold standby transformer
Note 2: Generation capacity <1MW is mostly solar PV
Note 3: The 2017 demand figures are actuals for summer and forecast for winter.
Note 4: Where load is above N-1 rating
Note 5: Supplied from DPTS from late 2017
Note 6: TNA generation <1MW based on load transfers to TNA
Note 6: TNA not commissioned in winter 2017
Note 8: LVN11 - used last years forecast. No actual value
Note 9: SU Transferred to DPTS in 2017, MLN transferred to DPTS in 2018

## Sub-transmission lines
Subtransmission line |  | Line Rating (MVA) | Hours Load is 95% of MD | Power Factor at MD | Load Transfers (MVA) | Generation Capacity (MW) | Historical Demand Worst case N-1 Scenario (MVA) | Forecast Demand Worst case N-1 Scenario (MVA) |  |  |  |  | % Load Above N-1 Rating (2020) | Energy at Risk (MWh) (N-1 50% PoE) |  |  |  |  | Hours at Risk (N-1 50% PoE)
[7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 |  | 2020 | 2021 | 2022 | 2023 | 2024 | 2020 | 2021 | 2022 | 2023 | 2024
ATS 66kV
ATS-HCP | S | 109.7 | 4 | 0.94459 | 19.8 |  | 118.5 | 129.9 | 140.3 | 152.7 | 159.6 | 167.9 | 18.41% | 74 | 217 | 496 | 718 | 1042 | 9 | 20 | 33 | 43 | 54
| W | 134.9 | 4 | 0.96257 | 40.8 |  | 77.7 | 92.1 | 94.3 | 98.6 | 103.3 | 106 | -
ATS-WBE | S | 109.7 | 4 | 0.94286 | 19.8 |  | 118.8 | 130.2 | 140.6 | 153 | 160.2 | 168.4 | 18.69% | 82 | 230 | 521 | 751 | 1078 | 10 | 21 | 34 | 43 | 53
| W | 134.9 | 4 | 0.96123 | 40.8 |  | 77.8 | 92.3 | 94.5 | 98.8 | 103.4 | 107.3 | -
HCP-WBE | S | 109.7 | 4 | 0.962 | 19.8 |  | 104 | 115.1 | 123.7 | 134 | 139.3 | 146 | 4.923%
| W | 134.9 | 4 | 0.97511 | 40.8 |  | 70 | 82.8 | 84.7 | 88.5 | 92.5 | 94.9 | -
ATS-LV1 | S | 135.5 |  | 0.95242 |  |  | 119.2 | 109 | 109.8 | 115.4 | 111 | 115.2 | -
| W | 142.3 |  | 0.99022 |  |  | 72.3 | 72.1 | 75.6 | 76 | 74.8 | 75.8 | -
ATS-LV2 | S | 135.5 |  | 0.94604 |  |  | 121.5 | 109.8 | 111.8 | 117.5 | 113 | 117.5 | -
| W | 142.3 |  | 0.99022 |  |  | 72.3 | 72.9 | 75.6 | 76 | 75.6 | 76.6 | -
ATS/BLTS 66kV
ATS-AC | S | 102.3 |  | 0.98958 |  |  | 29.1 | 27.6 | 28.4 | 29.6 | 28.8 | 26.8 | -
| W | 108 |  | 1 |  |  | 31.9 | 24.2 | 24.1 | 23.8 | 24.2 | 23.8 | -
AC-CPL | S | 102.9 |  | 0.99278 |  | 22.5 | 27.9 | 26.4 | 27.3 | 28.4 | 27.7 | 25.7 | -
| W | 108 |  | 1 |  | 22.5 | 23.3 | 23.1 | 23.1 | 22.7 | 23.1 | 22.6 | -
CPL-AL | S | 91.5 |  | 1 |  | 22.5 | 21.6 | 19.1 | 21 | 21.6 | 20.5 | 19.1 | -
| W | 91.5 |  | 0.94857 |  | 22.5 | 18.4 | 20.8 | 20.6 | 20.2 | 19.7 | 20 | -
AL-BLTS | S | 91.5 |  | 0.96703 |  |  | 18.8 | 20.3 | 19 | 19.4 | 20 | 20.5 | -
| W | 91.5 |  | 0.98062 |  |  | 26.3 | 13.8 | 13.9 | 17 | 16.9 | 16.9 | -
ATS-ATD | S | 101.7407 |  | 1 |  |  | 8.2 | 10.7 | 13.3 | 15 | 17.4 | 21.2 | -
| W | 122.3174 |  | 0.98551 |  |  | 7 | 14.2 | 16 | 20.5 | 23.7 | 28 | -
BLTS-ATD | S | 97.1681 |  | 1 |  |  | 8.2 | 9.7 | 10.8 | 13.3 | 17.5 | 21.3 | -
| W | 125.7469 |  | 0.98551 |  |  | 7 | 12.7 | 16 | 20.6 | 23.8 | 28.1 | -
ATS-LVN | S | 109.7 |  | 0.97257 |  |  | 82.5 | 82.4 | 83.6 | 84.9 | 85.2 | 86.1 | -
| W | 134.9 |  | 0.99306 |  |  | 72.5 | 77.2 | 78.2 | 75.8 | 76.7 | 77.5 | -
BLTS-LVN | S | 109.7 |  | 0.96552 |  |  | 84.1 | 84 | 85.3 | 85.8 | 86.2 | 87.2 | -
| W | 122.3 |  | 0.9904 |  |  | 73.6 | 78.4 | 79.4 | 76.5 | 77.3 | 78.2 | -
ATS-SCI | S | 90.8 |  | 0.81465 |  |  | 53.6 | 64.8 | 55 | 51.8 | 56.8 | 63 | -
| W | 116 |  | 0.80396 |  |  | 56.5 | 56.6 | 56.6 | 57 | 56.8 | 56.7 | -
BLTS-SCI | S | 97.2 |  | 0.99135 |  |  | 70 | 70.1 | 70.1 | 69.9 | 69.8 | 69.7 | -
| W | 125.7 |  | 0.99275 |  |  | 69.5 | 69.4 | 69.4 | 69.3 | 69.2 | 69 | -
ATS-TYA | S | 102.3 |  | 0.99519 |  |  | 20.9 | 17.5 | 19.5 | 20.5 | 19.1 | 19 | -
| W | 130.3 |  | 0.98907 |  |  | 18.5 | 19.2 | 19.1 | 18.9 | 18.3 | 18.2 | -
BLTS-TYA | S | 88 |  | 0.99485 |  |  | 19.5 | 16.7 | 18.7 | 19.6 | 18.2 | 20.1 | -
| W | 112 |  | 0.87662 |  |  | 17.6 | 20.6 | 20.5 | 20.5 | 19.8 | 19.7 | -
BLTS-BMH | S | 32.6 | 3 | 0.98354 | 3.2 |  | 24.7 | 26.1 | 27.1 | 30.1 | 31.5 | 33.9 | -
| W | 37.7 | 12 | 0.97273 | 7.5 |  | 22.6 | 20.7 | 22.4 | 23.4 | 25.4 | 27.1 | -
BATS 66kV
BATS-BAN1 | S | 96 | 6 | 0.95972 | 12.3 |  | 90.5 | 87 | 89.2 | 92 | 93 | 94.9 | -
| W | 102.9 | 21 | 1 | 15 |  | 72.7 | 71.5 | 72.7 | 75.8 | 76.6 | 77.2 | -
BATS-BAN2 | S | 96 | 6 | 0.95762 | 12.3 |  | 91.2 | 87.6 | 89.8 | 91.7 | 92.8 | 94.6 | -
| W | 102.9 | 21 | 0.99862 | 15 |  | 72.4 | 71.2 | 72.4 | 75.5 | 76.3 | 76.8 | -
BAN-BGR | S | 46.2977 |  | 1 |  | 52.5 | 14.6 | 12.5 | 12.9 | 13.8 | 13.3 | 13.4 | -
| W | 47.4409 |  | 0.97842 |  | 52.5 | 14.2 | 11.9 | 12.4 | 12.5 | 12.4 | 12 | -
BGR-ART | S | 45.7261 |  | 0.96503 |  | 52.5 | 14.8 | 12.5 | 13.1 | 14 | 13.5 | 13.6 | -
| W | 47.4409 |  | 0.99231 |  | 52.5 | 13.1 | 10.6 | 11.2 | 11.4 | 11.3 | 10.8 | -
BATS-YSW/BGL | S | 33.3 | 4 | 0.96842 | 3.2 | 28.7 | 29.4 | 30.5 | 31.6 | 34 | 35.8 | 38.7 | -
| W | 33.3 | 5 | 0.92549 | 7.5 | 28.7 | 27.6 | 24.4 | 27.2 | 28.8 | 30.7 | 32.3 | -
YSW-BMH | S | 38.9 | 4 | 0.99554 | 3.2 | 28.7 | 22.5 | 23.4 | 24.4 | 26.5 | 28 | 30.3 | -
| W | 38.9 | 5 | 1 | 7.5 | 28.7 | 19.8 | 18.2 | 19.6 | 20.7 | 22.4 | 23.8 | -
BATS-BAS1 | S | 83.5 |  | 0.97724 | 15.3084 |  | 80.9 | 75.1 | 77 | 79.6 | 80.9 | 82.8 | -
| W | 102.9 |  | 0.98401 | 20.3366 |  | 69.9 | 73.4 | 75 | 76.4 | 78 | 81 | -
BATS-BAS2/BGF | S | 93.2 |  | 0.97601 |  |  | 81.1 | 76.4 | 78.3 | 79.7 | 81.1 | 83 | -
| W | 94.9 |  | 0.98401 |  |  | 69.9 | 73.4 | 75 | 77.6 | 79.3 | 81.1 | -
BETS 66kV
BETS-BGO | S | 109.7 |  | 0.96673 |  |  | 102.6 | 97.1 | 101.3 | 103.2 | 104.6 | 105.5 | -
| W | 114.3 |  | 1 |  |  | 70.6 | 66 | 68.9 | 70.7 | 71.8 | 71.8 | -
BGO-EHK | S | 54.9 | 4 | 0.92857 | 0 |  | 55.8 | 51.4 | 53 | 54.8 | 55.2 | 56.1 | -
| W | 52.6 | 3 | 1 | 4.8 |  | 35.7 | 33.3 | 35.2 | 36.6 | 37.3 | 37.6 | -
BETS-EHK | S | 111.5 |  | 0.95941 |  |  | 105.3 | 99.6 | 103.8 | 106 | 107.4 | 109.2 | -
| W | 111.5 |  | 0.99859 |  |  | 71.2 | 66.6 | 69.5 | 71.3 | 72.5 | 72.4 | -
BETS-CMN | S | 64 |  | 0.97394 |  |  | 63 | 62.2 | 62.1 | 63.5 | 62.4 | 50.8 | -
| W | 65.2 |  | 0.99774 |  |  | 44.3 | 38.3 | 38.2 | 38.1 | 37.9 | 41.1 | -
CMN-MRO | S | 26.3 | 6 | 0.97407 | 0 |  | 27.7 | 23.1 | 22.5 | 23.4 | 22.7 | 23.8 | -
| W | 35.4 | 4 | 1 | 0 |  | 23.2 | 19.3 | 19.2 | 19 | 18.7 | 21.5 | -
BETS-MRO | S | 76.6 |  | 0.88633 |  |  | 73.4 | 79.1 | 79.1 | 79.1 | 80 | 59.8 | -
| W | 89.2 |  | 0.97447 |  |  | 48.2 | 40.5 | 40.3 | 40.1 | 39.7 | 44 | -
BETS-CTN | S | 27.4 | 6.5 | 1 | 0.4 | 19.8 | 22 | 18.2 | 17.4 | 16.9 | 16.4 | 16.1 | -
| W | 26.3 | 3 | 0.98844 | 0.4 | 19.8 | 17.5 | 13.8 | 13.5 | 13.2 | 12.7 | 12.3 | -
CTN-CBW | S | 28 |  | 0 |  | 19.8 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | -
| W | 28 |  | 0 |  | 19.8 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | -
DPTS 66kV
DPTS-MLN1 | S | 135.4 |  | 0.94696 |  |  | 81.6 | 81.9 | 86.3 | 93.6 | 100.7 | 106.1 | -
| W | 142.3 |  | 0.97845 |  |  | 47.4 | 54.8 | 58.6 | 62 | 66.2 | 68.7 | -
DPTS-MLN2 | S | 135.4 |  | 0.94825 |  |  | 81.5 | 80.9 | 86.2 | 92.5 | 98.5 | 105.9 | -
| W | 142.3 |  | 0.97845 |  |  | 47.4 | 54.8 | 58.6 | 61.3 | 66.2 | 68.6 | -
DPTS-SU1 | S | 135.4 |  | 0.96827 |  |  | 100.9 | 110.7 | 119.7 | 121.2 | 125.6 | 128.6 | -
| W | 142.3 |  | 0.96709 |  |  | 81.7 | 91.6 | 93.6 | 96 | 98.3 | 98.3 | -
DPTS-SU2 | S | 135.4 |  | 0.95996 |  |  | 104.1 | 114.2 | 123.4 | 125 | 129.6 | 132.6 | -
| W | 142.3 |  | 0.96159 |  |  | 83.9 | 92.2 | 96.3 | 98.6 | 100.1 | 100.1 | -
DPTS-TNA1 | S | 135.4 |  | 0.97279 |  |  | 45.3 | 54.5 | 59.3 | 63.7 | 75.7 | 79.7 | -
| W | 142.3 |  | 0.96119 |  |  | 45.6 | 47 | 50 | 55.5 | 59.5 | 60.8 | -
DPTS-TNA2 | S | 135.4 |  | 0.97279 |  |  | 45.3 | 54.5 | 59.4 | 63.7 | 75.7 | 79.7 | -
| W | 142.3 |  | 0.96119 |  |  | 45.6 | 47 | 50 | 55.5 | 59.5 | 60.8 | -
FBTS 66kV
FBTS-DLF1 | S | 87.4512 |  | 0.95 |  |  | 27.4 | 20.9 | 21.7 | 22.6 | 23.8 | 25.1 | -
| W | 87.4512 |  | 0.9661 |  |  | 18.3 | 17.3 | 16.3 | 17.1 | 17.6 | 18 | -
FBTS-DLF3 | S | 87.4512 |  | 0.95 |  |  | 27.4 | 20.9 | 21.8 | 22.6 | 23.9 | 25.1 | -
| W | 87.4512 |  | 0.9661 |  |  | 18.3 | 17.3 | 16.4 | 17.1 | 17.7 | 18 | -
GTS 66kV
GTS-BCG | S | 109.7 |  | 0.96752 |  |  | 76.4 | 77.2 | 78.6 | 81.5 | 85.8 | 91.9 | -
| W | 134.9 |  | 0.98292 |  |  | 53.6 | 49 | 51.1 | 51.7 | 52.4 | 52.2 | -
BCG-WPD | S | 91.5 |  | 0.98955 |  |  | 67.7 | 67.2 | 68.3 | 70.7 | 74.6 | 79.5 | -
| W | 91.5 |  | 0.9958 |  |  | 47.8 | 42.7 | 44.5 | 45.2 | 45.8 | 45.7 | -
GTS-WPD | S | 91.5 | 3 | 0.97111 | 9.5 |  | 74.9 | 75.7 | 77 | 79.9 | 85.3 | 90 | -
| W | 91.5 | 5 | 0.98669 | 19.8 |  | 53.3 | 48.9 | 50.2 | 50.8 | 52.1 | 52 | -
GTS-WIN | S | 74.3 |  | 0.99291 |  |  | 42.6 | 35.5 | 36.3 | 39.1 | 38.4 | 39.4 | -
| W | 87.4 |  | 0.98982 |  |  | 39.7 | 30.6 | 31.5 | 32 | 32.6 | 32.2 | -
CLC-MGW | S | 92 |  | 0.99688 |  |  | 32.2 | 27.5 | 27.9 | 30.4 | 29.8 | 30.4 | -
| W | 92 |  | 1 |  |  | 30 | 23.9 | 24.6 | 25 | 25.5 | 25.2 | -
MGW-WIN | S | 95 |  | 0.97329 |  |  | 34.6 | 29.3 | 30 | 32.4 | 31.9 | 32.9 | -
| W | 100 |  | 0.96845 |  |  | 32.7 | 25.5 | 26.3 | 26.8 | 27.5 | 27.2 | -
GTS-CRO | S | 91.5 |  | 0.9434 |  |  | 33.7 | 30.1 | 31.7 | 33.5 | 32.3 | 32.5 | -
| W | 91.5 |  | 0.97635 |  |  | 30.3 | 23.2 | 23.5 | 23.7 | 23.6 | 23.2 | -
CRO-FDN | S | 109.7 |  | 0.94322 |  |  | 33.6 | 30 | 31.6 | 33.4 | 32.2 | 32.9 | -
| W | 134.9 |  | 0.97417 |  |  | 27.8 | 20.7 | 21.2 | 21.1 | 21 | 20.7 | -
GTS-FDN | S | 102.9 |  | 0.9434 |  |  | 33.7 | 30.1 | 31.7 | 33.5 | 32.3 | 33.1 | -
| W | 134.9 |  | 0.97635 |  |  | 30.3 | 23.2 | 23.8 | 23.7 | 23.6 | 23.2 | -
GTS-FNS | S | 88 |  | 0.97536 |  |  | 79 | 79.7 | 82.6 | 85.7 | 84.1 | 85 | -
| W | 112 |  | 0.98658 |  |  | 60.4 | 66.2 | 67 | 67.5 | 67.5 | 66.9 | -
FNS-SRC | S | 109.7 |  | 0.96107 |  |  | 42.8 | 41.2 | 42.2 | 45.1 | 44 | 44.9 | -
| W | 126.9 |  | 0.97222 |  |  | 37 | 37.7 | 38.1 | 38.4 | 38.3 | 38.2 | -
GTS-SRC | S | 109.7 |  | 0.97406 |  |  | 79.2 | 79.8 | 82.7 | 85.9 | 84.2 | 85.1 | -
| W | 134.9 |  | 0.985 |  |  | 60.9 | 66.3 | 67.2 | 67.6 | 68 | 67.4 | -
GTS-GB | S | 135.5 |  | 0.94804 |  |  | 115.7 | 118.7 | 125.4 | 130.4 | 129.3 | 132.4 | -
| W | 142.3 |  | 0.97558 |  |  | 88.2 | 77.4 | 78.8 | 80.3 | 79.7 | 78.7 | -
GB-GL | S | 110.3 | 3 | 0.9553 | 15.9 |  | 100.7 | 102.8 | 109 | 112.8 | 112.3 | 115.3 | -
| W | 131.5 | 4 | 0.97781 | 18.5 |  | 73.7 | 67 | 68.9 | 70.2 | 69.9 | 69 | -
GL-GCY | S | 109.7 |  | 0.9936 |  |  | 62.9 | 66.1 | 69.7 | 70.5 | 71.3 | 71.8 | -
| W | 134.9 |  | 0.99634 |  |  | 54.8 | 48.6 | 49.5 | 49.5 | 49.6 | 49 | -
GTS-GCY | S | 102.9 | 4 | 0.95672 | 15.9 |  | 113.5 | 117.9 | 123.9 | 128 | 127.7 | 131 | 14.58% | 87 | 198 | 307 | 298 | 398 | 15 | 25 | 32 | 31 | 37
| W | 110.3 | 7 | 0.97691 | 18.5 |  | 88.6 | 77.7 | 79.2 | 79.5 | 79.6 | 78.5 | -
GTS-GLE1 | S | 135.5 |  | 0.93586 |  |  | 126.6 | 141.7 | 139 | 144.5 | 147.5 | 156.3 | 4.576%
| W | 142.4 |  | 0.97582 |  |  | 84.7 | 84.2 | 86.3 | 89.4 | 90.2 | 91.8 | -
GTS-GLE2 | S | 135.5 |  | 0.9051 |  |  | 138.5 | 157.3 | 153.8 | 161.3 | 163.8 | 175.4 | 16.09% | 28.8385 | 21.9923 | 38.0169 | 45.6858 | 109.4184 | 2 | 2 | 3 | 4 | 10
| W | 142.4 |  | 0.96222 |  |  | 88 | 87.3 | 90.4 | 92.2 | 93.4 | 96.1 | -
GLE-DDL1 | S | 74.3 |  | 0.94746 |  |  | 62.3 | 67.4 | 63.4 | 66.8 | 68.7 | 72.8 | -
| W | 86.9 |  | 0.98982 |  |  | 39.7 | 40.2 | 41.2 | 42.1 | 42.7 | 43.8 | -
GLE-DDL2 | S | 74.3 |  | 0.94676 |  |  | 63.5 | 68.7 | 64.6 | 68.1 | 68.9 | 73.1 | -
| W | 86.9 |  | 0.9875 |  |  | 40.5 | 40.4 | 41.3 | 42.3 | 43.6 | 44.7 | -
HOTS 66kV
HOTS-STL1 | S | 49.2 |  | 0.99653 |  |  | 21.4 | 26.1 | 26.1 | 26.1 | 26 | 26.3 | -
| W | 57.2 |  | 0.98577 |  |  | 21.2 | 29.4 | 29.1 | 29.2 | 29.1 | 28.7 | -
HOTS-STL2 | S | 25.7 |  | 0.99635 |  |  | 20.2 | 24.3 | 24.3 | 24.5 | 24.3 | 24.6 | -
| W | 34.9 |  | 0.97328 |  |  | 19.8 | 27.8 | 27.5 | 27.7 | 27.5 | 27.1 | -
STL-ART | S | 38.3 |  | 0.96226 |  |  | 14.7 | 16.9 | 17.3 | 17.8 | 17.8 | 18.3 | -
| W | 43.4 |  | 0.94709 |  |  | 12.5 | 18.1 | 18.9 | 19.2 | 19.5 | 19.9 | -
HOTS-HSM1 | S | 49.2 |  | 0.9905 |  |  | 41.7 | 39.3 | 40.3 | 41.1 | 39.6 | 38.9 | -
| W | 52.6 |  | 1 |  |  | 35 | 32.5 | 32.7 | 32.8 | 31.8 | 30.5 | -
HOTS-HSM2 | S | 49.2 |  | 0.9905 |  |  | 41.7 | 39.2 | 40.2 | 41.1 | 39.6 | 38.9 | -
| W | 52.6 |  | 1 |  |  | 35 | 32.5 | 32.7 | 32.8 | 31.8 | 30.5 | -
HOTS-KWF | S | 44 |  | 0.75694 |  | 31 | 13.5 | 16.1 | 16.2 | 16.4 | 15.5 | 14.9 | -
| W | 43.4 |  | 0.78505 |  | 31 | 11.6 | 13.5 | 12.7 | 12.4 | 11.8 | 11.3 | -
KWF-NHL | S | 44 |  | 1 |  |  | 9.4 | 8.5 | 8.5 | 8.5 | 8.1 | 7.8
| W | 43.4 |  | 0.98734 |  |  | 8.5 | 7.5 | 7.4 | 7.3 | 7 | 6.7
HOTS-CHM | S | 26.2925 |  | 0.96429 |  |  | 2.9 | 2.7 | 2.7 | 2.7 | 2.6 | 2.5 | -
| W | 35.4378 |  | 0.36486 |  |  | 3 | 20.6 | 20.8 | 20.3 | 19.7 | 18.9 | -
KTS 66kV
SBY-GSB1 | S | 51.4 |  | 0.9685 |  |  | 52.5 | 50.8 | 53.1 | 54.7 | 56.2 | 57.9 | -
| W | 69.7 |  | 0.98755 |  |  | 48.8 | 50.1 | 51.3 | 52.8 | 53.9 | 54.2 | -
SBY-GSB2 | S | 76.6 |  | 0.96252 |  |  | 52.7 | 51.3 | 53.3 | 55.6 | 56.8 | 58.8 | -
| W | 89.2 |  | 0.98133 |  |  | 49.1 | 50.4 | 51.6 | 53 | 54.1 | 55.1 | -
GSB-WND1 | S | 109.7 |  | 0.97203 |  |  | 29.4 | 30.7 | 31.3 | 31.8 | 32.9 | 33.8 | -
| W | 114.3 |  | 0.99278 |  |  | 27.9 | 27.9 | 28.4 | 29.2 | 29.7 | 29.8 | -
GSB-WND2 | S | 46.3 |  | 0.9726 |  |  | 30 | 31.3 | 31.9 | 32.5 | 33.6 | 34.5 | -
| W | 49.7 |  | 0.9894 |  |  | 28.6 | 28.5 | 29.1 | 29.9 | 30.5 | 30.5 | -
KTS-SA1 | S | 108 |  | 0.91667 |  |  | 102.1 | 91.5 | 89.8 | 91.2 | 93.9 | 95.8 | -
| W | 122.3 |  | 0.97143 |  |  | 61.3 | 61.9 | 63.1 | 64.6 | 66 | 67 | -
KTS-SA2 | S | 116.6 |  | 0.91453 |  |  | 102.3 | 91.7 | 90 | 91.4 | 94.1 | 96.1 | -
| W | 122.3 |  | 0.97143 |  |  | 61.3 | 61.9 | 63.1 | 64.6 | 66.1 | 67 | -
KTS-SSE2 | S | 89.7 |  | 0.88656 |  |  | 91.5 | 93.2 | 94.7 | 98.2 | 100.8 | 102.6 | -
| W | 100.6 |  | 0.89496 |  |  | 79.8 | 78.2 | 79.9 | 80.3 | 82.2 | 82.1 | -
KTS-SSE1 | S | 100.6 |  | 0.88185 |  |  | 93.1 | 94.8 | 96.4 | 98.9 | 101.5 | 103.3 | -
| W | 125.7 |  | 0.89076 |  |  | 80.2 | 78.7 | 80.3 | 81.7 | 82.7 | 82.6 | -
KGTS 66kV
KGTS-CHA | S | 31.4 |  | 1 |  |  | 15.8 | 12.6 | 12.5 | 12.5 | 12.1 | 12.2 | -
| W | 41.2 |  | 0.99371 |  |  | 16 | 14.5 | 15.3 | 16 | 16.3 | 16.1 | -
KGTS-SHL | S | 36.009 | 7 | 0.96728 | 0.8 |  | 50.6 | 50.2 | 50.1 | 50.9 | 50.7 | 51 | 39.41% | 340.3775 | 380.5181 | 654.7955 | 943.123 | 930.2761 | 87 | 109 | 183 | 233 | 232
| W | 42.182 | 6 | 0.99373 | 1.7 |  | 32.1 | 37.6 | 41 | 44.9 | 47.8 | 47.5 | -
KGTS-GSF | S | 48.6 | 7 | 0.98544 | 0.8 |  | 41.8 | 41.5 | 41.4 | 42.7 | 42.5 | 42.8 | -
| W | 52.6 | 6 | 1 | 1.7 |  | 29 | 33.3 | 36.1 | 38 | 39.5 | 39.8 | -
GSF-SHL | S | 40 | 7 | 0.99244 | 0.8 |  | 40 | 39.7 | 39.6 | 40.8 | 40.6 | 40.9 | -
| W | 49.7 | 6 | 0.99648 | 1.7 |  | 28.5 | 32.5 | 35.1 | 36.9 | 38.2 | 38.6 | -
RCTS 66kV
RCTS-MBN | S | 97.2 |  | 0.91532 |  |  | 54.2 | 54.6 | 55.3 | 56.8 | 58.4 | 59.8 | -
| W | 114.3 |  | 0.99388 |  |  | 32.9 | 34.4 | 34.8 | 35.3 | 35.6 | 35.8 | -
MBN-DTN | S | 74.305 |  | 0.93805 |  |  | 24.1 | 24.1 | 24.1 | 24.2 | 24.1 | 24.1 | -
| W | 86.8797 |  | 0.96053 |  |  | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | -
MBN-MDA | S | 74.3 |  | 0.9479 |  |  | 52.6 | 53.6 | 53.6 | 55.2 | 56.7 | 57.5 | -
| W | 86.9 |  | 1 |  |  | 32.7 | 35.1 | 35.7 | 36.4 | 36.5 | 36.7 | -
MDA-BNG | S | 104.027 |  | 0.95015 |  |  | 35.9 | 36.7 | 37.4 | 37.7 | 38.2 | 38.5 | -
| W | 114.3154 |  | 1 |  |  | 25 | 26.3 | 26.6 | 27 | 27 | 27.1 | -
RCTS-MDA1 | S | 72.01 |  | 0.91166 |  |  | 89.4 | 89.8 | 90.9 | 93.2 | 96.3 | 98.4 | 24.7% | 165.6437 | 206.0664 | 309.1428 | 483.4044 | 628.259 | 40 | 45 | 59 | 76 | 90
| W | 90.9 |  | 0.99263 |  |  | 54.7 | 56.8 | 57.2 | 58 | 58.6 | 58.8 | -
RCTS-MDA2 | S | 104 |  | 0.92144 |  |  | 96.7 | 97.2 | 99.1 | 101.7 | 104.2 | 106.6 | -
| W | 114.3 |  | 0.99341 |  |  | 61.1 | 63.4 | 63.9 | 64.8 | 65.4 | 65.6 | -
RCTS-YSF | S | 84.6 |  | 0.8642 |  |  | 9.4 | 9.3 | 9.4 | 9.6 | 9.7 | 9.7 | -
| W | 106.3 |  | 0.75269 |  |  | 12.4 | 3.7 | 4.1 | 4.3 | 4.3 | 4.1 | -
YSF-HTH | S | 17.7 |  | 0.90909 |  |  | 8.5 | 8.4 | 8.5 | 8.7 | 8.8 | 8.8 | -
| W | 35.4 |  | 0.79545 |  |  | 11.1 | 2.4 | 2.9 | 3 | 3 | 2.9 | -
RCTS-KSF | S | 84.6 |  | 0.97927 |  |  | 19.7 | 18.7 | 19.1 | 19.4 | 19.6 | 19.7 | -
| W | 106.3 |  | 0.96491 |  |  | 11.8 | 5.8 | 6.4 | 6.7 | 6.7 | 6.7 | -
KSF-RVL | S | 65 |  | 0.97895 |  |  | 19.4 | 18.5 | 18.8 | 19.1 | 19.3 | 19.4 | -
| W | 65 |  | 0.97321 |  |  | 11.5 | 5.5 | 6.2 | 6.5 | 6.5 | 6.5 | -
RVL-BSP | S | 65.2 |  | 0.99457 |  |  | 18.5 | 17.6 | 18 | 18.2 | 18.4 | 18.5 | -
| W | 67.4 |  | 0.96364 |  |  | 11.4 | 5.5 | 6.1 | 6.4 | 6.4 | 6.4 | -
BSP-BBD | S | 65.2 |  | 0.95946 |  |  | 30.9 | 31.7 | 30.6 | 30.6 | 31.1 | 30.3 | -
| W | 67.4 |  | 0.95098 |  |  | 21.5 | 18.6 | 18.4 | 18.8 | 18.5 | 18.5 | -
SHTS 66kV
SHTS-KYM1 | S | 79.4 |  | 0.99023 |  |  | 51.7 | 55.3 | 56.1 | 56.8 | 57 | 57.2 | -
| W | 90.3 |  | 1 |  |  | 36.3 | 37.7 | 39.3 | 40.7 | 41.9 | 42.4 | -
SHTS-KYM2 | S | 79.4 |  | 0.99035 |  |  | 52.3 | 55.9 | 56.8 | 57.4 | 57.6 | 57.9 | -
| W | 90.3 |  | 1 |  |  | 36.7 | 38.1 | 39.8 | 41.2 | 42.4 | 42.9 | -
KYM-ECA1 | S | 45.7 |  | 0.98919 |  |  | 37.4 | 44.7 | 42.6 | 42.5 | 43.4 | 43.7 | -
| W | 53.2 |  | 1 |  |  | 23.9 | 27.9 | 29 | 29.8 | 31.2 | 31.5 | -
KYM-ECA2 | S | 45.7 |  | 0.98939 |  |  | 38.1 | 45.6 | 43.5 | 43.3 | 44.2 | 43.8 | -
| W | 53.2 |  | 1 |  |  | 23.9 | 27.9 | 29.1 | 30.3 | 31.3 | 32.1 | -
KYM-SHP | S | 104 |  | 0.9726 |  |  | 22.5 | 20 | 23.2 | 24 | 24.3 | 24 | -
| W | 114.3 |  | 0.99419 |  |  | 17.3 | 18.1 | 18.9 | 19.2 | 19.9 | 19.9 | -
SHTS-SHP | S | 101.7 |  | 0.98421 |  |  | 38.6 | 40.2 | 41.8 | 42.3 | 42.5 | 42.6 | -
| W | 118.3 |  | 0.99635 |  |  | 27.5 | 28.5 | 29.8 | 30.9 | 31.7 | 32.1 | -
SHTS-MNA | S | 88 |  | 0.96841 |  |  | 75.2 | 75.5 | 77.3 | 79.4 | 80 | 81.2 | -
| W | 111.5 |  | 0.98943 |  |  | 47.8 | 48.3 | 51.6 | 53.8 | 55.7 | 56.7 | -
MNA-STN | S | 48.6 |  | 0.99455 |  |  | 36.9 | 36.4 | 37 | 37.6 | 37.9 | 38.5 | -
| W | 52.6 |  | 0.9918 |  |  | 24.6 | 25.8 | 27.7 | 28.8 | 29.9 | 30.7 | -
SHTS-STN | S | 91.5 |  | 0.97497 |  |  | 73.7 | 73.6 | 75.4 | 77.4 | 78 | 79.2 | -
| W | 91.5 |  | 0.99153 |  |  | 47.6 | 48.1 | 50.7 | 52.7 | 55.1 | 56 | -
SHTS-NKA | S | 91 |  | 0.92072 |  |  | 84.9 | 85.4 | 83.3 | 86 | 88 | 88.6 | -
| W | 91 |  | 0.99271 |  |  | 55.3 | 56.3 | 57.5 | 60.4 | 63.2 | 64.1 | -
SHTS-NSF | S | 98 |  | 0.93709 |  |  | 81.4 | 81.8 | 78.9 | 82.5 | 83.1 | 84.9 | -
| W | 144 |  | 0.99453 |  |  | 55.1 | 55.6 | 56.8 | 59.7 | 62.3 | 63.2 | -
NSF-NKA | S | 103 |  | 0.96634 |  |  | 73.8 | 74.2 | 71.8 | 74.7 | 75.1 | 76.7 | -
| W | 144 |  | 0.99812 |  |  | 53.4 | 53.8 | 54.9 | 57.5 | 59.8 | 60.7 | -
NKA-CME | S | 74.3 |  | 0.95652 |  |  | 43.3 | 41.9 | 41.7 | 43.1 | 44 | 44.1 | -
| W | 86.9 |  | 0.99251 |  |  | 26.9 | 28.5 | 28.6 | 30.5 | 31.7 | 32 | -
SHTS-SHN1 | S | 88 |  | 0.97826 |  |  | 37.6 | 38.7 | 38.4 | 38.7 | 40.2 | 40.7 | -
| W | 112 |  | 0.99597 |  |  | 24.9 | 25.9 | 27.2 | 28.2 | 29.2 | 30.1 | -
SHTS-SHN2 | S | 88 |  | 0.97826 |  |  | 37.6 | 38.7 | 38.4 | 38.7 | 40.2 | 40.7 | -
| W | 112 |  | 0.99597 |  |  | 24.9 | 25.9 | 27.2 | 28.2 | 29.2 | 30.1 | -
TGTS 66kV
TGTS-CDN | S | 76.6 |  | 0.98413 |  |  | 38.4 | 36.6 | 36.8 | 38.1 | 37.6 | 38.1 | -
| W | 85.7 |  | 0.99459 |  |  | 37.2 | 34.3 | 35 | 35.3 | 35.3 | 35.2 | -
CDN-COB | S | 49.2 |  | 1 |  |  | 22 | 20.7 | 20.9 | 21.7 | 21.3 | 21.9 | -
| W | 57.2 |  | 1 |  |  | 21.7 | 18.7 | 19.1 | 19.3 | 19.2 | 19 | -
CDN-CLC | S | 74.3 |  | 0.99394 |  |  | 33.2 | 28.3 | 28.8 | 31.3 | 30.7 | 31.5 | -
| W | 86.9 |  | 0.9871 |  |  | 31.4 | 24.9 | 25.7 | 26.1 | 26.7 | 26.4 | -
TGTS-COB | S | 109.7 |  | 0.97024 |  |  | 34.6 | 33 | 33.2 | 34.4 | 33.9 | 34.3 | -
| W | 116 |  | 0.9878 |  |  | 33.2 | 30.8 | 31.4 | 31.7 | 31.8 | 31.6 | -
TGTS-HTN | S | 44.9 | 5 | 0.91349 | 2.7 | 86.7 | 43 | 35.5 | 36 | 36.7 | 36.7 | 36.8 | -
| W | 44.9 | 5 | 0.95536 | 3.4 | 86.7 | 35.2 | 44 | 51.8 | 53 | 53.7 | 54.4 | -
HTN-NRB | S | 42.2 | 5 | 0.93793 | 2.7 | 86.7 | 30.9 | 27.3 | 27.6 | 27.9 | 27.8 | 28
| W | 42.2 | 5 | 0.98479 | 3.4 | 86.7 | 26.7 | 30.4 | 30.4 | 30.3 | 30.6 | 30.6
TGTS-NRB | S | 42.2 | 5 | 0.86073 | 2.7 | 86.7 | 50.9 | 38.2 | 39 | 39.7 | 39.7 | 40.1 | - | 184 | 184 | 184 | 184 | 184 | 72 | 72 | 72 | 72 | 72
| W | 42.2 | 5 | 0.94169 | 3.4 | 86.7 | 36.4 | 50.1 | 50.1 | 50.1 | 50.1 | 50.1 | 18.72%
TGTS-KRT1 | S | 44 |  | 0.98494 |  |  | 33.7 | 30.1 | 30.8 | 32.3 | 32.6 | 33.7 | -
| W | 44.6 |  | 0.98718 |  |  | 31.6 | 33.7 | 35 | 36.4 | 37.8 | 38.5 | -
TGTS-KRT2 | S | 97.2 |  | 0.88432 |  |  | 44 | 38.6 | 39.4 | 41.4 | 41.7 | 43.2 | -
| W | 116 |  | 0.89636 |  |  | 39.8 | 42.1 | 44.1 | 45.2 | 47.4 | 48.1 | -
KRT-PLD1/CWF | S | 40 |  | 1 |  | 18.2 | 19.5 | 17 | 17.4 | 17.6 | 17.7 | 18.5 | -
| W | 45.7 |  | 1 |  | 18.2 | 20.3 | 21.2 | 21.8 | 21.9 | 22.5 | 22.7 | -
KRT-PLD2/YWF | S | 40 |  | 0.99512 |  | 30 | 20.6 | 17.8 | 18.3 | 18.8 | 19.1 | 19.7 | -
| W | 45.7 |  | 1 |  | 30 | 21.6 | 22.7 | 23.2 | 23.5 | 24.1 | 24.3 | -
KRT-WBL | S | 46.9 |  | 0.87649 |  |  | 28.6 | 24.3 | 24.9 | 26.6 | 26.9 | 28.2 | -
| W | 47.4 |  | 0.867 |  |  | 23.4 | 21.3 | 22.8 | 23.5 | 24.3 | 25 | -
TRG-WBL1 | S | 47.4 |  | 0.9555 |  |  | 40 | 35.4 | 36.2 | 38.1 | 38.4 | 39.9 | -
| W | 49.7 |  | 0.96023 |  |  | 36.7 | 38.4 | 40 | 41.6 | 43.3 | 44.2 | -
TRG-WBL2 | S | 45.7 |  | 0.9913 |  |  | 34.8 | 30.4 | 31 | 32.7 | 33 | 34.3 | -
| W | 46.3 |  | 0.99359 |  |  | 31.4 | 32.6 | 34.2 | 35.1 | 36.8 | 37.4 | -
TGTS-TRG1 | S | 91.5 |  | 0.99355 |  |  | 62.4 | 58.1 | 59.2 | 61.4 | 61.9 | 63.2 | -
| W | 91.5 |  | 0.99678 |  |  | 62.4 | 65.4 | 67.3 | 68.8 | 71.2 | 72.3 | -
TGTS-TRG2 | S | 91.5 |  | 0.99355 |  |  | 62.4 | 58.1 | 59.2 | 61.4 | 61.9 | 63.2 | -
| W | 91.5 |  | 0.99678 |  |  | 62.4 | 65.4 | 67.3 | 68.9 | 71.3 | 72.4 | -
WETS 66kV
WETS-HTH | S | 17.7 |  | 0.90789 |  |  | 8.4 | 8.3 | 8.5 | 8.6 | 8.7 | 8.7 | -
| W | 35.4 |  | 0.80233 |  |  | 10.7 | 2.1 | 2.5 | 2.7 | 2.7 | 2.6 | -
HTH-OYN | S | 17.7 |  | 0.91892 |  |  | 8.1 | 8.1 | 8.2 | 8.3 | 8.4 | 8.4 | -
| W | 35.4 |  | 0.79762 |  |  | 10.5 | 1.8 | 2.3 | 2.4 | 2.5 | 2.4 | -
WETS-WSF | S | 31.4 |  | 0.99582 |  |  | 24 | 21.9 | 21.6 | 21.4 | 21.5 | 22.1 | -
| W | 43.4 |  | 0.97619 |  |  | 12.9 | 8.6 | 8.2 | 8.5 | 8.6 | 8.5 | -
WSF-WMN | S | 31.4 |  | 0.99582 |  |  | 24 | 21.9 | 21.6 | 21.4 | 21.6 | 22.1 | -
| W | 43.4 |  | 0.984 |  |  | 12.7 | 8.4 | 8 | 8.2 | 8.3 | 8.3 | -
WETS-BSP | S | 87 | 10 | 0.93822 | 0 |  | 55.2 | 55.1 | 54.3 | 54.4 | 55.2 | 54.4 | -
| W | 87 | 1 | 0.98714 | 0.76923 |  | 31.5 | 22.8 | 23.2 | 23.9 | 23.6 | 23.7 | -
Note 1: Generation capacity is specified at the location (sub-transmission line/ loop) where the generation is connected to the network.
Note 2: The 2017 demand figures are actuals for summer and forecast for winter.
Note 3: Forecast demand worst case N-1 scenario refers to the expected load that the sub-transmission line would supply in the event of the worst case outage of a sub-transmission line within the loop system.
Note 4: Radial lines are studied with the expected load under system normal (or N) conditions and also under N-1 if normally open loop arrangement exists. Where load does not exceed the N rating, the N-1 risk is shown if this is worse case.
Note 5: With transfer of MLN to DPTS early 2017, sections of SBY-MLN & KTS-MLN are used for new Jemena KTS-SBY2 66kV line
Note 6: With transfer of SU to DPTS Oct 2017, SU-SSE is Out Of Service, part KTS-SU1 used for DPTS-SU1 with remainder OOS, KTS-SU2 becomes KTS-SSE1 and KTS-SSE becomes KTS-SSE2
Note 7: New looped lines to MLN, SU & TNA from DPTS by late 2017 early 2018
Note 8: With the construction of ATD, part of ATS-BLTS used for ATS-ATD and BLTS-ATD in 2017, this also reduces loads in adjacent loops
Note 9:
Note 10: WETS-RVL becomes WETS-BBD/RVL in mid 2018